## Tag Naming and Examples
Points List Creation Process You will be creating two points lists. One is a pared down list for GMS which will include controls. The other is for our Bazefield historian which will be read-only and contain additional points. When building the lists take note of the Column Required In List. Both lists need to be delivered in the Attachment 2: Owner's Points List Format. 1. Review the project single line diagrams and identify all the relays and power systems devices 2. For each device, identify the Device Type 3. Select the Device Type tab in this spreadsheet that matches the Device Type 4. Copy the columns for Attribute, Units, Point Type, and Description VERBATIM to the Attachment 2 Owner's Points List 5. Determine the Device ID using the below table and the single line diagrams 6. Populate the Device ID column in the owner's points list for all attributes you just copied 7. Fill out the remaining additional columns (Native RTAC Point Name, DNP Index, EGU Min and EGU Max) 8. Fill out the Availability coulumn per the direction in Attachment 2 Owner's Points List 9. Repeat steps 2-8 for remaining devices 10. If project is in Texas include the ERCOT tab in the points list. You will need to create calculated points for these. 11. Coordinate with the Transmission operator for the project and request all points in the TOP tab of this spreadsheet. It's okay if some of these are unavailable. 12. FOR GMS LIST ONLY: Identify all controllable breakers and switches and add them all to the Owner's points list per the Breaker Controls and MODs tab in this spreadsheet. Use the Device Type and DeviceID of Breaker and MOD Controls 13. If the project is a Battery Project and the vendor is Wartsila, include the additional points from the Generator tab for each generation resource and a Wartsila ESS Unit object for each ESS Unit tied to the generation resource. All of these points should be available
Device Type | Device ID | Example #1 | Example #2 | Notes
Turbine | WTG### | WTG002 | WTG013D
Inverter | INV### | INV003 | INV001A
Inverter Module | INV###-<##> | INV002-1A | INV002-01
MET Station | MET### | MET1 | MET14A
Meter | Use model #-name on one-line and HS or LS for high/low side | SEL-735-M1 HS | SEL-735-M2 LS
Breaker Relay | Use model #-name on one-line | SEL-351S-11F1
Bus Relay | Use model #-name on one-line | SEL-587Z-87B1
Transformer Relay | Use model #-name on one-line | SEL-487E-87T1P
Line Relay | Use model #-name on one-line | SEL-411L-87L1S
Reactive Power Relay | Use model #-name on one-line | SEL-487V-87VC1P
Annunciator | Use model #-name on one-line | SEL-2523-ANN1
Transformer Device | XFMR###-Device Model | XFMR001-Qualitrol ITM | XFMR002-Hydran
Soiling Station | SOIL### | SOIL001 | SOIL002
Discrete IO (DPAC) | use model #-Name on one-line | SEL-2440-1
Analog IO (Axion) | use model #-Name on one-line | SEL-2240-1
Transmission Operator | TOP | TOP
Generator PPC | Use Resource ID if dispatched by ISO, otherwise name from drawing set | CMDLND-2-2DS2R1 | UNIT1
POI | POI | POI
Breaker and MOD Controls | Breaker and MOD Controls | Breaker and MOD Controls
ESS Unit | Use Resource ID if dispatched by ISO, otherwise name from drawing set-ESS Unit # | CMDLND-2-2DS2R1 ESS Unit 4 | UNIT1 ESS Unit 4 | This is specific to a Wartsila BESS system

## Breaker and MOD Controls
Attribute Name | Units | Point Type | Description | Notes | Required In List
GMS # Breaker Control | Latch Off = Trip, Latch On = Close | Binary Output | Breaker Controls | Include all controls for all breakers shown on the one lines (i.e. GMS 52T1 Breaker Control) | GMS
GMS # MOD Control | Latch Off = Open, Latch On = Close | Binary Output | Breaker Controls | Include all controls for all MOD switches shown on the one lines (i.e. GMS 89L1 MOD Control) | GMS

## Soiling Station
Attribute Name | Units | Point Type | Description | Required In List | Notes
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | HISTORIAN
SoilingRatio | % | Analog Input | Soiling Ratio | HISTORIAN
SoilingRatioCumulative | % | Analog Input | Cumulative Soiling Ratio | HISTORIAN | Cumulative Soiling Ratio = (Energy Output without Soiling) / (Actual Energy Output) A Cumulative Soiling Ratio greater than 1 indicates that the energy output has decreased due to soiling
CurrentSCControlSample | A | Analog Input | ControlSample Short Circuit Current | HISTORIAN | Short Circuit Current of the sample clean PV module used as a benchmark for soiling analysis
CurrentSCCleanedSample | A | Analog Input | CleanedSample Short Circuit Current | HISTORIAN | Short Circuit Current of the actual PV module for soiling analysis

## Meter
Attribute Name | Units | Point Type | Description | Required In List | Notes
ApparentPower | MVA | Analog Input | Three Phase Apparent Power | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Apparent Power A Phase | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Apparent Power A Phase | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Apparent Power A Phase | GMS and HISTORIAN
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN | This should be the SEL_POU.Offline point in the meter inverted
Current0Imbalance | % | Analog Input | Zero-sequence current imbalance | GMS and HISTORIAN
CurrentA | A | Analog Input | Current A Phase | GMS and HISTORIAN
CurrentAAggregatedTHD | A | Analog Input | Total Harmonic Distortion Current A Phase | GMS and HISTORIAN
CurrentAHarmonic1 | A | Analog Input | mth Harmonic, Aggregate Current, Ia | GMS and HISTORIAN
CurrentAHarmonic2 | A | Analog Input | mth Harmonic, Aggregate Current, Ia | GMS and HISTORIAN
CurrentAHarmonic5 | A | Analog Input | mth Harmonic, Aggregate Current, Ia | GMS and HISTORIAN
CurrentAHarmonic7 | A | Analog Input | mth Harmonic, Aggregate Current, Ia | GMS and HISTORIAN
CurrentB | A | Analog Input | Current B Phase | GMS and HISTORIAN
CurrentB Harmonic5 | A | Analog Input | mth Harmonic, Aggregate Current, Ib | GMS and HISTORIAN
CurrentBAggregatedTHD | A | Analog Input | Total Harmonic Distortion Current B Phase | GMS and HISTORIAN
CurrentBHarmonic1 | A | Analog Input | mth Harmonic, Aggregate Current, Ib | GMS and HISTORIAN
CurrentBHarmonic2 | A | Analog Input | mth Harmonic, Aggregate Current, Ib | GMS and HISTORIAN
CurrentBHarmonic7 | A | Analog Input | mth Harmonic, Aggregate Current, Ib | GMS and HISTORIAN
CurrentC | A | Analog Input | Current C Phase | GMS and HISTORIAN
CurrentCAggregatedTHD | A | Analog Input | Total Harmonic Distortion Current C Phase | GMS and HISTORIAN
CurrentCHarmonic1 | A | Analog Input | mth Harmonic, Aggregate Current, Ic | GMS and HISTORIAN
CurrentCHarmonic2 | A | Analog Input | mth Harmonic, Aggregate Current, Ic | GMS and HISTORIAN
CurrentCHarmonic5 | A | Analog Input | mth Harmonic, Aggregate Current, Ic | GMS and HISTORIAN
CurrentCHarmonic7 | A | Analog Input | mth Harmonic, Aggregate Current, Ic | GMS and HISTORIAN
CurrentImbalance | % | Analog Input | Negative-sequence current imbalance | GMS and HISTORIAN
CurrentNAggregatedTHD | A | Analog Input | Total Harmonic Distortion Voltage N Phase | GMS and HISTORIAN
CurrentNeutral | A | Analog Input | Neutral Current | GMS and HISTORIAN
CurrentNHarmonic1 | A | Analog Input | mth Harmonic, Aggregate Current, In | GMS and HISTORIAN
CurrentNHarmonic2 | A | Analog Input | mth Harmonic, Aggregate Current, In | GMS and HISTORIAN
CurrentNHarmonic5 | A | Analog Input | mth Harmonic, Aggregate Current, In | GMS and HISTORIAN
CurrentNHarmonic7 | A | Analog Input | mth Harmonic, Aggregate Current, In | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_HALARM in the meter
PowerFactor | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
PowerFactorA | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
PowerFactorB | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
PowerFactorC | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
ReactiveEnergyDelivered | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredA | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredB | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredC | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyReceived | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedA | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedB | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedC | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
RealEnergyDelivered | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
RealEnergyDeliveredA | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
RealEnergyDeliveredB | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
RealEnergyDeliveredC | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
RealEnergyReceived | MWh | Accumulator | Energy Received | GMS and HISTORIAN
RealEnergyReceivedA | MWh | Accumulator | Energy Received | GMS and HISTORIAN
RealEnergyReceivedB | MWh | Accumulator | Energy Received | GMS and HISTORIAN
RealEnergyReceivedC | MWh | Accumulator | Energy Received | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Real Power A Phase | GMS and HISTORIAN
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Real Power B Phase | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Real Power C Phase | GMS and HISTORIAN
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN | This should be the SEL.FM_INST_EN point in the meter
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_SALARM in the meter
TransformerTotalLosses | watts | Analog Input | VAs 3 Total Transformer Losses | GMS and HISTORIAN
Voltage0Imbalance | % | Analog Input | Zero-sequence voltage imbalance | GMS and HISTORIAN
VoltageAAggregatedTHD | Volts | Analog Input | Total Harmonic Distortion Voltage A Phase | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Voltage A-B Phase | GMS and HISTORIAN
VoltageAHarmonic1 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Va | GMS and HISTORIAN
VoltageAHarmonic2 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Va | GMS and HISTORIAN
VoltageAHarmonic5 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Va | GMS and HISTORIAN
VoltageAHarmonic7 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Va | GMS and HISTORIAN
VoltageAN | KV | Analog Input | L-N Voltages | GMS and HISTORIAN
VoltageBAggregatedTHD | Volts | Analog Input | Total Harmonic Distortion Voltage B Phase | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Voltage B-C Phase | GMS and HISTORIAN
VoltageBHarmonic1 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vb | GMS and HISTORIAN
VoltageBHarmonic2 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vb | GMS and HISTORIAN
VoltageBHarmonic5 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vb | GMS and HISTORIAN
VoltageBHarmonic7 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vb | GMS and HISTORIAN
VoltageBN | KV | Analog Input | L-N Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Voltage C-A Phase | GMS and HISTORIAN
VoltageCAggregatedTHD | Volts | Analog Input | Total Harmonic Distortion Voltage C Phase | GMS and HISTORIAN
VoltageCHarmonic1 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vc | GMS and HISTORIAN
VoltageCHarmonic2 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vc | GMS and HISTORIAN
VoltageCHarmonic5 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vc | GMS and HISTORIAN
VoltageCHarmonic7 | Volts | Analog Input | mth Harmonic, Aggregate Voltage, Vc | GMS and HISTORIAN
VoltageCN | KV | Analog Input | L-N Voltages | GMS and HISTORIAN
VoltageImbalance | % | Analog Input | Negative Sequence Voltage Imbalance | GMS and HISTORIAN
VoltageLL | KV | Analog Input | Line to Line Voltage | GMS and HISTORIAN
VoltageLN | KV | Analog Input | Line to Neutral Voltage | GMS and HISTORIAN

## Bus Relay
Attribute Name | Units | Point Type | Description | Required In List | Notes
87DifferentialTrip | 0 = False 1 = True | Binary Input | 87 Relay Trip Signal, stays high until fault is cleared | GMS and HISTORIAN
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN | This should be the SEL_POU.Offline point in the relay inverted
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN | This should be the SEL.FM_INST_EN point in the relay
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_SALARM in the relay
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_HALARM in the relay
CurrentA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentC | A | Analog Input | Phase Currents | GMS and HISTORIAN

## Line Relay
Attribute Name | Units | Point Type | Description | Required In List | Notes
|  | Binary Input | Hard Wired Contacts | GMS and HISTORIAN | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out below, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
87DifferentialTrip | 0 = False 1 = True | Binary Input | 87 Relay Trip Signal, should stay high untill the relay is reset | GMS and HISTORIAN
87DirectTransferTrip | 0 = False 1 = True | Binary Input | DTT Trip Signal, should stay high untill the relay is reset | GMS and HISTORIAN
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN | This should be the SEL_POU.Offline point in the relay inverted
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN | This should be the SEL.FM_INST_EN point in the relay
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_SALARM in the relay
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_HALARM in the relay
BreakerFailInitiate | 0 = Normal, 1 = BFI | Binary Input | Breaker Fail Initiate | GMS and HISTORIAN
LineCommCutout | 0 = Normal, 1 = Cutout | Binary Input | Line Relaying Comm Cutout | GMS and HISTORIAN
LineCommFailure | 0 = Normal, 1 = Alarm | Binary Input | Line Relaying Comm Failure | GMS and HISTORIAN
50InstantaneousOCTrip | 0 = Normal, 1 = Trip | Binary Input | 50 Relay Instantaneous OC Trip, Should stay high until the fault condition is cleared | GMS and HISTORIAN
51TimeDelayOCTrip | 0 = Normal, 1 = Trip | Binary Input | 51 Relay Time Delay OC Trip, , Should stay high until the fault condition is cleared | GMS and HISTORIAN
#_Loss Of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Loss Of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Breaker Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | GMS and HISTORIAN | Invert any breakers where 0=Closed, typical of B contacts. If it is a 3 pole breaker logical OR them for a single status. Replace # with breaker name from one line (i.e. 52L1)
#_BreakerFailInitiate | 0 = Normal, 1 = BFI | Binary Input | Breaker Fail Initiate | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
#_Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52L1)
CurrentA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentC | A | Analog Input | Phase Currents | GMS and HISTORIAN
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
PowerFactor | Unitless | Analog Input | Power Factor | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Phase Power | GMS and HISTORIAN
VoltageAN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageBN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageCN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
PowerFactorA | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorB | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorC | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN

## Transformer Relay
Attribute Name | Units | Point Type | Description | Required In List | Notes
|  | Binary Input | Hard Wired Contacts | GMS and HISTORIAN | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out below, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN
#_LockOutStatus | 0=Normal, 1=Trip | Binary Input | 86 Lockout Relay Element Status | GMS and HISTORIAN | Replace # with LOR name from one line (i.e. 86T1)
87DifferentialTrip | 0 = Normal, 1 = Trip | Binary Input | 87 Relay element Trip Signal, stay high untill the fault conditions are cleared | GMS and HISTORIAN
TripStatus | 0 = Normal, 1 = Trip | Binary Input | Relay Trip Status, stay high untill the fault conditions are cleared | GMS and HISTORIAN
OilTempTrip | 0 = Normal, 1 = Trip | Binary Input | Oil Temp Trip, stay high untill the fault conditions are cleared | GMS and HISTORIAN
BucholzRelayTrip | 0 = Normal, 1 = Trip | Binary Input | Bucholz Relay Trip, stay high untill the fault conditions are cleared | GMS and HISTORIAN
#_Loss Of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Loss Of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Breaker Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | GMS and HISTORIAN | Invert any breakers where 0=Closed, typical of B contacts. If it is a 3 pole breaker logical OR them for a single status. Replace # with breaker name from one line (i.e. 52T1)
#_BreakerFailInitiate | 0 = Normal, 1 = BFI | Binary Input | Breaker Fail Initiate | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
#_Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52T1)
CurrentLowSideA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentLowSideB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentLowSideC | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentHighSideA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentHighSideB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentHighSideC | A | Analog Input | Phase Currents | GMS and HISTORIAN
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
PowerFactor | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Phase Power | GMS and HISTORIAN
VoltageAN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageBN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageCN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN

## POI
Attribute Name | Units | Point Type | Description | Required In List | Notes
GMS-PowerFactorSetpoint | PF*100 | Analog Output | GMS POI PF Setpoint | GMS
GMS-VoltageSetpoint | KV*100 | Analog Output | GMS POI Voltage Setpoint | GMS
GMS-ReactivePowerSetpoint | MVAR*100 | Analog Output | GMS POI VAR Setpoint | GMS
GMS-VoltageModeDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Voltage Mode Disable/Enable | GMS
GMS-PFModeDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS PF Mode Disable/Enable | GMS
GMS-MVARModeDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS MVAR Mode Disable/Enable | GMS
GMS-ReactivePowerSetpointFeedback | MVAR | Analog Input | GMS POI VAR Setpoint Feedback | GMS and HISTORIAN
GMS-PowerFactorSetpointFeedback | positive is lagging, negative is leading | Analog Input | GMS POI PF Setpoint Feedback | GMS and HISTORIAN
GMS-VoltageSetpointFeedback | KV | Analog Input | GMS POI Voltage Setpoint Feedback | GMS and HISTORIAN
EffectiveReactivePowerSetpoint | MVAR | Analog Input | PPC Reactive Power Setpoint | GMS and HISTORIAN
EffectivePowerFactorSetpoint | positive is lagging, negative is leading | Analog Input | PPC Power Factor Setpoint | GMS and HISTORIAN
EffectiveVoltageSetpoint | KV | Analog Input | PPC Voltage Setpoint | GMS and HISTORIAN
EffectiveReactivePowerControlMode | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Analog Input | PPC Control Status | GMS and HISTORIAN
FrequencyContribution | MW | Analog Input | Power offset due to freqency response | GMS and HISTORIAN
FrequencyMaxWhenLastActive | Hz | Analog Input | Highest frequency observed last time frequency control was active | GMS and HISTORIAN
FrequencyMinWhenLastActive | Hz | Analog Input | Lowest frequency observed last time frequency control was active | GMS and HISTORIAN
HMI-PowerFactorSetpoint | positive is lagging, negative is leading | Analog Input | HMI POI PF Setpoint Feedback | GMS and HISTORIAN
HMI-ReactivePowerSetpoint | MVAR | Analog Input | HMI POI VAR Setpoint Feedback | GMS and HISTORIAN
HMI-VoltageSetpoint | KV | Analog Input | HMI POI Voltage Setpoint Feedback | GMS and HISTORIAN
Offtaker-PowerFactorSetpoint | positive is lagging, negative is leading | Analog Input | Offtaker POI PF Setpoint Feedback | GMS and HISTORIAN
Offtaker-ReactivePowerSetpoint | MVAR | Analog Input | Offtaker POI VAR Setpoint Feedback | GMS and HISTORIAN
Offtaker-VoltageSetpoint | KV | Analog Input | Offtaker POI Voltage Setpoint Feedback | GMS and HISTORIAN
ReactivePowerDegradedBasis | 0=on setpoint, 1=asset(s) not responding, 3=other | Analog Input | Reason why reactive power is not at the setpoint | GMS and HISTORIAN
ReactivePowerPIDerror | MVAR | Analog Input | Error signal prior to PID compensation for Reactive Power loop | GMS and HISTORIAN
VoltageDroopVARtarget | MVAR | Analog Input | Output of voltage droop curve (setpoint input to the PID loop) | GMS and HISTORIAN
GMS-ReactivePowerControlStatus | 0=Disabled, 1=Enabled | Binary Input | GMS Reactive Power Control Disabled/Enabled | GMS and HISTORIAN
GMS-PowerFactorControlStatus | 0=Disabled, 1=Enabled | Binary Input | GMS Power Factor Control Disabled/Enabled | GMS and HISTORIAN
GMS-VoltageControlStatus | 0=Disabled, 1=Enabled | Binary Input | GMS Voltage Control Disabled/Enabled | GMS and HISTORIAN
AVRActive | 0=FALSE, 1=TRUE | Binary Input | AVR Active | GMS and HISTORIAN
GMS-InvalidVoltageSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Voltage Setpoint Alarm | GMS and HISTORIAN
GMS-InvalidVARSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS VAR Setpoint Alarm | GMS and HISTORIAN
GMS-InvalidPFSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS PF Setpoint Alarm | GMS and HISTORIAN
HighFrequencyEventFlag | 0=Off, 1=On | Binary Input | High Frequency Event Flag | GMS and HISTORIAN
LowFrequencyEventFlag | 0=Off, 1=On | Binary Input | Low Frequency Event Flag | GMS and HISTORIAN
HMI-PowerFactorControlStatus | 0=Disabled, 1=Enabled | Binary Input | HMI Power Factor Control Disabled/Enabled | GMS and HISTORIAN
HMI-ReactivePowerControStatus | 0=Disabled, 1=Enabled | Binary Input | HMI Reactive Power Control Disabled/Enabled | GMS and HISTORIAN
HMI-VoltageControlStatus | 0=Disabled, 1=Enabled | Binary Input | HMI Voltage Control Disabled/Enabled | GMS and HISTORIAN
MeterAlarm | 0=FALSE, 1=TRUE | Binary Input | PPC has failed over to alternate control feedback signal to due loss of comms with meter or other fault | GMS and HISTORIAN
OverFrequencyResponseActive | 0=Disabled, 1=Enabled | Binary Input | Indication when frequency control is biasing real power downwards | GMS and HISTORIAN
PPCWatchdogAlarm | 0=FALSE, 1=TRUE | Binary Input | PPC internal watchdog has triggered | GMS and HISTORIAN
ReactivePowerCurtailmentAlarm | 0=FALSE, 1=TRUE | Binary Input | Reactive power is beyond 1% of setpoint for more than 60 minutes | GMS and HISTORIAN
ReactivePowerCurtailmentIndication | 0=FALSE, 1=TRUE | Binary Input | Reactive power is beyond 1% of setpoint for more than 5 minutes | GMS and HISTORIAN
ReactivePowerCurtailmentWarning | 0=FALSE, 1=TRUE | Binary Input | Reactive power is beyond 1% of setpoint for more than 15 minutes | GMS and HISTORIAN
UnderFrequencyResponseActive | 0=Disabled, 1=Enabled | Binary Input | Indication when frequency control is biasing real power upwards | GMS and HISTORIAN

## Generator PPC
Attribute Name | Units | Point Type | Description | Required In List | Notes
GMS-RealPowerSetpoint | MW*100 | Analog Output | MW Setpoint | GMS
GMS-RampUpRateSetpoint | (MW/min)*100 | Analog Output | GMS Ramp Up Rate Setpoint | GMS
GMS-RampDownRateSetpoint | (MW/min)*100 | Analog Output | GMS Ramp Down Rate Setpoint | GMS
GMS-RealPowerSetpointFeedback | MW | Analog Input | GMS MW Setpoint Feedback | GMS and HISTORIAN
GMS-RampUpRateSetpointFeedback | MW/Min | Analog Input | GMS Ramp Up Rate Setpoint Feedback | GMS and HISTORIAN
GMS-RampDownRateSetpointFeedback | MW/Min | Analog Input | GMS Ramp Down Rate Setpoint Feedback | GMS and HISTORIAN
EffectiveRealPowerSetpoint | MW | Analog Input | PPC Real Power Setpoint | GMS and HISTORIAN
EffectiveRampRateUpSetpoint | MW/Min | Analog Input | PPC Ramp Rate Up Setpoint | GMS and HISTORIAN
EffectiveRampRateDownSetpoint | MW/Min | Analog Input | PPC Ramp Rate Down Setpoint | GMS and HISTORIAN
RealTimePowerPotential | MW | Analog Input | PPC Real Time Power Potential | GMS and HISTORIAN
Offtaker-RealPowerSetpoint | MW | Analog Input | Offtaker MW Setpoint Feedback (one for each PPA) | GMS and HISTORIAN
HMI-RealPowerSetpoint | MW | Analog Input | HMI MW Setpoint Feedback (one for each PPA) | GMS and HISTORIAN
HMI-RampDownRateSetpoint | MW/Min | Analog Input | HMI Ramp Down Rate Setpoint Feedback (one for each PPA) | GMS and HISTORIAN
HMI-RampUpRateSetpoint | MW/Min | Analog Input | HMI Ramp Up Rate Setpoint Feedback (one for each PPA) | GMS and HISTORIAN
GMS-CurtailmentDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Curtailment Disable/Enable | GMS
GMS-RampUpRateSetpointDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Ramp Up Rate Setpoint Disable/Enable | GMS
GMS-RampDownRateSetpointDisable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Ramp Down Rate Setpoint Disable/Enable | GMS
GMS-CurtailmentDisabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Curtailment Disabled/Enabled | GMS and HISTORIAN
GMS-RampUpRateControlDisabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Ramp Up Rate Control Disabled/Enabled | GMS and HISTORIAN
GMS-RampDownRateControlDisabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Ramp Down Rate Control Disabled/Enabled | GMS and HISTORIAN
GMS-InvalidCurtailmentSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Curtailment Setpoint Alarm | GMS and HISTORIAN
GMS-InvalidRampRateUpSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Ramp Rate Setpoint Alarm | GMS and HISTORIAN
GMS-InvalidRampRateDownSetpointAlarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Ramp Rate Setpoint Alarm | GMS and HISTORIAN
ActiveCurtailment | 0=FALSE, 1=TRUE | Binary Input | Active Curtailment | GMS and HISTORIAN
Offtaker-UnitCurtailmentEnabled | 0=Disabled, 1=Enabled | Binary Input | Offtaker Curtailment Disabled/Enabled (one for each PPA) | GMS and HISTORIAN
HMI-UnitCurtailmentEnabled | 0=Disabled, 1=Enabled | Binary Input | HMI Curtailment Disabled/Enabled (one for each PPA) | GMS and HISTORIAN
HMI-RampDownRateControlStatus | 0=Disabled, 1=Enabled | Binary Input | HMI Ramp Down Rate Control Disabled/Enabled (one for each PPA) | GMS and HISTORIAN
HMI-RampUpRateControlStatus | 0=Disabled, 1=Enabled | Binary Input | HMI Ramp Up Rate Control Disabled/Enabled (one for each PPA) | GMS and HISTORIAN
SiteESSRealPower | MW | Analog Input | Site ESS Real Power | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSReactivePower | MVAR | Analog Input | Site ESS Reactive Power | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSBatteryEffectiveSOC | % | Analog Input | Site ESS Battery Effective SOC | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSBatteryAverageSOC | % | Analog Input | Site ESS Battery Average SOC | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSChargePowerLimit | KW | Analog Input | Site ESS Charge Power Limit | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSDischargePowerLimit | KW | Analog Input | Site ESS Discharge Power Limit | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSChargeableEnergy | KWh | Analog Input | Site ESS Chargeable Energy | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSDischargeableEnergy | KWh | Analog Input | Site ESS Dischargeable Energy | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSMinimumChargeTime | Minutes | Analog Input | Site ESS Minimum Charge Time | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSMaximumChargeTime | Minutes | Analog Input | Site ESS Maximum Charge Time | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSChargeRampRate | MW/min | Analog Input | Site ESS Charge Ramp Rate | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSMinimumDischargeTime | Minutes | Analog Input | Site ESS Minimum Discharge Time | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSMaximumDischargeTime | Minutes | Analog Input | Site ESS Maximum Discharge Time | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
Ratioofactiveinverters | % | Analog Input | Ratio of active inverters | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSOperationCodeIndicator | N/A | Analog Input | 0: No Operation, 1: Target SoC, 2: Stacked Operation | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
TotalNumberofESSUnitsinIdlestate | N/A | Analog Input | Total Number of ESS Units in Idle state | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
NumberofESSUnitsDischarging | N/A | Analog Input | Number of ESS Units Discharging | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
NumberofESSUnitsCharging | N/A | Analog Input | Number of ESS Units Charging | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
AllowedDischargeableEnergy | KWh | Analog Input | Allowed Dischargeable Energy | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
AllowedChargeableEnergy | KWh | Analog Input | Allowed Chargeable Energy | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSOperableUnitsCount | N/A | Analog Input | Site ESS Operable Units Count | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSSOH | % | Analog Input | Site ESS SOH | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteAutoOperationIndicator | 0 - Disabled; 1 - Enabled | Binary Input | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSLockIndicator | 0 - Unlocked; 1 - Locked | Binary Input | Site ESS Lock Indicator | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSRunIndicator | 0 - Off; 1 - On | Binary Input | Site ESS Run Indicator | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSRemoteControlIndicator | 0 - Disabled; 1 - Enabled | Binary Input | Site ESS Remote Control Indicator | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSWarningIndicator | 0 - No Site ESS warning; 1 - Site ESS warning present | Binary Input | Site ESS Warning Indicator | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSFaultIndicator | 0 - No Site ESS fault; 1 - Site ESS fault present | Binary Input | Site ESS Fault Indicator | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSChargeLimit | KW | Analog Output | Max P charge limit to avoid charging from the grid | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSDischargeLimit | kW | Analog Output | Max P discharge limit to avoid over-discharging to the grid | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteAutoOperationControl | 0 - Disabled; 1 - Enabled | Binary Output | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSLockControl | 0 - Unlock; 1 - Lock | Binary Output | 0 - Unlock; 1 - Lock | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSRunControl | 0 - Stop; 1 - Start | Binary Output | 0 - Stop; 1 - Start. This command is only for manually operating the site. Don't use this command when either ESS Auto-start or ESS Auto-Operation is enabled | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSRemoteControlControl | 0 - Disable; 1 - Enable | Binary Output | 0 - Disable; 1 - Enable. When external power control enabled, GEMS follows P and Q set points received at the AO point list | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
SiteESSFaultReset | 1 - Reset | Binary Output | Send 1 to reset Site ESS fault. It will reset all ESS units | GMS | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
TotalPowerPlantEnergyChargedToDate | KWH | Accumulator | Total Power Plant Energy Charged To Date | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
TotalPowerPlantEnergyDischargedToDate | KWH | Accumulator | Total Power Plant Energy Discharged To Date | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
TotalSiteESSEnergyChargedToDate | KWH | Accumulator | Total Site ESS Energy Charged To Date | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely
TotalSiteESSEnergyDischargedToDate | KWH | Accumulator | Total Site ESS Energy Discharged To Date | GMS and HISTORIAN | Include only if Generator is a Wartsila BESS, otherwise leave out entirely

## Transformer Device
Attribute Name | Units | Point Type | Description | Required In List | Notes
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN
OilTemperatureHighAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
WindingTemperatureHighAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
HighPressureAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
LowPressureAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
LowVacuumAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
OilLevelLowAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
SuddenPressureAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
LossOfCoolingAlarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms | GMS and HISTORIAN
LiquidLevelAlarm | 0 = false 1 = true | Binary Input | Water Detected in Sensor or Oil Level Not OK | GMS and HISTORIAN
HumiditySensorFailure | 0 = Normal, 1 = Failed | Binary Input | Humidity Sensor Failed | GMS and HISTORIAN
RegenerationFailure | 0 = Normal, 1 = Failed | Binary Input | Regeneration Cycle Failed | GMS and HISTORIAN
EnclosureHeaterTemperatureSensorFailure | 0 = Normal, 1 = Failed | Binary Input | Enclosure Temperature Sensor Failure | GMS and HISTORIAN
SolenoidPressureSwitchFailure | 0 = Normal, 1 = Failed | Binary Input | Pressure Switch for (Which Solenoid) Failure | GMS and HISTORIAN
FanStageStatus | 0,1,2 | Analog Input | Stage Fan Status | GMS and HISTORIAN
FanRPM | RPM | Analog Input | Oil Cooling Fan RPM | GMS and HISTORIAN
TemperatureOil | °C | Analog Input | Oil Temperature | GMS and HISTORIAN
TemperatureWinding | °C | Analog Input | Winding Temperature | GMS and HISTORIAN
PressureTransformer | hPa | Analog Input | Case Pressure | GMS and HISTORIAN
OilLevel | % | Analog Input | Oil Level | GMS and HISTORIAN
TapPosition | Tap Number | Analog Input | Transformer Tap Position | GMS and HISTORIAN
TotalTransformerLosses | W | Analog Input | 3 Phase Total Transformer (copper +core) Losses | GMS and HISTORIAN
CurrentAPrimaryWinding | A | Analog Input | A Phase Current for HV Primary Winding | GMS and HISTORIAN
CurrentBPrimaryWinding | A | Analog Input | B Phase Current for HV Primary Winding | GMS and HISTORIAN
CurrentCPrimaryWinding | A | Analog Input | C Phase Current for HV Primary Winding | GMS and HISTORIAN
CurrentASecondaryWinding | A | Analog Input | A Phase Current for LV Secondary Winding | GMS and HISTORIAN
CurrentBSecondaryWinding | A | Analog Input | B Phase Current for LV Secondary Winding | GMS and HISTORIAN
CurrentCSecondaryWinding | A | Analog Input | C Phase Current for LV Secondary Winding | GMS and HISTORIAN
CurrentATertiaryWinding | A | Analog Input | A Phase Current for LV Tertiary Winding | GMS and HISTORIAN
CurrentBTertiaryWinding | A | Analog Input | B Phase Current for LV Tertiary Winding | GMS and HISTORIAN
CurrentCTertiaryWinding | A | Analog Input | C Phase Current for LV Tertiary Winding | GMS and HISTORIAN
CurrentH0 | A | Analog Input | H0 Current (Magnetizing Current of the trasfomer) | GMS and HISTORIAN
CurrentX0 | A | Analog Input | X0 Current (No-Load Loss Current of the transformer) | GMS and HISTORIAN
PrimaryWindingBushingLeakageCurrentA | mA | Analog Input | A Phase Current Leakage, HV Winding Bushing | GMS and HISTORIAN
PrimaryWindingBushingLeakageCurrentB | mA | Analog Input | B Phase Current Leakage, HV Winding Bushing | GMS and HISTORIAN
PrimaryWindingBushingLeakageCurrentC | mA | Analog Input | C Phase Current Leakage, HV Winding Bushing | GMS and HISTORIAN
SecondaryWindingBushingLeakageCurrentA | mA | Analog Input | A Phase Current Leakage, LV Winding Bushing | GMS and HISTORIAN
SecondaryWindingBushingLeakageCurrentB | mA | Analog Input | B Phase Current Leakage, LV Winding Bushing | GMS and HISTORIAN
SecondaryWindingBushingLeakagecurrentC | mA | Analog Input | C Phase Current Leakage, LV Winding Bushing | GMS and HISTORIAN
MoistureInOil | ppm | Analog Input | Disolved H2O in Oil | GMS and HISTORIAN
RelativeTimeDay | Days | Analog Input | Number of days since the device was energized | GMS and HISTORIAN
RelativeTimeHours | Hours | Analog Input | Number of hours in the current day since the device was energized | GMS and HISTORIAN
RelativeTimeMinutes | Minutes | Analog Input | Number of minutes in the current day since the device was energized | GMS and HISTORIAN
DaysSinceRegenration | Days | Analog Input | Number of days since last Regeneration occurred | GMS and HISTORIAN
ConfigureGenPeriod | Minutes | Analog Input | Number of minutes to engage Desiccant Heater during Regeneration. Defaults to 180 minutes | GMS and HISTORIAN
ConfigCoolDownPeriod | Minutes | Analog Input | Number of minutes to wait after turning off Desiccant Heater during the Regeneration cycle. Defaults to 60 minutes. | GMS and HISTORIAN
PPMLSB | NA | Analog Input | Moisture in PPM: Least significant 16 bits of reading | GMS and HISTORIAN
PPMMSB | NA | Analog Input | Moisture in PPM: Most significant 16 bits of reading | GMS and HISTORIAN
HumidityLSB | NA | Analog Input | Relative Humidity: Least significant 16 bits of reading | GMS and HISTORIAN
HumidityMSB | NA | Analog Input | Relative Humidity: Most significant 16 bits of reading | GMS and HISTORIAN
TemperatureLSB | NA | Analog Input | Temperature: Least significant 16 bits of reading | GMS and HISTORIAN
TemperatureMSB | NA | Analog Input | Temperature: Most significant 16 bits of reading | GMS and HISTORIAN

## Reactive Power Relay
Attribute Name | Units | Point Type | Description | Required In List | Notes
|  | Binary Input | Hard Wired Contacts | GMS and HISTORIAN | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out below, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN | This should be the SEL_POU.Offline point in the relay inverted
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN | This should be the SEL.FM_INST_EN point in the relay
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_SALARM in the relay
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_HALARM in the relay
VoltageTrip | 0 = Normal, 1 = Trip | Binary Input | Under / Over Voltage Trip Signal, should stay high until the trip conditions clear | GMS and HISTORIAN
OverCurrentTrip | 0 = Normal, 1 = Trip | Binary Input | 50 or 51 Overcurrent Trip signal, should stay high until the Trip conditions clear | GMS and HISTORIAN
#_TripCoilMonitor1 | 0 = Normal, 1 = Alarm | Binary Input | 52XX TCM 1 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_TripCoilMonitor2 | 0 = Normal, 1 = Alarm | Binary Input | 52XX TCM 2 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
VoltageInterrupt | 0 = Normal, 1 = Alarm | Binary Input | if volatge < 10% nominal, should stay high | GMS and HISTORIAN
VoltageSag | 0 = Normal, 1 = Alarm | Binary Input | if volatge <90% nominal, should stay high | GMS and HISTORIAN
VoltageSwell | 0 = Normal, 1 = Alarm | Binary Input | if volatge >110% nominal, should stay high | GMS and HISTORIAN
#_Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Loss of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss Of AC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Loss of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss Of DC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52V1)
#_Switch Status | 0 = Open, 1 = Closed | Binary Input | Switch Status | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Loss of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Loss of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
#_TripCoilAlarm | 0 = Normal, 1 = Alarm | Binary Input | 89 TCM Alarm | GMS and HISTORIAN | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
CurrentA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentC | A | Analog Input | Phase Currents | GMS and HISTORIAN
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
PowerFactor | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Phase Power | GMS and HISTORIAN
VoltageAN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageBN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageCN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
PowerFactorA | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorB | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorC | Positive = Leading, Negative = Lagging | Analog Input | Phase Power Factor | GMS and HISTORIAN

## TOP
Attribute Name | Units | Point Type | Description | Required In List | Notes
EnergyReceivedA | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyReceivedB | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyReceivedC | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyDeliveredA | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
EnergyDeliveredB | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
EnergyDeliveredC | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
ReactiveEnergyReceivedA | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedB | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedC | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyDeliveredA | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredB | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredC | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN
EnergyReceived | MWh | Accumulator | Energy Received | GMS and HISTORIAN
EnergyDelivered | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
ReactiveEnergyReceived | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyDelivered | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
PowerFactor | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
CurrentA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentC | A | Analog Input | Phase Currents | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Phase Power | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
PowerFactorA | N/A | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorB | N/A | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorC | N/A | Analog Input | Phase Power Factor | GMS and HISTORIAN
POI Breaker 52# Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | GMS and HISTORIAN | Get the status of all breakers that we are connected to at the POI. If this is a ring bus there may be more than one Replace # with the actual breaker notation on the one line

## MET Station
Attribute Name | Units | Point Type | Description | Required In List | Notes
CommStatus | 0=Offline, 1=Online | Binary Input | Communications staus | GMS and HISTORIAN
Icing | mm | Binary Input | Icing Detection | GMS and HISTORIAN | Only Available at Wind Plants
VoltageBattery | V | Analog Input | Voltage of Logger battery (12V typical) | GMS and HISTORIAN
TemperatureAmbient | °C | Analog Input | Ambient Temperature | GMS and HISTORIAN
WindSpeed | m/s | Analog Input | Wind Speed | GMS and HISTORIAN
WindDirection | ° | Analog Input | Wind Direction | GMS and HISTORIAN
RelativeHumidity | % | Analog Input | Relative Humidity | GMS and HISTORIAN
Rain | mm | Analog Input | Rainfall Measurement Sensor | GMS and HISTORIAN
AlbedometerSolarSide | W/m2 | Analog Input | Albedometer - Solar Side | GMS and HISTORIAN | Only Available at Solar Plants
AlbedometerGroundSide | W/m2 | Analog Input | Albedometer - Ground Side | GMS and HISTORIAN | Only Available at Solar Plants
IrradianceReferenceCell2 | W/m^2 | Analog Input | POA-Reference Cell2 | GMS and HISTORIAN | Only Available at Solar Plants
IrradianceReferenceCell | W/m^2 | Analog Input | POA-Reference Cell1 | GMS and HISTORIAN | Only Available at Solar Plants
TemperatureModule1 | °C | Analog Input | Module Temperature 1 | GMS and HISTORIAN | Only Available at Solar Plants
TemperatureModule2 | °C | Analog Input | Module Temperature 2 | GMS and HISTORIAN | Only Available at Solar Plants
TemperatureModule3 | °C | Analog Input | Module Temperature 3 | GMS and HISTORIAN | Only Available at Solar Plants
TemperatureModule4 | °C | Analog Input | Module Temperature 4 | GMS and HISTORIAN | Only Available at Solar Plants
TiltAnglePOA | ° | Analog Input | Tilt Angle-POA | GMS and HISTORIAN | Only Available at Solar Plants
IrradianceGHI | W/m^2 | Analog Input | Irradiance GHI | GMS and HISTORIAN | Only Available at Solar Plants
IrradiancePOA | W/m^2 | Analog Input | Irradiance POA | GMS and HISTORIAN | Only Available at Solar Plants
PressureBarometric | hPa | Analog Input | Barometric Pressure | GMS and HISTORIAN | Only Available at Solar Plants
AirDensity | Kg/m^3 | Analog Input | Air density from Met Station or calculation based on pressure, temperature, and humidity measured from Met station | GMS and HISTORIAN | Only Available at Wind Plants
WindDirectionHubHeight | ° | Analog Input | Wind Direction at Hub Height | GMS and HISTORIAN | Only Available at Wind Plants
WindDirectionHeight2 | ° | Analog Input | Wind Direction at Height 2 (Optional) | GMS and HISTORIAN | Only Available at Wind Plants
WindDirectionHeight3 | ° | Analog Input | Wind Direction at Height 3 (Optional) | GMS and HISTORIAN | Only Available at Wind Plants
WindSpeedHubHeight | m/s | Analog Input | Wind Speed at Hub Height | GMS and HISTORIAN | Only Available at Wind Plants
WindSpeedHeight2 | m/s | Analog Input | Wind Speed at Height 2 (Optional) | GMS and HISTORIAN | Only Available at Wind Plants
WindSpeedHeight3 | m/s | Analog Input | Wind Speed at Height 3 (Optional) | GMS and HISTORIAN | Only Available at Wind Plants
PressureBarometric | mbar | Analog Input | Barometric Pressure | GMS and HISTORIAN | Only Available at Wind Plants

## Analog IO (Axion)
Attribute Name | Units | Point Type | Description | Notes | Required In List
|  | Analog Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2 | HISTORIAN

## Discrete IO (DPAC)
Attribute Name | Units | Point Type | Description | Notes | Required In List
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2 | HISTORIAN
Use this template for any SEL DPACs

## Breaker Relay
Attribute Name | Units | Point Type | Description | Required In List | Notes
CommStatus | 0 = Offline, 1 = Online | Binary Input | Communication Status | GMS and HISTORIAN | This should be the SEL_POU.Offline point in the relay inverted
RelayEnabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | GMS and HISTORIAN | This should be the SEL.FM_INST_EN point in the relay
SoftwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_SALARM in the relay
HardwareAlarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | GMS and HISTORIAN | This should be the SEL.FM_INST_HALARM in the relay
LowSF6Lockout | 0 = Normal, 1 = Lockout | Binary Input | Low SF6 Lockout | GMS and HISTORIAN
TRIPRelayTrip | 0 = Normal, 1 = Trip | Binary Input | Relay Trip signal, Should stay high until the fault conditions are cleared | GMS and HISTORIAN
50InstantaneousOCTrip | 0 = Normal, 1 = Trip | Binary Input | 50 Instantaneous OC Trip, Should stay high until the fault conditions are cleared | GMS and HISTORIAN
51TimeDelayOCTrip | 0 = Normal, 1 = Trip | Binary Input | 51 Time Delay OC Trip, , Should stay high until the fault conditions are cleared | GMS and HISTORIAN
81FrequencyTrip | 0 = Normal, 1 = Trip | Binary Input | 81FrequencyTrip, , Should stay high until the fault conditions are cleared | GMS and HISTORIAN
#_TC1TripCoilMonitorAlarm | 0=Normal, 1=Alarm | Binary Input | TC1 TripCoilMonitorAlarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_TC2TripCoilMonitorAlarm | 0=Normal, 1=Alarm | Binary Input | TC2 TripCoilMonitorAlarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_LockOutStatus | 0=Normal, 1=Trip | Binary Input | 86BFStatus | GMS and HISTORIAN | Replace # with LOR name from one line (i.e. 86T1)
#_BreakerFailInitiate | 0=Normal, 1=Activated | Binary Input | BreakerFailInitiate | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Breaker Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | GMS and HISTORIAN | Invert any breakers where 0=Closed, typical of B contacts. If it is a 3 pole breaker logical OR them for a single status. Replace # with breaker name from one line (i.e. 52F1)
#_Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Loss Of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Loss Of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
#_Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | GMS and HISTORIAN | Replace # with breaker name from one line (i.e. 52F1)
RealPowerAC | MW | Analog Input | AC Real Power | GMS and HISTORIAN
ReactivePower | MVAR | Analog Input | AC Reactive Power | GMS and HISTORIAN
PowerFactor | Unitless | Analog Input | Power Factor | GMS and HISTORIAN
VoltageAB | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageBC | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
VoltageCA | KV | Analog Input | Phase-Phase Voltages | GMS and HISTORIAN
CurrentA | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentB | A | Analog Input | Phase Currents | GMS and HISTORIAN
CurrentC | A | Analog Input | Phase Currents | GMS and HISTORIAN
Frequency | Hz | Analog Input | Frequency | GMS and HISTORIAN
RealPowerA | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerB | MW | Analog Input | Phase Power | GMS and HISTORIAN
RealPowerC | MW | Analog Input | Phase Power | GMS and HISTORIAN
VoltageAN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageBN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
VoltageCN | KV | Analog Input | L-N Phase Voltages | GMS and HISTORIAN
ApparentPowerA | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerB | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
ApparentPowerC | MVA | Analog Input | Phase Apparent Power | GMS and HISTORIAN
PowerFactorA | Unitless | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorB | Unitless | Analog Input | Phase Power Factor | GMS and HISTORIAN
PowerFactorC | Unitless | Analog Input | Phase Power Factor | GMS and HISTORIAN
EnergyReceived | MWh | Accumulator | Energy Received | GMS and HISTORIAN
EnergyDelivered | MWh | Accumulator | Energy Delivered | GMS and HISTORIAN
ReactiveEnergyReceived | MVARh | Accumulator | Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyDelivered | MVARh | Accumulator | Reactive Energy Delivered | GMS and HISTORIAN
EnergyReceivedA | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyReceivedB | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyReceivedC | MWh | Accumulator | Phase Energy Received | GMS and HISTORIAN
EnergyDeliveredA | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
EnergyDeliveredB | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
EnergyDeliveredC | MWh | Accumulator | Phase Energy Delivered | GMS and HISTORIAN
ReactiveEnergyReceivedA | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedB | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyReceivedC | MVARh | Accumulator | Phase Reactive Energy Received | GMS and HISTORIAN
ReactiveEnergyDeliveredA | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredB | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN
ReactiveEnergyDeliveredC | MVARh | Accumulator | Phase Reactive Energy Delivered | GMS and HISTORIAN

## Annunciator
Attribute Name | Units | Point Type | Description | Notes | Required In List
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the Annunciator's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2 | HISTORIAN
Use this template for any SEL DPACs

## Inverter
Attribute Name | Units | Point Type | Description | Required In List | Notes
CurrentA | A | Analog Input | A Phase Current | HISTORIAN
CurrentB | A | Analog Input | B Phase Current | HISTORIAN
CurrentC | A | Analog Input | C Phase Current | HISTORIAN
VoltageBus | KV | Analog Input | Bus Voltage | HISTORIAN
ApparentPower | KVA | Analog Input | Apparent Power | HISTORIAN
Frequency | Hz | Analog Input | Frequency | HISTORIAN
PowerFactor | Positive = Leading, Negative = Lagging | Analog Input | Power Factor | HISTORIAN
ReactivePower | KVAR | Analog Input | Reactive Power | HISTORIAN
VoltageAB | KV | Analog Input | Voltage A-B | HISTORIAN
VoltageAN | KV | Analog Input | Voltage A-N | HISTORIAN
VoltageBC | KV | Analog Input | Voltage B-C | HISTORIAN
VoltageBN | KV | Analog Input | Voltage B-N | HISTORIAN
VoltageCA | KV | Analog Input | Voltage C-A | HISTORIAN
VoltageCN | KV | Analog Input | Voltage C-N | HISTORIAN
RealPowerSetpoint | KW | Analog Input | Real Power Setpoint | HISTORIAN
ReactivePowerSetpoint | KVAR | Analog Input | Reactive Power Setpoint | HISTORIAN
TemperatureAmbient | °C | Analog Input | Ambient Temperature | HISTORIAN
Fault | NA | Analog Input | Inverter Fault | HISTORIAN | Last in Integer value of the Fault code
RealPowerAC | kW | Analog Input | Real Power-AC | GMS and HISTORIAN
OperatingState | NA | Analog Input | Inverter Operating State | GMS and HISTORIAN | Last in Integer value of the Operating state code
Start | Latch On | Binary Output | Start | GMS
Stop | Latch On | Binary Output | Stop | GMS
Reset | Latch On | Binary Output | Reset | GMS
KW Setpoint | KW | Analog Output | KW Setpoint Override | GMS

## Inverter Module
Attribute Name | Units | Point Type | Description | Required In List | Notes
ModuleStatus | 0 = Offline, 1 = Online | Binary Input | Status | HISTORIAN
TemperatureAmbient | °C | Analog Input | Temperature-Ambient | HISTORIAN
CurrentA | A | Analog Input | Current Phase A | HISTORIAN
CurrentB | A | Analog Input | Current Phase A | HISTORIAN
CurrentC | A | Analog Input | Current Phase A | HISTORIAN
EnergyDelivered | Kwh | Analog Input | Real Energy Delivered by the Module | HISTORIAN
ReactiveEnergy | KVarh | Analog Input | Reactive Energy Delivered | HISTORIAN
ReactivePower | KVAR | Analog Input | Reactive power | HISTORIAN
RealPowerAC | KW | Analog Input | Real Power | HISTORIAN
TemperatureIGBTR1 | °C | Analog Input | Temperature of IGBT R1 | HISTORIAN
TemperatureIGBTR2 | °C | Analog Input | Temperature of IGBT R2 | HISTORIAN
TemperatureIGBTR3 | °C | Analog Input | Temperature of IGBT R3 | HISTORIAN
TemperatureIGBTS1 | °C | Analog Input | Temperature of IGBT S1 | HISTORIAN
TemperatureIGBTS2 | °C | Analog Input | Temperature of IGBT S2 | HISTORIAN
TemperatureIGBTS3 | °C | Analog Input | Temperature of IGBT S3 | HISTORIAN
TemperatureIGBTT1 | °C | Analog Input | Temperature of IGBT T1 | HISTORIAN
TemperatureIGBTT2 | °C | Analog Input | Temperature of IGBT T2 | HISTORIAN
TemperatureIGBTT3 | °C | Analog Input | Temperature of IGBT T3 | HISTORIAN
TemperatureMax | °C | Analog Input | Maximum Temperature | HISTORIAN

## ERCOT
Attribute Name | Units | Point Type | Description | Required In List | Notes
Line MW | MW | Analog Input | High-Side transmission Line at the Resource MW (not TDSP POI) - positive value when real power exporting to the grid | GMS and Historian | See TPS_SCADA_Point_Req_ERCOT_WGR for more information
Line MVAR | MVAR | Analog Input | High-Side transmission Line at the Resource MVAR (not TDSP POI) - positive value when reactive power exporting to the grid | GMS and Historian
Unit # Gen Gross MW | MW | Analog Input | Total Turbine-only Gross measured to include the collector system per modeled unit/transformer, only positive values shown to ERCOT with a floor of 0 MW | GMS and Historian
Unit # Gen Gross MVAR | MVAR | Analog Input | Total Turbine-only Gross measured to include the collector system per modeled unit/transformer | GMS and Historian
Unit # Load MW | MW | Analog Input | Represents any real power consumption by the WGR per modeled transformer, and shows a positive value when load is present and '0' otherwise | GMS and Historian
Unit # Load MVAR | MVAR | Analog Input | Represents any reactive power consumption by the WGR per modeled transformer, and shows '0' when there is '0' MW load or actual value when real power load is present | GMS and Historian
Unit # Gen Net MW | MW | Analog Input | Net MW measured at the high-side including capacitive/reactive devices per modeled Generation unit/transformer, only positive values shown to ERCOT with a floor of 0 MW | GMS and Historian
Unit # Gen Net MVAR | MVAR | Analog Input | Net MVAR measured at the high-side including capacitive/reactive devices per modeled Generation unit/transformer | GMS and Historian
Unit # High Side Real Power | MW | Analog Input | Unit High-Side transformer values inverse polarity of Net MW per modeled transformer | GMS and Historian
Unit # High Side Reactive Power | MVAR | Analog Input | Unit High-Side transformer values inverse polarity of Net MVAR per modeled transformer | GMS and Historian
Unit # High Side Voltage VAB | KV | Analog Input | Line-to-line KV High-side of GSU transformer per modeled unit, not at the Line | GMS and Historian
Unit # High Side Voltage VBC | KV | Analog Input | Line-to-line KV High-side of GSU transformer per modeled unit, not at the Line | GMS and Historian
Unit # High Side Voltage VCA | KV | Analog Input | Line-to-line KV High-side of GSU transformer per modeled unit, not at the Line | GMS and Historian
Unit # Low Side Voltage VAB | KV | Analog Input | Line-to-line KV Low-side of GSU transformer / collector bus per modeled unit/transformer | GMS and Historian
Unit # Low Side Voltage VBC | KV | Analog Input | Line-to-line KV Low-side of GSU transformer / collector bus per modeled unit/transformer | GMS and Historian
Unit # Low Side Voltage VCA | KV | Analog Input | Line-to-line KV Low-side of GSU transformer / collector bus per modeled unit/transformer | GMS and Historian
Unit # RTPP | MW | Analog Input | Real Time Power Potential | GMS and Historian
Unit # Wind Speed | m/s | Analog Input | MPH or MPS, whatever is available per modeled unit/transformer. QSE will convert/send to ERCOT as MPH as required if necessary | GMS and Historian
Unit # Wind Direction | degrees | Analog Input | Degrees from North per modeled unit/transformer | GMS and Historian
Unit # Barometric Pressure | mpa | Analog Input | Millibars per modeled unit/transformer | GMS and Historian
Unit # Ambient Temperature | degrees celcius | Analog Input | Degrees Celcius per modeled unit/transformer | GMS and Historian
Unit # Turbines Online | Number | Analog Input | Total online/available to generate turbines per modeled unit/transformer - Three Turbine availability points should sum to total turbines. | GMS and Historian
Unit # Turbines Offline | Number | Analog Input | Total offline turbnes per modeled unit- Three Turbine availability points should sum to total turbines. | GMS and Historian
Unit # Turbines Unknown | Number | Analog Input | Total turbines in an unknown status - Three Turbine availability points should sum to total turbines and not exceed RARF values. | GMS and Historian
Capacitor Bank # MVAR | MVAR | Analog Input | Individual MVAR values per modeled Cap Bank | GMS and Historian
Unit # Generator Breaker Group | 0=Open, 1=Closed | Binary Input | Per modeled unit - psuedo-aggragate of all actual feeder breakers; if any one is CLOSED, AGG is CLOSED (even this still presents issues upon Part 1 & 2) | GMS and Historian
Unit # AVR Group | 0 = Disabled, 1 = Enabled | Binary Input | At transformer (one per registered unit/transformer) | GMS and Historian
CAP Bank Breaker # | 0=Open, 1=Closed | Binary Input | RARF modeled switchyard BREAKER status | GMS and Historian
CAP Bank Switch # | 0=Open, 1=Closed | Binary Input | RARF modeled switchyard SWITCH status | GMS and Historian

## Wartsila ESS Unit
Attribute Name | Units | Point Type | Description | Required In List | Notes
ACRealPower | KW | Analog Input | AC Real Power | GMS and HISTORIAN
ACReactivePower | KW | Analog Input | AC Reactive Power | GMS and HISTORIAN
BatteryEffectiveSOC | % | Analog Input | Battery Effective SOC | GMS and HISTORIAN
BatteryAverageSOC | % | Analog Input | Battery Average SOC | GMS and HISTORIAN
ChargePowerLimit | KW | Analog Input | Charge Power Limit | GMS and HISTORIAN
DischargePowerLimit | KW | Analog Input | Discharge Power Limit | GMS and HISTORIAN
ChargeableEnergy | KWh | Analog Input | Chargeable Energy | GMS and HISTORIAN
DischarableEnergy | KWh | Analog Input | Discharable Energy | GMS and HISTORIAN
OperationCodeIndicator | N/A | Analog Input | 0 - No operation; 1 - Target SOC | GMS and HISTORIAN
BatteryDCBusVoltage | V | Analog Input | Battery DC Bus Voltage | GMS and HISTORIAN
BatteryDCBusCurrent | Amp | Analog Input | Battery DC Bus Current | GMS and HISTORIAN
NumberofBatteryStringConnectedtoDCBus | N/A | Analog Input | Number of Battery String Connected to DC Bus | GMS and HISTORIAN
SOH | % | Analog Input | SOH | GMS and HISTORIAN
LockIndicator | 0 - Unlocked; 1 - Locked | Binary Input | ESS Unit Lock Indicator | GMS and HISTORIAN
RunIndicator | 0 - Off; 1 - On | Binary Input | ESS Unit Run Indicator | GMS and HISTORIAN
SiteParticipationIndicator | 0 - Unit is not participating in site level operation; 1 - Unit is participating in site level operation | Binary Input | ESS Unit Site Participation Indicator | GMS and HISTORIAN
WarningIndicator | 0 - No ESS unit warning; 1 - ESS unit warning present | Binary Input | ESS Unit Warning Indicator | GMS and HISTORIAN
FaultIndicator | 0 - No ESS unit fault; 1 - ESS unit fault present | Binary Input | ESS Unit Fault Indicator | GMS and HISTORIAN
Setpoint | KW | Analog Output | ESS Unit P Set Point | GMS
LockControl | 0 - Unlocked; 1 - Locked | Binary Output | ESS Unit Lock Control | GMS
SiteParticipationControl | 0 - Detach ESS unit from participating in site level operation 1 - Attach ESS Unit to participate in site level operation | Binary Output | ESS Unit Site Participation Control | GMS
FaultReset | Send 1 to reset ESS unit fault | Binary Output | ESS Unit Fault Reset | GMS
RunControl | 0 - Stop; 1 - Start. This command is only for manually operating the ESS Unit. | Binary Output | ESS Unit Run Control | GMS
EnergyChargedToDate | KWh | Accumulator | Energy Charged To Date | GMS and HISTORIAN
EnergyDischargedToDate | KWh | Accumulator | Energy Discharged To Date | GMS and HISTORIAN

## BESS BOP (OPC UA)
Attribute Name | Units | Point Type | Description | Required In List
FirePanelFireAlarm |  | Analog Input | Fire Alarm | HISTORIAN
FirePanelTroubleAlarm |  | Analog Input | Fire Alarm Panel Trouble | HISTORIAN
TemperatureInletWater1 | °C | Analog Input | Chiller Inlet Water Temperature | HISTORIAN
TemperatureOutletWater1 | °C | Analog Input | Chiller Outlet Water Temperature | HISTORIAN
TemperatureInletWater2 | °C | Analog Input | Chiller Inlet Water Temperature | HISTORIAN
TemperatureOutletWater2 | °C | Analog Input | Chiller Outlet Water Temperature | HISTORIAN
HasCriticalFault |  | Analog Input | Has Critical Fault | HISTORIAN | Wartsila-only
HasFault |  | Analog Input | Has Fault | HISTORIAN | Wartsila-only
TemperatureChillerSupplyWaterAverage | °C | Analog Input | Average Chiller Supply Water Temperature | HISTORIAN | Wartsila-only
HasAlarm |  | Analog Input | Has Alarm | HISTORIAN | Wartsila-only
HasFireFault |  | Analog Input | Has Fire Fault | HISTORIAN | Wartsila-only
HasFireWarning |  | Analog Input | Has Fire Warning | HISTORIAN | Wartsila-only
HasWarning |  | Analog Input | Has Warning | HISTORIAN | Wartsila-only
Chiller#Warn |  | Analog Input | Chiller Has Warning | HISTORIAN | Wartsila-only
Chiller#Alarm |  | Analog Input | Chiller Has Alarm | HISTORIAN | Wartsila-only
Chiller#Fault |  | Analog Input | Chiller Has Fault | HISTORIAN | Wartsila-only
Chiller#CritFault |  | Analog Input | Chiler Has Critical Fault | HISTORIAN | Wartsila-only
HVACWarn |  | Analog Input | HVAC Has Warning | HISTORIAN | Wartsila-only
HVACAlarm |  | Analog Input | HVAC Has Alarm | HISTORIAN | Wartsila-only
HVACFault |  | Analog Input | HVAC Has fault | HISTORIAN | Wartsila-only
HVACCritFault |  | Analog Input | HVAC Has Critical Fault | HISTORIAN | Wartsila-only
Humidity | % | Analog Input | Humidity | HISTORIAN | Wartsila-only
HVACOCTEHitempAlarm |  | Digital Input | OCTE HVAC Hi-temp Alarm | HISTORIAN | Fluence-only
HVACOCTELotempAlarm |  | Digital Input | OCTE HVAC Lo-temp Alarm | HISTORIAN | Fluence-only
HVACCube01IndoorTemp | °C | Analog Input | Cube HVAC Environment Temp | HISTORIAN | Fluence-only
HVACCube01Humidity | % | Analog Input | Cube Humidity | HISTORIAN | Fluence-only
ChillerPressureDropActive |  | Digital Input | Chiller Pressure Drop Active | HISTORIAN | Fluence-only
ChillerPressureDropActiveLocation |  | Digital Input | Chiller Pressure Drop Active Location | HISTORIAN | Fluence-only
ChillerFaultActive |  | Digital Input | Chiller Fault Active | HISTORIAN | Fluence-only
ChillerFaultActiveLocation |  | Digital Input | Chiller Fault Active Location | HISTORIAN | Fluence-only
CoreFStopActive |  | Digital Input | Core F-Stop Active | HISTORIAN | Fluence-only
FSSSmokeDetectActive |  | Digital Input | FSS Smoke Detect Active | HISTORIAN | Fluence-only
FSSFirePanelTroubleActive |  | Digital Input | FSS Fire Panel Trouble Active | HISTORIAN | Fluence-only
FSSCODetectedActive |  | Digital Input | FSS CO Detected Active | HISTORIAN | Fluence-only
Chiller##InletPressure |  | Digital Input | Chiller Inlet Water Pressure | HISTORIAN | Fluence-only
Chiller##OutletPressure |  | Digital Input | Chiller Outlet Water Pressure | HISTORIAN | Fluence-only
Chiller##WaterReplenishmentAlarm |  | Digital Input | Chiller 01 Water Replenishment Alarm | HISTORIAN | Fluence-only

## BESS Inverter (OPC UA)
Attribute Name | Units | Point Type | Description | Required In List
CurrentA | A | Analog Input | Phase A Current | HISTORIAN
CurrentB | A | Analog Input | Phase B Current | HISTORIAN
CurrentC | A | Analog Input | Phase C Current | HISTORIAN
VoltageBus | V | Analog Input | Low Voltage AC | HISTORIAN
ReactivePower | MVAr | Analog Input | Reactive Power | HISTORIAN
RealPowerAC | MW | Analog Input | Real Power AC | HISTORIAN
ApparentPower | MVA | Analog Input | Apparent Power | HISTORIAN
CurrentDCInput | A | Analog Input | DC Current | HISTORIAN
VoltageDCInput | V | Analog Input | DC Voltage | HISTORIAN
PowerFactor |  | Analog Input | Power Factor | HISTORIAN
VoltageAB | V | Analog Input | Grid Voltage A-B | HISTORIAN
VoltageBC | V | Analog Input | Grid Voltage B-C | HISTORIAN
VoltageCA | V | Analog Input | Grid Voltage C-A | HISTORIAN
RealPowerSetpoint | MW | Analog Input | Real Power Setpoint | HISTORIAN
ReactivePowerSetpoint | MVAr | Analog Input | Reactive Power Setpoint | HISTORIAN
Fault |  | Analog Input | Inverter Fault | HISTORIAN
OperatingState |  | Analog Input | Operating State | HISTORIAN
Frequency | Hz | Analog Input | Frequency of the inverter | HISTORIAN
ESSExcludedAlarm |  | Digital Input | ESS is excluded from control loop for more than 5 minutes | HISTORIAN
ESSExcludedBasis |  | Analog Input | Reason why ESS excluded from control loop (Numerically coded) | HISTORIAN
RealPowerMaxLimit | MW | Analog Input | Max Real Power Limit | HISTORIAN | Wartsila-only
ReactivePowerMaxLimit | MVAr | Analog Input | Max Reactive Power Limit | HISTORIAN | Wartsila-only
RealPowerMaxDerated | MW | Analog Input | Derated Maximum Real Power | HISTORIAN | Wartsila-only
ReactivePowerMaxDerated | MVAr | Analog Input | Derated Maximum Reactive Power | HISTORIAN | Wartsila-only
PowerACChargeableLimit | kW | Analog Input | AC Chargeable Power Limit | HISTORIAN | Wartsila-only
EnergyACCharged | kWh | Analog Input | AC Charged Energy | HISTORIAN | Wartsila-only
EnergyACDischarged | kWh | Analog Input | AC Discharged Energy | HISTORIAN | Wartsila-only
PowerACDischargeLimit | kW | Analog Input | AC Dischargeable Power Limit | HISTORIAN | Wartsila-only
EnergyACChargeableTotal | kWh | Analog Input | Total AC Chargeable Energy | HISTORIAN | Wartsila-only
EnergyChargeableTotal | kWh | Analog Input | Total Chargeable Energy | HISTORIAN | Wartsila-only
EnergyACDischargeabletotal | kWh | Analog Input | Total AC Dischargeable Energy | HISTORIAN | Wartsila-only
EnergyDischargeableTotal | kWh | Analog Input | Total Dischargeable Energy | HISTORIAN | Wartsila-only
RampRateRealPowerEffective | kW/min | Analog Input | Effective Real Power Ramp Rate | HISTORIAN | Wartsila-only
EnergyDCCharged | kWh | Analog Input | DC Charged Energy | HISTORIAN | Wartsila-only
EnergyDCDischarged | kWh | Analog Input | DC Discharged Energy | HISTORIAN | Wartsila-only
PowerDC | kW | Analog Input | DC power | HISTORIAN | Wartsila-only
SOCEffective | % | Analog Input | Effective SOC | HISTORIAN | Wartsila-only
Participating |  | Digital Input | Unit participating in market | HISTORIAN | Wartsila-only
Running |  | Digital Input | Unit Run Status | HISTORIAN | Wartsila-only
Stopped |  | Digital Input | Unit Stop Status | HISTORIAN | Wartsila-only
CanOperate |  | Digital Input | Unit Can Operate | HISTORIAN | Wartsila-only
Alive |  | Digital Input | Heartbeat Alive | HISTORIAN | Wartsila-only
Attach |  | Digital Input | Unit Attached | HISTORIAN | Wartsila-only
Detach |  | Digital Input | Unit Detached | HISTORIAN | Wartsila-only
Lock |  | Digital Input | Unit Locked | HISTORIAN | Wartsila-only
HasAlarm |  | Digital Input | Has Alarm | HISTORIAN | Wartsila-only
CriticalFault |  | Digital Input | Critical Fault | HISTORIAN | Wartsila-only
OwnAlarm |  | Digital Input | Own Alarm | HISTORIAN | Wartsila-only
HasOwnCriticalFault |  | Digital Input | Has Own Critical Fault | HISTORIAN | Wartsila-only
OwnFault |  | Digital Input | Own Fault | HISTORIAN | Wartsila-only
OwnWarning |  | Digital Input | Own Warning | HISTORIAN | Wartsila-only
HasWarning |  | Digital Input | Has Warning | HISTORIAN | Wartsila-only
Locked |  | Digital Input | Locked | HISTORIAN | Wartsila-only
TemperatureIGBTMax | °C | Analog Input | IGBT Max Temperature | HISTORIAN | Wartsila-only
TemperatureACModuleInternal | °C | Analog Input | AC Module internal temperature | HISTORIAN | Wartsila-only
BreakerStatus |  | Digital Input | Breaker Breaker Status | HISTORIAN | Fluence-only
DCSwitchStatus1 |  | Digital Input | DC Switch Status 1 | HISTORIAN | Fluence-only
DCSwitchStatus2 |  | Digital Input | DC Switch Status 2 | HISTORIAN | Fluence-only
DCSwitchStatus3 |  | Digital Input | DC Switch Status 3 | HISTORIAN | Fluence-only
DCSwitchStatus4 |  | Digital Input | DC Switch Status 4 | HISTORIAN | Fluence-only
InvAdmT | °C | Digital Input | Inverter Admission Temperature | HISTORIAN | Fluence-only
MvXfmrTemp1 | °C | Digital Input | MV Transformer Temperatue 1 | HISTORIAN | Fluence-only
MvXfmrTemp2 | °C | Digital Input | MV Transformer Temperatue 2 | HISTORIAN | Fluence-only
MvXfmrTemp3 | °C | Digital Input | MV Transformer Temperatue 3 | HISTORIAN | Fluence-only
EmergencyStopStatus |  | Digital Input | Emergency stop Status | HISTORIAN | Fluence-only
GroundFaultDetected |  | Digital Input | Ground Fault Detected | HISTORIAN | Fluence-only
GroundFaultLocation |  | Digital Input | Ground Fault Location | HISTORIAN | Fluence-only
Heartbeat |  | Digital Input | Inverter Heartbeat | HISTORIAN | Fluence-only
NumberNodesRunning |  | Digital Input | # of Nodes Connected | HISTORIAN | Fluence-only
ReactivePowerChargeCapability | MVAr | Digital Input | Reactive Charge Capb | HISTORIAN | Fluence-only
ReactivePowerDischargeCapability | MVAr | Digital Input | Reactive Discharge Capb | HISTORIAN | Fluence-only
RealPowerChargeCapability | MW | Digital Input | Real Charge Capb | HISTORIAN | Fluence-only
RealPowerDischargeCapability | MW | Digital Input | Real Discharge Capb | HISTORIAN | Fluence-only
Warning |  | Digital Input | SV113-Current Warning | HISTORIAN | Fluence-only
FaultCoreController |  | Digital Input | Core Alarm Status | HISTORIAN | Fluence-only
OperatingStateCoreController |  | Digital Input | Core Current State | HISTORIAN | Fluence-only
WarningCoreController |  | Digital Input | Core Warning Status | HISTORIAN | Fluence-only
SOC | % | Digital Input | Core SOC | HISTORIAN | Fluence-only
SOCOperational | % | Digital Input | Core Operational SOC | HISTORIAN | Fluence-only

## BESS Inverter Module (OPC UA)
Attribute Name | Units | Point Type | Description | Required In List
ReactivePower | MVAR | Analog Input | Module Reactive Power | HISTORIAN
RealPowerAC | MW | Analog Input | Module Real Power | HISTORIAN
CurrentDC | A | Analog Input | Module DC Input Current | HISTORIAN
VoltageDC | V | Analog Input | Module DC Voltage | HISTORIAN
PowerDC | MW | Analog Input | Module DC Power | HISTORIAN
CurrentAC | A | Analog Input | Module AC Current | HISTORIAN
VoltageAC | V | Analog Input | Module AC Voltage | HISTORIAN
Frequency | Hz | Analog Input | Module Frequency | HISTORIAN
PowerFactor |  | Analog Input | Module Power Factor | HISTORIAN
RunningStatus |  | Analog Input | Module Running | HISTORIAN
PowerACChargeLimit | MW | Analog Input | Module Ac Charge Power Limit | HISTORIAN
PowerACDischargeLimit | MW | Analog Input | Module Ac Discharge Power Limit | HISTORIAN
Fault |  | Analog Input | Module Has Fault | HISTORIAN
RealPowerMax | MW | Analog Input | Module Real Power Max | HISTORIAN | Wartsila-only
ReactivePowerMax | MVAr | Analog Input | Module Reactive Power Max | HISTORIAN | Wartsila-only
RealPowerDeratedMax | MW | Analog Input | Module Derated Real Power | HISTORIAN | Wartsila-only
ReactivePowerDeratedMax | MVAr | Analog Input | Module Derated Reactive Power | HISTORIAN | Wartsila-only
HasCriticalFault |  | Digital Input | Module Has Fault | HISTORIAN | Wartsila-only
ChargedWhAC | GWh | Analog Input | Module ac Charged Wh | HISTORIAN | Wartsila-only
DischargedWhAC | GWh | Analog Input | Module ac Discharged Wh | HISTORIAN | Wartsila-only
RealAutomatedDispatch | kW | Analog Input | Module Real Power Setpoint | HISTORIAN | Fluence-only
ReactiveAutomatedDispatch | kVAR | Analog Input | Module Reactive Power Setpoint Dispatch | HISTORIAN | Fluence-only
InvModVoltageAB | V | Analog Input | Inverter Module Voltage AB | HISTORIAN | Fluence-only
InvModVoltageBC | V | Analog Input | Inverter Module Voltage BC | HISTORIAN | Fluence-only
InvModVoltageCA | V | Analog Input | Inverter Module Voltage CA | HISTORIAN | Fluence-only
InvModCurrentA | A | Analog Input | Inverter Module Current A | HISTORIAN | Fluence-only
InvModCurrentB | A | Analog Input | Inverter Module Current B | HISTORIAN | Fluence-only
InvModCurrentC | A | Analog Input | Inverter Module Current C | HISTORIAN | Fluence-only

## BESS DC Bus (OPC UA)
Attribute Name | Units | Point Type | Description | Required In List
RunningStatus |  | Analog Input | RunningStatus | HISTORIAN
VoltageDCBus | V | Analog Input | DC Bus Voltage | HISTORIAN
CurrentDCBus | A | Analog Input | DC Bus Current | HISTORIAN
SOCAverage | % | Analog Input | Average SOC | HISTORIAN
SOHAverage | % | Analog Input | Average SOH | HISTORIAN
CellVoltageMax | V | Analog Input | Max Cell Voltage For DC Bus | HISTORIAN
CellVoltageMin | V | Analog Input | Min Cell Voltage For DC Bus | HISTORIAN
CellVoltageAvg | V | Analog Input | Average Cell Voltage For DC Bus | HISTORIAN
CellTempMax | °C | Analog Input | Max Cell Temperature For DC Bus | HISTORIAN
CellTempMin | °C | Analog Input | Min Cell Temperature For DC Bus | HISTORIAN
CellTempAvg | °C | Analog Input | Average Cell Temperature for DC Bus | HISTORIAN
CurrentChargeLimit | A | Analog Input | Maximum Allowable Charge Current | HISTORIAN
CurrentDischargeLimit | A | Analog Input | Maximum Allowable Discharge Current | HISTORIAN
NumberOfRacksConnected |  | Analog Input | Number of Racks Connected to DC Bus | HISTORIAN
PowerDischargeLimit | KW | Analog Input | Discharge Power Limit | HISTORIAN
PowerChargeLimit | KW | Analog Input | Charge Power Limit | HISTORIAN
PowerDC | kW | Analog Input | DC Real Power | HISTORIAN
EnergyTotalChargeable | kWh | Analog Input | Total Chargeable Energy | HISTORIAN
EnergyTotalDischargeable | kWh | Analog Input | Total Dischargeable Energy | HISTORIAN
RealPower | MW | Analog Input | DC Bus Real Power | HISTORIAN | Wartsila-only
RealPowerSetpoint | MW | Analog Input | DC Bus real Power Setpoint | HISTORIAN | Wartsila-only
RealPowerMaxLimit | MW | Analog Input | DC Bus Real Power Max Limit | HISTORIAN | Wartsila-only
RealPowerDeratedMax | MW | Analog Input | DC Bus Real Power Derated Max | HISTORIAN | Wartsila-only
ChargedWhDC | GWh | Analog Input | DC Bus dc Charged Wh | HISTORIAN | Wartsila-only
DischargedWhDC | GWh | Analog Input | DC Bus dc Discharged Wh | HISTORIAN | Wartsila-only
AllStringsRunning |  | Analog Input | DC Bus all strings running | HISTORIAN | Wartsila-only
SOC | % | Analog Input | DC Bus SOC | HISTORIAN | Wartsila-only
SOCMaxLimit | % | Analog Input | DC Bus max SOC Limit | HISTORIAN | Wartsila-only
SOCMinLimit | % | Analog Input | DC Bus min SOC Limit | HISTORIAN | Wartsila-only
SOCEffective | % | Analog Input | DC Bus Effective SOC | HISTORIAN | Wartsila-only
CanOperate |  | Analog Input | DC Bus Can Operate | HISTORIAN | Wartsila-only
DataQuality |  | String | DC Bus Data Quality | HISTORIAN | Wartsila-only
DataQualityGood |  | Digital Input | DC Bus Data Quality Good | HISTORIAN | Wartsila-only
hasAlarm |  | Digital Input | DC Bus Has Alarm | HISTORIAN | Wartsila-only
hasCriticalFault |  | Digital Input | DC Bus Has Critical Fault | HISTORIAN | Wartsila-only
hasFault |  | Digital Input | DC Bus Has Fault | HISTORIAN | Wartsila-only
hasOwnAlarm |  | Digital Input | DC Bus Has Own Alarm | HISTORIAN | Wartsila-only
hasOwnCriticalFault |  | Digital Input | DC Bus Has Own Critical Fault | HISTORIAN | Wartsila-only
hasOwnFault |  | Digital Input | DC Bus Has Own Fault | HISTORIAN | Wartsila-only
hasOwnWarning |  | Digital Input | DC Bus Has Own Warning | HISTORIAN | Wartsila-only
hasWarning |  | Digital Input | DC Bus Has Warning | HISTORIAN | Wartsila-only
Locked |  | Digital Input | DC Bus Locked | HISTORIAN | Wartsila-only
Participating |  | Digital Input | DC Bus Participating | HISTORIAN | Wartsila-only
Stopped |  | Digital Input | DC Bus Stopped | HISTORIAN | Wartsila-only
CapacityWh | MWh | Analog Input | DC Bus Wh Capacity | HISTORIAN | Wartsila-only
Health |  | Digital Input | DC Bus Health | HISTORIAN | Wartsila-only
Alive |  | Digital Input | DC Bus Alive | HISTORIAN | Wartsila-only
Attach |  | Digital Input | DC Bus Attach | HISTORIAN | Wartsila-only
Detach |  | Digital Input | DC Bus Detach | HISTORIAN | Wartsila-only
Lock |  | Digital Input | DC Bus lock | HISTORIAN | Wartsila-only
RawAvailabilityDaily |  | Analog Input | DC Bus raw Availability Daily | HISTORIAN | Wartsila-only
RawAvailabilityMonthly |  | Analog Input | DC Bus raw Availability Monthly | HISTORIAN | Wartsila-only
RawAvailabilityYearly |  | Analog Input | DC Bus raw Availability Yearly | HISTORIAN | Wartsila-only
BMSWarningWithDegrees |  | Analog Input | MBMU System warning (with degrees) | HISTORIAN | Fluence-only
BMSWarningCurrentOverLimit |  | Digital Input | BMS Current over limit warning | HISTORIAN | Fluence-only
BMSWarningSingleCellVoltageDifference |  | Digital Input | BMS Warning for big voltage difference of single cell | HISTORIAN | Fluence-only
BMSWarningTemperatureDifferenceWithinBank |  | Digital Input | BMS Warning for big temperature difference within bank | HISTORIAN | Fluence-only
BMSWarningSystemOverVoltage |  | Digital Input | BMS System overvoltage warning | HISTORIAN | Fluence-only
BMSWarningSystemUnderVoltage |  | Digital Input | BMS System under voltage warning | HISTORIAN | Fluence-only
BMSWarningCommunications |  | Digital Input | BMS Inner communication warning | HISTORIAN | Fluence-only
BMSWarningCellExtremeTemperature |  | Digital Input | BMS Cell extreme temperature warning | HISTORIAN | Fluence-only
BMSWarningCellExtremeVoltage |  | Digital Input | BMS Cell extreme voltage warning | HISTORIAN | Fluence-only
BMSWarningHeartbeatFault |  | Digital Input | BMS EMS heartbeat fault | HISTORIAN | Fluence-only
BMSWarningInputEStopFault |  | Digital Input | BMS Input ESTOP fault | HISTORIAN | Fluence-only
BMSWarningRacksHVPowerOnFault |  | Digital Input | BMS Racks numbers of high voltage power on fault | HISTORIAN | Fluence-only

## BESS Rack (OPC UA)
Attribute Name | Units | Point Type | Description | Required In List
RunningStatus |  | Digital Input | Running Status | HISTORIAN
VoltageDC | V | Analog Input | DC Voltage | HISTORIAN
CurrentDC | A | Analog Input | DC Current | HISTORIAN
PowerDC | kW | Analog Input | DC Power | HISTORIAN
SOC | % | Analog Input | State of Charge | HISTORIAN
SOH | % | Analog Input | SOH | HISTORIAN
CellVoltageMax | V | Analog Input | Maximum Cell Voltage | HISTORIAN
CellVoltageMin | V | Analog Input | Minimum Cell Voltage | HISTORIAN
CellVoltageAvg | V | Analog Input | Average Cell Voltage | HISTORIAN
CellTemperatureMax | °C | Analog Input | Maximum Cell Temperature | HISTORIAN
CellTemperatureMin | °C | Analog Input | Minimum Cell Temperature | HISTORIAN
CellTemperatureAvg | °C | Analog Input | Average Cell Temperature | HISTORIAN
CurrentChargeLimit | A | Analog Input | DC Charge Current Limit | HISTORIAN
CurrentDischargeLimit | A | Analog Input | DC Discharge Current Limit | HISTORIAN
EnergyChargeable | kWh | Analog Input | Total Chargeable Energy | HISTORIAN
EnergyDischargeable | kWh | Analog Input | Total Dischargeable Energy | HISTORIAN
PowerChargeDCLimit | kW | Analog Input | Charge Power Limit DC | HISTORIAN
PowerDischargeDCLimit | kW | Analog Input | Discharge Power Limit DC | HISTORIAN
ChargedWhDC | MWh | Analog Input | Rack DC Charged Wh | HISTORIAN | Wartsila-only
DischargedWhDC | MWh | Analog Input | Rack DC Discharged Wh | HISTORIAN | Wartsila-only
CapacityWh | kWh | Analog Input | Rack Wh Capacity | HISTORIAN | Wartsila-only
HasCriticalFault |  | Digital Input | Rack Has Critical Fault | HISTORIAN | Wartsila-only
HasFault |  | Digital Input | Rack Has Fault | HISTORIAN | Wartsila-only
HasOwnAlarm |  | Digital Input | Rack Has Own Alarm | HISTORIAN | Wartsila-only
HasOwnCriticalFault |  | Digital Input | Rack Has Own Critical Fault | HISTORIAN | Wartsila-only
HasOwnFault |  | Digital Input | Rack Has Own Fault | HISTORIAN | Wartsila-only
HasOwnWarning |  | Digital Input | Rack Has Own Warning | HISTORIAN | Wartsila-only
HasWarning |  | Digital Input | Rack Has Warning | HISTORIAN | Wartsila-only
PreChargeRelayStatus |  | Digital Input | Modbus address offset 01040 SBMU#1 Precharge relay status | HISTORIAN | Fluence-only
MasterPositiveRelayStatus |  | Digital Input | Modbus address offset 01041 SBMU#1 Master positive relay status | HISTORIAN | Fluence-only
MasterNegativeRelayStatus |  | Digital Input | Modbus address offset 01042 SBMU#1 Master negative relay status | HISTORIAN | Fluence-only
BalanceStatus |  | Digital Input | Modbus address offset 01044 SBMU#1 Balance status | HISTORIAN | Fluence-only
VoltagePositionSingleCellMax | V | Analog Input | Modbus address offset 01072 SBMU#1 Max single cell voltage position | HISTORIAN | Fluence-only
VoltagePositionSingleCellMin | V | Analog Input | Modbus address offset 01073 SBMU#1 Min single cell voltage position | HISTORIAN | Fluence-only
VoltageCellSum | V | Analog Input | Modbus address offset 01079 SBMU#1 Sum of cell voltage | HISTORIAN | Fluence-only
WarningWithDegrees |  | Analog Input | SBMU System warning (with degrees) | HISTORIAN | Fluence-only
WarningOverCurrentCharge |  | Digital Input | SBMU System warning (without degrees) - Charge over-current warning | HISTORIAN | Fluence-only
WarningOverCurrentDischarge |  | Digital Input | SBMU System warning (without degrees) - Discharge over-current warning | HISTORIAN | Fluence-only
WarningCellTemperatureDifference |  | Digital Input | SBMU System warning (without degrees) - Cell temperature difference warning | HISTORIAN | Fluence-only
WarningCellExtremeTemperature |  | Digital Input | SBMU System warning (without degrees) - Cell extreme temperature warning | HISTORIAN | Fluence-only
WarningCellExtremeVoltage |  | Digital Input | SBMU System warning (without degrees) - Cell extreme voltage warning | HISTORIAN | Fluence-only
WarningTotalExtremeVoltage |  | Digital Input | SBMU System warning (without degrees) - Extreme total voltage warning | HISTORIAN | Fluence-only
WarningPowerFault |  | Digital Input | SBMU System warning (without degrees) - Power fault warning | HISTORIAN | Fluence-only
WarningBalanceFault |  | Digital Input | SBMU System warning (without degrees) - Balance fault | HISTORIAN | Fluence-only
WarningInnerCommFaultCCAN |  | Digital Input | SBMU System warning (without degrees) - Inner communication fault(CCAN) | HISTORIAN | Fluence-only
WarningInnerCommFaultSCAN |  | Digital Input | SBMU System warning (without degrees) - Inner communication fault(SCAN) | HISTORIAN | Fluence-only
WarningCurrentSensorAbnormal |  | Digital Input | SBMU System warning (without degrees) - Current sensor abnormal fault | HISTORIAN | Fluence-only
WarningSingleCellVoltageSamplingAbnormal |  | Digital Input | SBMU System warning (without degrees) - Single cell voltage sampling abnormal fault | HISTORIAN | Fluence-only
WarningModuleTemperatureSamplingAbnormal |  | Digital Input | SBMU System warning (without degrees) - Module temperature sampling abnormal fault | HISTORIAN | Fluence-only
WarningHVCircuitOpen |  | Digital Input | SBMU System warning (without degrees) - High voltage circuit open fault | HISTORIAN | Fluence-only
WarningMSDFault |  | Digital Input | SBMU System warning (without degrees) - MSD fault | HISTORIAN | Fluence-only
WarningRackIsolateSwitchFault |  | Digital Input | SBMU System warning (without degrees) - Rack isolate switch fault | HISTORIAN | Fluence-only
WarningRackFuseFault |  | Digital Input | SBMU System warning (without degrees) - Rack fuse fault | HISTORIAN | Fluence-only
WarningOverCurrentExtremeFault |  | Digital Input | SBMU System warning (without degrees) - Fault for extreme over current | HISTORIAN | Fluence-only
WarningCommFaultMCAN |  | Digital Input | SBMU System warning (without degrees) - MCAN communication alarm | HISTORIAN | Fluence-only
WarningPowerCSC |  | Digital Input | SBMU System warning (without degrees) - CSC Power Warning | HISTORIAN | Fluence-only
WarningCurrentSensorPower |  | Digital Input | SBMU System warning (without degrees) - Current sensor Power Warning | HISTORIAN | Fluence-only
WarningContactorCoilAbnormal |  | Digital Input | SBMU System warning (without degrees) - Contactor coil abnormal warning | HISTORIAN | Fluence-only