## Sheet1 (hidden)
Requested, Available
Requested, Not applicable
Requested, Not Available
Not Requested, Available

## 1
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | 10.75.32.2 |  | DNP Server | 10.75.32.2
DNP Server Port# | 20001 |  | DNP Server Port# | 20010 (PROD); 20011 (QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 1 |  | RTAC DNP Server address | 1
| Data Type | DNP Event Class | Event Obj/Var | Static Obj/Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30/5
Digitals | Status with Flags | 1 | 2/2 | 1/2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20/1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband of 0.01 for all points except 0.001 for Frequency and Power Factor
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 1 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 0 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 1 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 2 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 3 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 4 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 5 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 6 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 7 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 8 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 9 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 10 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 11 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 12 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 13 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 14 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit 1 MW Setpoint Feedback | 15 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 16 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 17 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 18 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 19 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 20 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit 1 MW Setpoint Feedback | 21 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 22 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 23 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 24 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 25 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 26 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Frequency | PPC |  | BESS AC Frequency Measured at Plant Interconnect | 27 | Hz | Not Requested-Available | 56 | 64 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS MV Voltage | PPC |  | BESS AC Medium Voltage Measured at Plant Interconnect | 28 | V | Not Requested-Available | 210000 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Meter Real Power | PPC |  | BESS Site Real Power Measured at Plant Interconnect | 29 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Meter Reactive Power | PPC |  | BESS Site Reactive Power Measured at Plant Interconnect | 30 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Aux Meter Real Power | PPC |  | BESS Site Auxiliary Real Power Measured by Aux Meter | 31 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Aux Meter Reactive Power | PPC |  | BESS Site Auxiliary Reactive Power Measured by Aux Meter | 32 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Calculated Real Power | PPC |  | BESS Site Sum of real powers from all ESS units | 33 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Calculated Reactive Power | PPC |  | BESS Site Sum of reactive powers from all ESS units | 34 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Effective SOC | PPC |  | BESS Site Effective SOC | 35 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Average SOC | PPC |  | BESS Site Average SOC | 36 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Charge Power Limit | PPC |  | BESS Site Charge Power Limit | 37 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Discharge Power Limit | PPC |  | BESS Site Discharge Power Limit | 38 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Chargable Energy | PPC |  | BESS Site Chargable Energy | 39 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Dischargable Energy | PPC |  | BESS Site Discharable Energy | 40 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Minimum Charge Time | PPC |  | BESS Site Minimum Charge Time | 41 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Maximum Charge Time | PPC |  | BESS Site Maximum Charge Time | 42 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Charge Ramp Rate | PPC |  | BESS Site Charge Ramp Rate | 43 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Minimum Discharge Time | PPC |  | BESS Site Minimum Discharge Time | 44 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Maximum Discharge Time | PPC |  | BESS Site Maximum Discharge Time | 45 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Discharge Ramp Rate | PPC |  | BESS Site Discharge Ramp Rate | 46 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Operation Code Indicator | PPC |  | BESS Site Operation Code Indicator | 47 | 0 - No operation; 1 - Target SOC; 2 - External P/Q Singnale Handling. 3 - Automomous Frequency-Watt. Indicator number to operation mapping is fully customizable according to project requirements | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Number Of Units Idle | PPC |  | BESS Site Number of ESS Units in Idle state | 48 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Number Of Units Discharging | PPC |  | BESS Site Number of ESS Units Discharging | 49 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Number Of Units Charging | PPC |  | BESS Site Number of ESS Units Charging | 50 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS PV Meter Real Power | PPC |  | BESS Site PV Real Power | 51 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS PV Meter Reactive Power | PPC |  | BESS Site PV Reactive Power | 52 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 53 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 54 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 55 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 56 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 57 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 58 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 59 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 60 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 61 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 62 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 63 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 64 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Average Temperature | PPC |  | BESS Site BOP Temperature | 65 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Average Humidity | PPC |  | BESS Site BOP Humidity | 66 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 67 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 68 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 69 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 70 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 71 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 72 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 73 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 74 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 75 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 76 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 77 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 78 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Average Temperature | PPC |  | BESS Site BOP Temperature | 79 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Average Humidity | PPC |  | BESS Site BOP Humidity | 80 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 81 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 82 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 83 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 84 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 85 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 86 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 87 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 88 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 89 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 90 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 91 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 92 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Average Temperature | PPC |  | BESS Site BOP Temperature | 93 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Average Humidity | PPC |  | BESS Site BOP Humidity | 94 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 95 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 96 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 97 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 98 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 99 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 100 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 101 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 102 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 103 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 104 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 105 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 106 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Average Temperature | PPC |  | BESS Site BOP Temperature | 107 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Average Humidity | PPC |  | BESS Site BOP Humidity | 108 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 109 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 110 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 111 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 112 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 113 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 114 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 115 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 116 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 117 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 118 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 119 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 120 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Average Temperature | PPC |  | BESS Site BOP Temperature | 121 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Average Humidity | PPC |  | BESS Site BOP Humidity | 122 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 123 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 124 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 125 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 126 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 127 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 128 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 129 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 130 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 131 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 132 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 133 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 134 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Average Temperature | PPC |  | BESS Site BOP Temperature | 135 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Average Humidity | PPC |  | BESS Site BOP Humidity | 136 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 137 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 138 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 139 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 140 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 141 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 142 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 143 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 144 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 145 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 146 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 147 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 148 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Average Temperature | PPC |  | BESS Site BOP Temperature | 149 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Average Humidity | PPC |  | BESS Site BOP Humidity | 150 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 151 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 152 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 153 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 154 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 155 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 156 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 157 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 158 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 159 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 160 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 161 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 162 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Average Temperature | PPC |  | BESS Site BOP Temperature | 163 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Average Humidity | PPC |  | BESS Site BOP Humidity | 164 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 165 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 166 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 167 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 168 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 169 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 170 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 171 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 172 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 173 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 174 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 175 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 176 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Average Temperature | PPC |  | BESS Site BOP Temperature | 177 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Average Humidity | PPC |  | BESS Site BOP Humidity | 178 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 179 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 180 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 181 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 182 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 183 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 184 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 185 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 186 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 187 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 188 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 189 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 190 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Average Temperature | PPC |  | BESS Site BOP Temperature | 191 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Average Humidity | PPC |  | BESS Site BOP Humidity | 192 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 193 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 194 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 195 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 196 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 197 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 198 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 199 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 200 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 201 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 202 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 203 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 204 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Average Temperature | PPC |  | BESS Site BOP Temperature | 205 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Average Humidity | PPC |  | BESS Site BOP Humidity | 206 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 207 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 208 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 209 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 210 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 211 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 212 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 213 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 214 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 215 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 216 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 217 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 218 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Average Temperature | PPC |  | BESS Site BOP Temperature | 219 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Average Humidity | PPC |  | BESS Site BOP Humidity | 220 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 221 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 222 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 223 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 224 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 225 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 226 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 227 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 228 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 229 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 230 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 231 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 232 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Average Temperature | PPC |  | BESS Site BOP Temperature | 233 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Average Humidity | PPC |  | BESS Site BOP Humidity | 234 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 235 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 236 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 237 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 238 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 239 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 240 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 241 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 242 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 243 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 244 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 245 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 246 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Average Temperature | PPC |  | BESS Site BOP Temperature | 247 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Average Humidity | PPC |  | BESS Site BOP Humidity | 248 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 249 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 250 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 251 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 252 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 253 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 254 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 255 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 256 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 257 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 258 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 259 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 260 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Average Temperature | PPC |  | BESS Site BOP Temperature | 261 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Average Humidity | PPC |  | BESS Site BOP Humidity | 262 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 263 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 264 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 265 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 266 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 267 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 268 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 269 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 270 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 271 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 272 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 273 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 274 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Average Temperature | PPC |  | BESS Site BOP Temperature | 275 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Average Humidity | PPC |  | BESS Site BOP Humidity | 276 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 277 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 278 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 279 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 280 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 281 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 282 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 283 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 284 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 285 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 286 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 287 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 288 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Average Temperature | PPC |  | BESS Site BOP Temperature | 289 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Average Humidity | PPC |  | BESS Site BOP Humidity | 290 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 291 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 292 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 293 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 294 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 295 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 296 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 297 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 298 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 299 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 300 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 301 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 302 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Average Temperature | PPC |  | BESS Site BOP Temperature | 303 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Average Humidity | PPC |  | BESS Site BOP Humidity | 304 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 305 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 306 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 307 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 308 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 309 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 310 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 311 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 312 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 313 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 314 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 315 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 316 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Average Temperature | PPC |  | BESS Site BOP Temperature | 317 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Average Humidity | PPC |  | BESS Site BOP Humidity | 318 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 319 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 320 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 321 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 322 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 323 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 324 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 325 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 326 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 327 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 328 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 329 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 330 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Average Temperature | PPC |  | BESS Site BOP Temperature | 331 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Average Humidity | PPC |  | BESS Site BOP Humidity | 332 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 2 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 333 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 334 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 335 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 336 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 337 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 338 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 339 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 340 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 341 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 342 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 343 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 344 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 345 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 346 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 347 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit 2 MW Setpoint Feedback | 348 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 349 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 350 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 351 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 352 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 353 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit 2 MW Setpoint Feedback | 354 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 355 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 356 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 357 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 358 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 359 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Frequency | PPC |  | BESS AC Frequency Measured at Plant Interconnect | 360 | Hz | Not Requested-Available | 56 | 64 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS MV Voltage | PPC |  | BESS AC Medium Voltage Measured at Plant Interconnect | 361 | V | Not Requested-Available | 210000 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Meter Real Power | PPC |  | BESS Site Real Power Measured at Plant Interconnect | 362 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Meter Reactive Power | PPC |  | BESS Site Reactive Power Measured at Plant Interconnect | 363 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Aux Meter Real Power | PPC |  | BESS Site Auxiliary Real Power Measured by Aux Meter | 364 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Aux Meter Reactive Power | PPC |  | BESS Site Auxiliary Reactive Power Measured by Aux Meter | 365 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Calculated Real Power | PPC |  | BESS Site Sum of real powers from all ESS units | 366 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Calculated Reactive Power | PPC |  | BESS Site Sum of reactive powers from all ESS units | 367 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Effective SOC | PPC |  | BESS Site Effective SOC | 368 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Average SOC | PPC |  | BESS Site Average SOC | 369 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Charge Power Limit | PPC |  | BESS Site Charge Power Limit | 370 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Discharge Power Limit | PPC |  | BESS Site Discharge Power Limit | 371 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Chargable Energy | PPC |  | BESS Site Chargable Energy | 372 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Dischargable Energy | PPC |  | BESS Site Discharable Energy | 373 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Minimum Charge Time | PPC |  | BESS Site Minimum Charge Time | 374 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Maximum Charge Time | PPC |  | BESS Site Maximum Charge Time | 375 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Charge Ramp Rate | PPC |  | BESS Site Charge Ramp Rate | 376 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Minimum Discharge Time | PPC |  | BESS Site Minimum Discharge Time | 377 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Maximum Discharge Time | PPC |  | BESS Site Maximum Discharge Time | 378 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Discharge Ramp Rate | PPC |  | BESS Site Discharge Ramp Rate | 379 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Operation Code Indicator | PPC |  | BESS Site Operation Code Indicator | 380 | 0 - No operation; 1 - Target SOC; 2 - External P/Q Singnale Handling. 3 - Automomous Frequency-Watt. Indicator number to operation mapping is fully customizable according to project requirements | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Number Of Units Idle | PPC |  | BESS Site Number of ESS Units in Idle state | 381 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Number Of Units Discharging | PPC |  | BESS Site Number of ESS Units Discharging | 382 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Number Of Units Charging | PPC |  | BESS Site Number of ESS Units Charging | 383 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS PV Meter Real Power | PPC |  | BESS Site PV Real Power | 384 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS PV Meter Reactive Power | PPC |  | BESS Site PV Reactive Power | 385 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 386 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 387 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 388 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 389 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 390 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 391 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 392 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 393 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 394 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 395 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 396 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 397 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Average Temperature | PPC |  | BESS Site BOP Temperature | 398 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Average Humidity | PPC |  | BESS Site BOP Humidity | 399 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 400 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 401 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 402 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 403 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 404 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 405 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 406 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 407 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 408 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 409 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 410 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 411 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Average Temperature | PPC |  | BESS Site BOP Temperature | 412 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Average Humidity | PPC |  | BESS Site BOP Humidity | 413 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 3 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 414 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 415 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 416 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 417 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 418 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 419 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 420 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 421 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 422 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 423 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 424 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 425 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 426 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 427 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 428 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit 3 MW Setpoint Feedback | 429 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 430 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 431 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 432 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 433 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 434 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit 3 MW Setpoint Feedback | 435 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 436 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 437 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 438 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 439 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 440 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Frequency | PPC |  | BESS AC Frequency Measured at Plant Interconnect | 441 | Hz | Not Requested-Available | 56 | 64 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS MV Voltage | PPC |  | BESS AC Medium Voltage Measured at Plant Interconnect | 442 | V | Not Requested-Available | 210000 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Meter Real Power | PPC |  | BESS Site Real Power Measured at Plant Interconnect | 443 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Meter Reactive Power | PPC |  | BESS Site Reactive Power Measured at Plant Interconnect | 444 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Aux Meter Real Power | PPC |  | BESS Site Auxiliary Real Power Measured by Aux Meter | 445 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Aux Meter Reactive Power | PPC |  | BESS Site Auxiliary Reactive Power Measured by Aux Meter | 446 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Calculated Real Power | PPC |  | BESS Site Sum of real powers from all ESS units | 447 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Calculated Reactive Power | PPC |  | BESS Site Sum of reactive powers from all ESS units | 448 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Effective SOC | PPC |  | BESS Site Effective SOC | 449 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Average SOC | PPC |  | BESS Site Average SOC | 450 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Charge Power Limit | PPC |  | BESS Site Charge Power Limit | 451 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Discharge Power Limit | PPC |  | BESS Site Discharge Power Limit | 452 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Chargable Energy | PPC |  | BESS Site Chargable Energy | 453 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Dischargable Energy | PPC |  | BESS Site Discharable Energy | 454 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Minimum Charge Time | PPC |  | BESS Site Minimum Charge Time | 455 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Maximum Charge Time | PPC |  | BESS Site Maximum Charge Time | 456 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Charge Ramp Rate | PPC |  | BESS Site Charge Ramp Rate | 457 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Minimum Discharge Time | PPC |  | BESS Site Minimum Discharge Time | 458 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Maximum Discharge Time | PPC |  | BESS Site Maximum Discharge Time | 459 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Discharge Ramp Rate | PPC |  | BESS Site Discharge Ramp Rate | 460 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Operation Code Indicator | PPC |  | BESS Site Operation Code Indicator | 461 | 0 - No operation; 1 - Target SOC; 2 - External P/Q Singnale Handling. 3 - Automomous Frequency-Watt. Indicator number to operation mapping is fully customizable according to project requirements | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Number Of Units Idle | PPC |  | BESS Site Number of ESS Units in Idle state | 462 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Number Of Units Discharging | PPC |  | BESS Site Number of ESS Units Discharging | 463 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Number Of Units Charging | PPC |  | BESS Site Number of ESS Units Charging | 464 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS PV Meter Real Power | PPC |  | BESS Site PV Real Power | 465 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS PV Meter Reactive Power | PPC |  | BESS Site PV Reactive Power | 466 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 467 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 468 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 469 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 470 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 471 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 472 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 473 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 474 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 475 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 476 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 477 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 478 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Average Temperature | PPC |  | BESS Site BOP Temperature | 479 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Average Humidity | PPC |  | BESS Site BOP Humidity | 480 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 481 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 482 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 483 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 484 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 485 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 486 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 487 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 488 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 489 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 490 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 491 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 492 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Average Temperature | PPC |  | BESS Site BOP Temperature | 493 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Average Humidity | PPC |  | BESS Site BOP Humidity | 494 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 4 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 495 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 496 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 497 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 498 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 499 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 500 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 501 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 502 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 503 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 504 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 505 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 506 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 507 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 508 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 509 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit 4 MW Setpoint Feedback | 510 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 511 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 512 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 513 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 514 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 515 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit 4 MW Setpoint Feedback | 516 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 517 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 518 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 519 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 520 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 521 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Frequency | PPC |  | BESS AC Frequency Measured at Plant Interconnect | 522 | Hz | Not Requested-Available | 56 | 64 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS MV Voltage | PPC |  | BESS AC Medium Voltage Measured at Plant Interconnect | 523 | V | Not Requested-Available | 210000 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Meter Real Power | PPC |  | BESS Site Real Power Measured at Plant Interconnect | 524 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Meter Reactive Power | PPC |  | BESS Site Reactive Power Measured at Plant Interconnect | 525 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Aux Meter Real Power | PPC |  | BESS Site Auxiliary Real Power Measured by Aux Meter | 526 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Aux Meter Reactive Power | PPC |  | BESS Site Auxiliary Reactive Power Measured by Aux Meter | 527 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Calculated Real Power | PPC |  | BESS Site Sum of real powers from all ESS units | 528 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Calculated Reactive Power | PPC |  | BESS Site Sum of reactive powers from all ESS units | 529 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Effective SOC | PPC |  | BESS Site Effective SOC | 530 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Average SOC | PPC |  | BESS Site Average SOC | 531 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Charge Power Limit | PPC |  | BESS Site Charge Power Limit | 532 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Discharge Power Limit | PPC |  | BESS Site Discharge Power Limit | 533 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Chargable Energy | PPC |  | BESS Site Chargable Energy | 534 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Dischargable Energy | PPC |  | BESS Site Discharable Energy | 535 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Minimum Charge Time | PPC |  | BESS Site Minimum Charge Time | 536 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Maximum Charge Time | PPC |  | BESS Site Maximum Charge Time | 537 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Charge Ramp Rate | PPC |  | BESS Site Charge Ramp Rate | 538 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Minimum Discharge Time | PPC |  | BESS Site Minimum Discharge Time | 539 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Maximum Discharge Time | PPC |  | BESS Site Maximum Discharge Time | 540 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Discharge Ramp Rate | PPC |  | BESS Site Discharge Ramp Rate | 541 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Operation Code Indicator | PPC |  | BESS Site Operation Code Indicator | 542 | 0 - No operation; 1 - Target SOC; 2 - External P/Q Singnale Handling. 3 - Automomous Frequency-Watt. Indicator number to operation mapping is fully customizable according to project requirements | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Number Of Units Idle | PPC |  | BESS Site Number of ESS Units in Idle state | 543 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Number Of Units Discharging | PPC |  | BESS Site Number of ESS Units Discharging | 544 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Number Of Units Charging | PPC |  | BESS Site Number of ESS Units Charging | 545 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS PV Meter Real Power | PPC |  | BESS Site PV Real Power | 546 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS PV Meter Reactive Power | PPC |  | BESS Site PV Reactive Power | 547 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 548 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 549 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 550 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 551 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 552 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 553 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 554 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 555 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 556 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 557 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 558 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 559 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Average Temperature | PPC |  | BESS Site BOP Temperature | 560 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Average Humidity | PPC |  | BESS Site BOP Humidity | 561 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 562 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 563 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 564 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 565 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 566 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 567 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 568 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 569 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 570 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 571 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 572 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 573 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Average Temperature | PPC |  | BESS Site BOP Temperature | 574 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Average Humidity | PPC |  | BESS Site BOP Humidity | 575 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 576 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 577 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 578 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 579 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 580 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 581 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 582 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 583 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 584 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 585 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 586 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 587 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Average Temperature | PPC |  | BESS Site BOP Temperature | 588 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Average Humidity | PPC |  | BESS Site BOP Humidity | 589 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 590 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 591 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 592 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 593 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 594 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 595 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 596 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 597 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 598 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 599 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 600 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 601 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Average Temperature | PPC |  | BESS Site BOP Temperature | 602 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Average Humidity | PPC |  | BESS Site BOP Humidity | 603 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 604 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 605 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 606 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 607 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 608 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 609 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 610 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 611 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 612 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 613 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 614 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 615 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Average Temperature | PPC |  | BESS Site BOP Temperature | 616 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Average Humidity | PPC |  | BESS Site BOP Humidity | 617 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 5 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 618 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 619 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 620 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 621 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 622 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 623 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 624 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 625 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 626 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 627 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 628 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 629 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 630 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 631 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 632 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit 5 MW Setpoint Feedback | 633 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 634 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 635 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 636 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 637 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 638 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit 5 MW Setpoint Feedback | 639 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 640 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 641 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 642 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 643 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 644 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Frequency | PPC |  | BESS AC Frequency Measured at Plant Interconnect | 645 | Hz | Not Requested-Available | 56 | 64 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS MV Voltage | PPC |  | BESS AC Medium Voltage Measured at Plant Interconnect | 646 | V | Not Requested-Available | 210000 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Meter Real Power | PPC |  | BESS Site Real Power Measured at Plant Interconnect | 647 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Meter Reactive Power | PPC |  | BESS Site Reactive Power Measured at Plant Interconnect | 648 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Aux Meter Real Power | PPC |  | BESS Site Auxiliary Real Power Measured by Aux Meter | 649 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Aux Meter Reactive Power | PPC |  | BESS Site Auxiliary Reactive Power Measured by Aux Meter | 650 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Calculated Real Power | PPC |  | BESS Site Sum of real powers from all ESS units | 651 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Calculated Reactive Power | PPC |  | BESS Site Sum of reactive powers from all ESS units | 652 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Effective SOC | PPC |  | BESS Site Effective SOC | 653 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Average SOC | PPC |  | BESS Site Average SOC | 654 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Charge Power Limit | PPC |  | BESS Site Charge Power Limit | 655 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Discharge Power Limit | PPC |  | BESS Site Discharge Power Limit | 656 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Chargable Energy | PPC |  | BESS Site Chargable Energy | 657 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Dischargable Energy | PPC |  | BESS Site Discharable Energy | 658 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Minimum Charge Time | PPC |  | BESS Site Minimum Charge Time | 659 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Maximum Charge Time | PPC |  | BESS Site Maximum Charge Time | 660 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Charge Ramp Rate | PPC |  | BESS Site Charge Ramp Rate | 661 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Minimum Discharge Time | PPC |  | BESS Site Minimum Discharge Time | 662 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Maximum Discharge Time | PPC |  | BESS Site Maximum Discharge Time | 663 | Minutes | Not Requested-Available | 0 | 1440 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Discharge Ramp Rate | PPC |  | BESS Site Discharge Ramp Rate | 664 | MW/min | Not Requested-Available | 0 | 30 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Operation Code Indicator | PPC |  | BESS Site Operation Code Indicator | 665 | 0 - No operation; 1 - Target SOC; 2 - External P/Q Singnale Handling. 3 - Automomous Frequency-Watt. Indicator number to operation mapping is fully customizable according to project requirements | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Number Of Units Idle | PPC |  | BESS Site Number of ESS Units in Idle state | 666 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Number Of Units Discharging | PPC |  | BESS Site Number of ESS Units Discharging | 667 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Number Of Units Charging | PPC |  | BESS Site Number of ESS Units Charging | 668 | # | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS PV Meter Real Power | PPC |  | BESS Site PV Real Power | 669 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS PV Meter Reactive Power | PPC |  | BESS Site PV Reactive Power | 670 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 671 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 672 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 673 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 674 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 675 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 676 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 677 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 678 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 679 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 680 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 681 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 682 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Average Temperature | PPC |  | BESS Site BOP Temperature | 683 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Average Humidity | PPC |  | BESS Site BOP Humidity | 684 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 685 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 686 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 687 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 688 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 689 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 690 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 691 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 692 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 693 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 694 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 695 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 696 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Average Temperature | PPC |  | BESS Site BOP Temperature | 697 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Average Humidity | PPC |  | BESS Site BOP Humidity | 698 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 699 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 700 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 701 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 702 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 703 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 704 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 705 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 706 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 707 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 708 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 709 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 710 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Average Temperature | PPC |  | BESS Site BOP Temperature | 711 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Average Humidity | PPC |  | BESS Site BOP Humidity | 712 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 713 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 714 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 715 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 716 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 717 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 718 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 719 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 720 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 721 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 722 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 723 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 724 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Average Temperature | PPC |  | BESS Site BOP Temperature | 725 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Average Humidity | PPC |  | BESS Site BOP Humidity | 726 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 727 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 728 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 729 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 730 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 731 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 732 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 733 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 734 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 735 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 736 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 737 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 738 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Average Temperature | PPC |  | BESS Site BOP Temperature | 739 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Average Humidity | PPC |  | BESS Site BOP Humidity | 740 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 741 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 742 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 743 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 744 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 745 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 746 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 747 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 748 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 749 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 750 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 751 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 752 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Average Temperature | PPC |  | BESS Site BOP Temperature | 753 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Average Humidity | PPC |  | BESS Site BOP Humidity | 754 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 755 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 756 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 757 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 758 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 759 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 760 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 761 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 762 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 763 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 764 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 765 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 766 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Average Temperature | PPC |  | BESS Site BOP Temperature | 767 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Average Humidity | PPC |  | BESS Site BOP Humidity | 768 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 769 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 770 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 771 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 772 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 773 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 774 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 775 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 776 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 777 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 778 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 779 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 780 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Average Temperature | PPC |  | BESS Site BOP Temperature | 781 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Average Humidity | PPC |  | BESS Site BOP Humidity | 782 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 783 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 784 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 785 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 786 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 787 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 788 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 789 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 790 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 791 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 792 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 793 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 794 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Average Temperature | PPC |  | BESS Site BOP Temperature | 795 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Average Humidity | PPC |  | BESS Site BOP Humidity | 796 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 797 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 798 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 799 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 800 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 801 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 802 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 803 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 804 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 805 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 806 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 807 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 808 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Average Temperature | PPC |  | BESS Site BOP Temperature | 809 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Average Humidity | PPC |  | BESS Site BOP Humidity | 810 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 811 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 812 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 813 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 814 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 815 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 816 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 817 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 818 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 819 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 820 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 821 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 822 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Average Temperature | PPC |  | BESS Site BOP Temperature | 823 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Average Humidity | PPC |  | BESS Site BOP Humidity | 824 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 825 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 826 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 827 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 828 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 829 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 830 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 831 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 832 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 833 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 834 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 835 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 836 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Average Temperature | PPC |  | BESS Site BOP Temperature | 837 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Average Humidity | PPC |  | BESS Site BOP Humidity | 838 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 839 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 840 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 841 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 842 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 843 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 844 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 845 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 846 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 847 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 848 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 849 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 850 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Average Temperature | PPC |  | BESS Site BOP Temperature | 851 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Average Humidity | PPC |  | BESS Site BOP Humidity | 852 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 853 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 854 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 855 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 856 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 857 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 858 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 859 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 860 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 861 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 862 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 863 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 864 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Average Temperature | PPC |  | BESS Site BOP Temperature | 865 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Average Humidity | PPC |  | BESS Site BOP Humidity | 866 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 867 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 868 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 869 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 870 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 871 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 872 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 873 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 874 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 875 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 876 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 877 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 878 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Average Temperature | PPC |  | BESS Site BOP Temperature | 879 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Average Humidity | PPC |  | BESS Site BOP Humidity | 880 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 881 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 882 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 883 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 884 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 885 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 886 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 887 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 888 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 889 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 890 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 891 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 892 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Average Temperature | PPC |  | BESS Site BOP Temperature | 893 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Average Humidity | PPC |  | BESS Site BOP Humidity | 894 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 895 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 896 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 897 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 898 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 899 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 900 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 901 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 902 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 903 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 904 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 905 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 906 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Average Temperature | PPC |  | BESS Site BOP Temperature | 907 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Average Humidity | PPC |  | BESS Site BOP Humidity | 908 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Real Power | PPC |  | BESS Site ESS Unit AC Real Power | 909 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Reactive Power | PPC |  | BESS Site ESS Unit AC Reactive Power | 910 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Effective SOC | PPC |  | BESS Site ESS Unit Battery Effective SOC | 911 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Average SOC | PPC |  | BESS Site ESS Unit Battery Average SOC | 912 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Charge Power Limit | PPC |  | BESS Site ESS Unit Charge Power Limit | 913 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Discharge Power Limit | PPC |  | BESS Site ESS Unit Discharge Power Limit | 914 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Chargable Energy | PPC |  | BESS Site ESS Unit Chargeable Energy | 915 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Dischargable Energy | PPC |  | BESS Site ESS Unit Discharable Energy | 916 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Operation Code Indicator | PPC |  | BESS Site ESS Unit Operation Code Indicator | 917 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 DC Bus Voltage | PPC |  | BESS Site ESS Unit Battery DC Bus Voltage | 918 | V | Not Requested-Available | 0 | 250000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 DC Bus Current | PPC |  | BESS Site ESS Unit Battery DC Bus Current | 919 | A | Not Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Number Of Strings Online | PPC |  | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 920 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Average Temperature | PPC |  | BESS Site BOP Temperature | 921 | Celcius | Not Requested-Available | -40 | 80 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Average Humidity | PPC |  | BESS Site BOP Humidity | 922 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Battery Voltage | MET Station | MET94_MODBUS.BatteryVoltage | Battery Voltage | 923 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Humidity | MET Station | MET94_MODBUS.Humidity | Humidity | 924 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Pressure | MET Station | MET94_MODBUS.Pressure | Pressure | 925 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Temperature | MET Station | MET94_MODBUS.Temperature | Temperature | 926 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Wind Direction | MET Station | MET94_MODBUS.WindDirection | Wind Direction | 927 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Wind Speed | MET Station | MET94_MODBUS.WindSpeed | Wind Speed | 928 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Wind Speed-10 minute average | MET Station | MET94_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 929 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Wind Direction Average | MET Station | MET94_MODBUS.AvgWindDirection | Wind Direction Average | 930 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Humidity Average | MET Station | MET94_MODBUS.AvgHumidity | Humidity Average | 931 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Pressure Average | MET Station | MET94_MODBUS.AvgPressure | Pressure Average | 932 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Temperature Average | MET Station | MET94_MODBUS.AvgTemperature | Temperature Average | 933 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Rain-10 Minute | MET Station | MET94_MODBUS.10MinRain | Rain-10 Minute | 934 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET094 | Dagget 3_SUB1_MET094_Panel Temperature | MET Station | MET94_MODBUS.PanelTemperature | Panel Temperature | 935 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET094 | Dagget 3_SUB1_MET094_Heartbeat | MET Station | MET94_MODBUS.HeartBeat | Heartbeat | 936 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Battery Voltage | MET Station | MET87_MODBUS.BatteryVoltage | Battery Voltage | 937 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Humidity | MET Station | MET87_MODBUS.Humidity | Humidity | 938 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Pressure | MET Station | MET87_MODBUS.Pressure | Pressure | 939 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Temperature | MET Station | MET87_MODBUS.Temperature | Temperature | 940 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Wind Direction | MET Station | MET87_MODBUS.WindDirection | Wind Direction | 941 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Wind Speed | MET Station | MET87_MODBUS.WindSpeed | Wind Speed | 942 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Wind Speed-10 minute average | MET Station | MET87_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 943 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Wind Direction Average | MET Station | MET87_MODBUS.AvgWindDirection | Wind Direction Average | 944 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Humidity Average | MET Station | MET87_MODBUS.AvgHumidity | Humidity Average | 945 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Pressure Average | MET Station | MET87_MODBUS.AvgPressure | Pressure Average | 946 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Temperature Average | MET Station | MET87_MODBUS.AvgTemperature | Temperature Average | 947 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Rain-10 Minute | MET Station | MET87_MODBUS.10MinRain | Rain-10 Minute | 948 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET087 | Dagget 3_SUB1_MET087_Panel Temperature | MET Station | MET87_MODBUS.PanelTemperature | Panel Temperature | 949 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET087 | Dagget 3_SUB1_MET087_Heartbeat | MET Station | MET87_MODBUS.HeartBeat | Heartbeat | 950 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Battery Voltage | MET Station | MET83_MODBUS.BatteryVoltage | Battery Voltage | 951 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Humidity | MET Station | MET83_MODBUS.Humidity | Humidity | 952 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Pressure | MET Station | MET83_MODBUS.Pressure | Pressure | 953 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Temperature | MET Station | MET83_MODBUS.Temperature | Temperature | 954 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Wind Direction | MET Station | MET83_MODBUS.WindDirection | Wind Direction | 955 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Wind Speed | MET Station | MET83_MODBUS.WindSpeed | Wind Speed | 956 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Wind Speed-10 minute average | MET Station | MET83_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 957 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Wind Direction Average | MET Station | MET83_MODBUS.AvgWindDirection | Wind Direction Average | 958 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Humidity Average | MET Station | MET83_MODBUS.AvgHumidity | Humidity Average | 959 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Pressure Average | MET Station | MET83_MODBUS.AvgPressure | Pressure Average | 960 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Temperature Average | MET Station | MET83_MODBUS.AvgTemperature | Temperature Average | 961 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Rain-10 Minute | MET Station | MET83_MODBUS.10MinRain | Rain-10 Minute | 962 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET083 | Dagget 3_SUB1_MET083_Panel Temperature | MET Station | MET83_MODBUS.PanelTemperature | Panel Temperature | 963 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET083 | Dagget 3_SUB1_MET083_Heartbeat | MET Station | MET83_MODBUS.HeartBeat | Heartbeat | 964 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Battery Voltage | MET Station | MET75_MODBUS.BatteryVoltage | Battery Voltage | 965 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Humidity | MET Station | MET75_MODBUS.Humidity | Humidity | 966 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Pressure | MET Station | MET75_MODBUS.Pressure | Pressure | 967 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Temperature | MET Station | MET75_MODBUS.Temperature | Temperature | 968 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Wind Direction | MET Station | MET75_MODBUS.WindDirection | Wind Direction | 969 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Wind Speed | MET Station | MET75_MODBUS.WindSpeed | Wind Speed | 970 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Wind Speed-10 minute average | MET Station | MET75_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 971 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Wind Direction Average | MET Station | MET75_MODBUS.AvgWindDirection | Wind Direction Average | 972 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Humidity Average | MET Station | MET75_MODBUS.AvgHumidity | Humidity Average | 973 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Pressure Average | MET Station | MET75_MODBUS.AvgPressure | Pressure Average | 974 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Temperature Average | MET Station | MET75_MODBUS.AvgTemperature | Temperature Average | 975 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Rain-10 Minute | MET Station | MET75_MODBUS.10MinRain | Rain-10 Minute | 976 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET075 | Dagget 3_SUB1_MET075_Panel Temperature | MET Station | MET75_MODBUS.PanelTemperature | Panel Temperature | 977 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET075 | Dagget 3_SUB1_MET075_Heartbeat | MET Station | MET75_MODBUS.HeartBeat | Heartbeat | 978 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Battery Voltage | MET Station | MET68_MODBUS.BatteryVoltage | Battery Voltage | 979 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Humidity | MET Station | MET68_MODBUS.Humidity | Humidity | 980 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Pressure | MET Station | MET68_MODBUS.Pressure | Pressure | 981 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Temperature | MET Station | MET68_MODBUS.Temperature | Temperature | 982 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Wind Direction | MET Station | MET68_MODBUS.WindDirection | Wind Direction | 983 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Wind Speed | MET Station | MET68_MODBUS.WindSpeed | Wind Speed | 984 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Wind Speed-10 minute average | MET Station | MET68_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 985 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Wind Direction Average | MET Station | MET68_MODBUS.AvgWindDirection | Wind Direction Average | 986 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Humidity Average | MET Station | MET68_MODBUS.AvgHumidity | Humidity Average | 987 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Pressure Average | MET Station | MET68_MODBUS.AvgPressure | Pressure Average | 988 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Temperature Average | MET Station | MET68_MODBUS.AvgTemperature | Temperature Average | 989 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Rain-10 Minute | MET Station | MET68_MODBUS.10MinRain | Rain-10 Minute | 990 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET068 | Dagget 3_SUB1_MET068_Panel Temperature | MET Station | MET68_MODBUS.PanelTemperature | Panel Temperature | 991 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET068 | Dagget 3_SUB1_MET068_Heartbeat | MET Station | MET68_MODBUS.HeartBeat | Heartbeat | 992 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Battery Voltage | MET Station | MET52_MODBUS.BatteryVoltage | Battery Voltage | 993 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Humidity | MET Station | MET52_MODBUS.Humidity | Humidity | 994 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Pressure | MET Station | MET52_MODBUS.Pressure | Pressure | 995 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Temperature | MET Station | MET52_MODBUS.Temperature | Temperature | 996 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Wind Direction | MET Station | MET52_MODBUS.WindDirection | Wind Direction | 997 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Wind Speed | MET Station | MET52_MODBUS.WindSpeed | Wind Speed | 998 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Wind Speed-10 minute average | MET Station | MET52_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 999 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Wind Direction Average | MET Station | MET52_MODBUS.AvgWindDirection | Wind Direction Average | 1000 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Humidity Average | MET Station | MET52_MODBUS.AvgHumidity | Humidity Average | 1001 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Pressure Average | MET Station | MET52_MODBUS.AvgPressure | Pressure Average | 1002 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Temperature Average | MET Station | MET52_MODBUS.AvgTemperature | Temperature Average | 1003 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Rain-10 Minute | MET Station | MET52_MODBUS.10MinRain | Rain-10 Minute | 1004 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET052 | Dagget 3_SUB1_MET052_Panel Temperature | MET Station | MET52_MODBUS.PanelTemperature | Panel Temperature | 1005 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET052 | Dagget 3_SUB1_MET052_Heartbeat | MET Station | MET52_MODBUS.HeartBeat | Heartbeat | 1006 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Battery Voltage | MET Station | MET12_MODBUS.BatteryVoltage | Battery Voltage | 1007 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Humidity | MET Station | MET12_MODBUS.Humidity | Humidity | 1008 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Pressure | MET Station | MET12_MODBUS.Pressure | Pressure | 1009 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Temperature | MET Station | MET12_MODBUS.Temperature | Temperature | 1010 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Wind Direction | MET Station | MET12_MODBUS.WindDirection | Wind Direction | 1011 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Wind Speed | MET Station | MET12_MODBUS.WindSpeed | Wind Speed | 1012 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Wind Speed-10 minute average | MET Station | MET12_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1013 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Wind Direction Average | MET Station | MET12_MODBUS.AvgWindDirection | Wind Direction Average | 1014 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Humidity Average | MET Station | MET12_MODBUS.AvgHumidity | Humidity Average | 1015 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Pressure Average | MET Station | MET12_MODBUS.AvgPressure | Pressure Average | 1016 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Temperature Average | MET Station | MET12_MODBUS.AvgTemperature | Temperature Average | 1017 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Rain-10 Minute | MET Station | MET12_MODBUS.10MinRain | Rain-10 Minute | 1018 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET012 | Dagget 3_SUB1_MET012_Panel Temperature | MET Station | MET12_MODBUS.PanelTemperature | Panel Temperature | 1019 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET012 | Dagget 3_SUB1_MET012_Heartbeat | MET Station | MET12_MODBUS.HeartBeat | Heartbeat | 1020 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Battery Voltage | MET Station | MET11_MODBUS.BatteryVoltage | Battery Voltage | 1021 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Humidity | MET Station | MET11_MODBUS.Humidity | Humidity | 1022 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Pressure | MET Station | MET11_MODBUS.Pressure | Pressure | 1023 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Temperature | MET Station | MET11_MODBUS.Temperature | Temperature | 1024 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Wind Direction | MET Station | MET11_MODBUS.WindDirection | Wind Direction | 1025 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Wind Speed | MET Station | MET11_MODBUS.WindSpeed | Wind Speed | 1026 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Wind Speed-10 minute average | MET Station | MET11_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1027 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Wind Direction Average | MET Station | MET11_MODBUS.AvgWindDirection | Wind Direction Average | 1028 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Humidity Average | MET Station | MET11_MODBUS.AvgHumidity | Humidity Average | 1029 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Pressure Average | MET Station | MET11_MODBUS.AvgPressure | Pressure Average | 1030 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Temperature Average | MET Station | MET11_MODBUS.AvgTemperature | Temperature Average | 1031 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Rain-10 Minute | MET Station | MET11_MODBUS.10MinRain | Rain-10 Minute | 1032 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET011 | Dagget 3_SUB1_MET011_Panel Temperature | MET Station | MET11_MODBUS.PanelTemperature | Panel Temperature | 1033 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET011 | Dagget 3_SUB1_MET011_Heartbeat | MET Station | MET11_MODBUS.HeartBeat | Heartbeat | 1034 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Battery Voltage | MET Station | MET65_MODBUS.BatteryVoltage | Battery Voltage | 1035 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Humidity | MET Station | MET65_MODBUS.Humidity | Humidity | 1036 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Pressure | MET Station | MET65_MODBUS.Pressure | Pressure | 1037 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Temperature | MET Station | MET65_MODBUS.Temperature | Temperature | 1038 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Wind Direction | MET Station | MET65_MODBUS.WindDirection | Wind Direction | 1039 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Wind Speed | MET Station | MET65_MODBUS.WindSpeed | Wind Speed | 1040 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Wind Speed-10 minute average | MET Station | MET65_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1041 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Wind Direction Average | MET Station | MET65_MODBUS.AvgWindDirection | Wind Direction Average | 1042 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Humidity Average | MET Station | MET65_MODBUS.AvgHumidity | Humidity Average | 1043 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Pressure Average | MET Station | MET65_MODBUS.AvgPressure | Pressure Average | 1044 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Temperature Average | MET Station | MET65_MODBUS.AvgTemperature | Temperature Average | 1045 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Rain-10 Minute | MET Station | MET65_MODBUS.10MinRain | Rain-10 Minute | 1046 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET065 | Dagget 3_SUB1_MET065_Panel Temperature | MET Station | MET65_MODBUS.PanelTemperature | Panel Temperature | 1047 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET065 | Dagget 3_SUB1_MET065_Heartbeat | MET Station | MET65_MODBUS.HeartBeat | Heartbeat | 1048 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Battery Voltage | MET Station | MET44_MODBUS.BatteryVoltage | Battery Voltage | 1049 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Humidity | MET Station | MET44_MODBUS.Humidity | Humidity | 1050 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Pressure | MET Station | MET44_MODBUS.Pressure | Pressure | 1051 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Temperature | MET Station | MET44_MODBUS.Temperature | Temperature | 1052 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Wind Direction | MET Station | MET44_MODBUS.WindDirection | Wind Direction | 1053 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Wind Speed | MET Station | MET44_MODBUS.WindSpeed | Wind Speed | 1054 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Wind Speed-10 minute average | MET Station | MET44_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1055 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Wind Direction Average | MET Station | MET44_MODBUS.AvgWindDirection | Wind Direction Average | 1056 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Humidity Average | MET Station | MET44_MODBUS.AvgHumidity | Humidity Average | 1057 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Pressure Average | MET Station | MET44_MODBUS.AvgPressure | Pressure Average | 1058 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Temperature Average | MET Station | MET44_MODBUS.AvgTemperature | Temperature Average | 1059 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Rain-10 Minute | MET Station | MET44_MODBUS.10MinRain | Rain-10 Minute | 1060 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET044 | Dagget 3_SUB1_MET044_Panel Temperature | MET Station | MET44_MODBUS.PanelTemperature | Panel Temperature | 1061 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET044 | Dagget 3_SUB1_MET044_Heartbeat | MET Station | MET44_MODBUS.HeartBeat | Heartbeat | 1062 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Battery Voltage | MET Station | MET50_MODBUS.BatteryVoltage | Battery Voltage | 1063 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Humidity | MET Station | MET50_MODBUS.Humidity | Humidity | 1064 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Pressure | MET Station | MET50_MODBUS.Pressure | Pressure | 1065 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Temperature | MET Station | MET50_MODBUS.Temperature | Temperature | 1066 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Wind Direction | MET Station | MET50_MODBUS.WindDirection | Wind Direction | 1067 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Wind Speed | MET Station | MET50_MODBUS.WindSpeed | Wind Speed | 1068 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Wind Speed-10 minute average | MET Station | MET50_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1069 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Wind Direction Average | MET Station | MET50_MODBUS.AvgWindDirection | Wind Direction Average | 1070 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Humidity Average | MET Station | MET50_MODBUS.AvgHumidity | Humidity Average | 1071 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Pressure Average | MET Station | MET50_MODBUS.AvgPressure | Pressure Average | 1072 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Temperature Average | MET Station | MET50_MODBUS.AvgTemperature | Temperature Average | 1073 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Rain-10 Minute | MET Station | MET50_MODBUS.10MinRain | Rain-10 Minute | 1074 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET050 | Dagget 3_SUB1_MET050_Panel Temperature | MET Station | MET50_MODBUS.PanelTemperature | Panel Temperature | 1075 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET050 | Dagget 3_SUB1_MET050_Heartbeat | MET Station | MET50_MODBUS.HeartBeat | Heartbeat | 1076 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Battery Voltage | MET Station | MET19_MODBUS.BatteryVoltage | Battery Voltage | 1077 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Humidity | MET Station | MET19_MODBUS.Humidity | Humidity | 1078 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Pressure | MET Station | MET19_MODBUS.Pressure | Pressure | 1079 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Temperature | MET Station | MET19_MODBUS.Temperature | Temperature | 1080 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Wind Direction | MET Station | MET19_MODBUS.WindDirection | Wind Direction | 1081 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Wind Speed | MET Station | MET19_MODBUS.WindSpeed | Wind Speed | 1082 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Wind Speed-10 minute average | MET Station | MET19_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1083 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Wind Direction Average | MET Station | MET19_MODBUS.AvgWindDirection | Wind Direction Average | 1084 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Humidity Average | MET Station | MET19_MODBUS.AvgHumidity | Humidity Average | 1085 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Pressure Average | MET Station | MET19_MODBUS.AvgPressure | Pressure Average | 1086 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Temperature Average | MET Station | MET19_MODBUS.AvgTemperature | Temperature Average | 1087 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Rain-10 Minute | MET Station | MET19_MODBUS.10MinRain | Rain-10 Minute | 1088 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET019 | Dagget 3_SUB1_MET019_Panel Temperature | MET Station | MET19_MODBUS.PanelTemperature | Panel Temperature | 1089 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET019 | Dagget 3_SUB1_MET019_Heartbeat | MET Station | MET19_MODBUS.HeartBeat | Heartbeat | 1090 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Battery Voltage | MET Station | MET08_MODBUS.BatteryVoltage | Battery Voltage | 1091 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Humidity | MET Station | MET08_MODBUS.Humidity | Humidity | 1092 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Pressure | MET Station | MET08_MODBUS.Pressure | Pressure | 1093 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Temperature | MET Station | MET08_MODBUS.Temperature | Temperature | 1094 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Wind Direction | MET Station | MET08_MODBUS.WindDirection | Wind Direction | 1095 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Wind Speed | MET Station | MET08_MODBUS.WindSpeed | Wind Speed | 1096 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Wind Speed-10 minute average | MET Station | MET08_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1097 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Wind Direction Average | MET Station | MET08_MODBUS.AvgWindDirection | Wind Direction Average | 1098 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Humidity Average | MET Station | MET08_MODBUS.AvgHumidity | Humidity Average | 1099 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Pressure Average | MET Station | MET08_MODBUS.AvgPressure | Pressure Average | 1100 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Temperature Average | MET Station | MET08_MODBUS.AvgTemperature | Temperature Average | 1101 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Rain-10 Minute | MET Station | MET08_MODBUS.10MinRain | Rain-10 Minute | 1102 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET008 | Dagget 3_SUB1_MET008_Panel Temperature | MET Station | MET08_MODBUS.PanelTemperature | Panel Temperature | 1103 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET008 | Dagget 3_SUB1_MET008_Heartbeat | MET Station | MET08_MODBUS.HeartBeat | Heartbeat | 1104 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Battery Voltage | MET Station | MET23_MODBUS.BatteryVoltage | Battery Voltage | 1105 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Humidity | MET Station | MET23_MODBUS.Humidity | Humidity | 1106 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Pressure | MET Station | MET23_MODBUS.Pressure | Pressure | 1107 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Temperature | MET Station | MET23_MODBUS.Temperature | Temperature | 1108 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Wind Direction | MET Station | MET23_MODBUS.WindDirection | Wind Direction | 1109 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Wind Speed | MET Station | MET23_MODBUS.WindSpeed | Wind Speed | 1110 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Wind Speed-10 minute average | MET Station | MET23_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1111 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Wind Direction Average | MET Station | MET23_MODBUS.AvgWindDirection | Wind Direction Average | 1112 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Humidity Average | MET Station | MET23_MODBUS.AvgHumidity | Humidity Average | 1113 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Pressure Average | MET Station | MET23_MODBUS.AvgPressure | Pressure Average | 1114 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Temperature Average | MET Station | MET23_MODBUS.AvgTemperature | Temperature Average | 1115 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Rain-10 Minute | MET Station | MET23_MODBUS.10MinRain | Rain-10 Minute | 1116 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET023 | Dagget 3_SUB1_MET023_Panel Temperature | MET Station | MET23_MODBUS.PanelTemperature | Panel Temperature | 1117 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET023 | Dagget 3_SUB1_MET023_Heartbeat | MET Station | MET23_MODBUS.HeartBeat | Heartbeat | 1118 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Battery Voltage | MET Station | MET34_MODBUS.BatteryVoltage | Battery Voltage | 1119 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Humidity | MET Station | MET34_MODBUS.Humidity | Humidity | 1120 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Pressure | MET Station | MET34_MODBUS.Pressure | Pressure | 1121 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Temperature | MET Station | MET34_MODBUS.Temperature | Temperature | 1122 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Wind Direction | MET Station | MET34_MODBUS.WindDirection | Wind Direction | 1123 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Wind Speed | MET Station | MET34_MODBUS.WindSpeed | Wind Speed | 1124 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Wind Speed-10 minute average | MET Station | MET34_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1125 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Wind Direction Average | MET Station | MET34_MODBUS.AvgWindDirection | Wind Direction Average | 1126 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Humidity Average | MET Station | MET34_MODBUS.AvgHumidity | Humidity Average | 1127 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Pressure Average | MET Station | MET34_MODBUS.AvgPressure | Pressure Average | 1128 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Temperature Average | MET Station | MET34_MODBUS.AvgTemperature | Temperature Average | 1129 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Rain-10 Minute | MET Station | MET34_MODBUS.10MinRain | Rain-10 Minute | 1130 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET034 | Dagget 3_SUB1_MET034_Panel Temperature | MET Station | MET34_MODBUS.PanelTemperature | Panel Temperature | 1131 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET034 | Dagget 3_SUB1_MET034_Heartbeat | MET Station | MET34_MODBUS.HeartBeat | Heartbeat | 1132 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Battery Voltage | MET Station | MET31_MODBUS.BatteryVoltage | Battery Voltage | 1133 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Humidity | MET Station | MET31_MODBUS.Humidity | Humidity | 1134 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Pressure | MET Station | MET31_MODBUS.Pressure | Pressure | 1135 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Temperature | MET Station | MET31_MODBUS.Temperature | Temperature | 1136 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Wind Direction | MET Station | MET31_MODBUS.WindDirection | Wind Direction | 1137 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Wind Speed | MET Station | MET31_MODBUS.WindSpeed | Wind Speed | 1138 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Wind Speed-10 minute average | MET Station | MET31_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1139 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Wind Direction Average | MET Station | MET31_MODBUS.AvgWindDirection | Wind Direction Average | 1140 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Humidity Average | MET Station | MET31_MODBUS.AvgHumidity | Humidity Average | 1141 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Pressure Average | MET Station | MET31_MODBUS.AvgPressure | Pressure Average | 1142 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Temperature Average | MET Station | MET31_MODBUS.AvgTemperature | Temperature Average | 1143 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Rain-10 Minute | MET Station | MET31_MODBUS.10MinRain | Rain-10 Minute | 1144 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET031 | Dagget 3_SUB1_MET031_Panel Temperature | MET Station | MET31_MODBUS.PanelTemperature | Panel Temperature | 1145 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET031 | Dagget 3_SUB1_MET031_Heartbeat | MET Station | MET31_MODBUS.HeartBeat | Heartbeat | 1146 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Battery Voltage | MET Station | MET42_MODBUS.BatteryVoltage | Battery Voltage | 1147 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Humidity | MET Station | MET42_MODBUS.Humidity | Humidity | 1148 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Pressure | MET Station | MET42_MODBUS.Pressure | Pressure | 1149 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Temperature | MET Station | MET42_MODBUS.Temperature | Temperature | 1150 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Wind Direction | MET Station | MET42_MODBUS.WindDirection | Wind Direction | 1151 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Wind Speed | MET Station | MET42_MODBUS.WindSpeed | Wind Speed | 1152 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Wind Speed-10 minute average | MET Station | MET42_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1153 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Wind Direction Average | MET Station | MET42_MODBUS.AvgWindDirection | Wind Direction Average | 1154 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Humidity Average | MET Station | MET42_MODBUS.AvgHumidity | Humidity Average | 1155 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Pressure Average | MET Station | MET42_MODBUS.AvgPressure | Pressure Average | 1156 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Temperature Average | MET Station | MET42_MODBUS.AvgTemperature | Temperature Average | 1157 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Rain-10 Minute | MET Station | MET42_MODBUS.10MinRain | Rain-10 Minute | 1158 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET042 | Dagget 3_SUB1_MET042_Panel Temperature | MET Station | MET42_MODBUS.PanelTemperature | Panel Temperature | 1159 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET042 | Dagget 3_SUB1_MET042_Heartbeat | MET Station | MET42_MODBUS.HeartBeat | Heartbeat | 1160 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | SOIL094 | Dagget 3_SUB1_SOIL094_Soiling Ratio | Soiling Station | MET94_MODBUS.SoilingRatio | Soiling Ratio | 1161 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL087 | Dagget 3_SUB1_SOIL087_Soiling Ratio | Soiling Station | MET87_MODBUS.SoilingRatio | Soiling Ratio | 1162 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL083 | Dagget 3_SUB1_SOIL083_Soiling Ratio | Soiling Station | MET83_MODBUS.SoilingRatio | Soiling Ratio | 1163 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL075 | Dagget 3_SUB1_SOIL075_Soiling Ratio | Soiling Station | MET75_MODBUS.SoilingRatio | Soiling Ratio | 1164 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL068 | Dagget 3_SUB1_SOIL068_Soiling Ratio | Soiling Station | MET68_MODBUS.SoilingRatio | Soiling Ratio | 1165 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL052 | Dagget 3_SUB1_SOIL052_Soiling Ratio | Soiling Station | MET52_MODBUS.SoilingRatio | Soiling Ratio | 1166 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL012 | Dagget 3_SUB1_SOIL012_Soiling Ratio | Soiling Station | MET12_MODBUS.SoilingRatio | Soiling Ratio | 1167 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL011 | Dagget 3_SUB1_SOIL011_Soiling Ratio | Soiling Station | MET11_MODBUS.SoilingRatio | Soiling Ratio | 1168 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL065 | Dagget 3_SUB1_SOIL065_Soiling Ratio | Soiling Station | MET65_MODBUS.SoilingRatio | Soiling Ratio | 1169 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL044 | Dagget 3_SUB1_SOIL044_Soiling Ratio | Soiling Station | MET44_MODBUS.SoilingRatio | Soiling Ratio | 1170 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL050 | Dagget 3_SUB1_SOIL050_Soiling Ratio | Soiling Station | MET50_MODBUS.SoilingRatio | Soiling Ratio | 1171 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL019 | Dagget 3_SUB1_SOIL019_Soiling Ratio | Soiling Station | MET19_MODBUS.SoilingRatio | Soiling Ratio | 1172 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL008 | Dagget 3_SUB1_SOIL008_Soiling Ratio | Soiling Station | MET08_MODBUS.SoilingRatio | Soiling Ratio | 1173 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL023 | Dagget 3_SUB1_SOIL023_Soiling Ratio | Soiling Station | MET23_MODBUS.SoilingRatio | Soiling Ratio | 1174 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL034 | Dagget 3_SUB1_SOIL034_Soiling Ratio | Soiling Station | MET34_MODBUS.SoilingRatio | Soiling Ratio | 1175 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL031 | Dagget 3_SUB1_SOIL031_Soiling Ratio | Soiling Station | MET31_MODBUS.SoilingRatio | Soiling Ratio | 1176 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL042 | Dagget 3_SUB1_SOIL042_Soiling Ratio | Soiling Station | MET42_MODBUS.SoilingRatio | Soiling Ratio | 1177 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL094 | Dagget 3_SUB1_SOIL094_Transmission Loss | Soiling Station | MET94_MODBUS.TransmissionLoss | Transmission Loss | 1178 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL087 | Dagget 3_SUB1_SOIL087_Transmission Loss | Soiling Station | MET87_MODBUS.TransmissionLoss | Transmission Loss | 1179 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL083 | Dagget 3_SUB1_SOIL083_Transmission Loss | Soiling Station | MET83_MODBUS.TransmissionLoss | Transmission Loss | 1180 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL075 | Dagget 3_SUB1_SOIL075_Transmission Loss | Soiling Station | MET75_MODBUS.TransmissionLoss | Transmission Loss | 1181 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL068 | Dagget 3_SUB1_SOIL068_Transmission Loss | Soiling Station | MET68_MODBUS.TransmissionLoss | Transmission Loss | 1182 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL052 | Dagget 3_SUB1_SOIL052_Transmission Loss | Soiling Station | MET52_MODBUS.TransmissionLoss | Transmission Loss | 1183 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL012 | Dagget 3_SUB1_SOIL012_Transmission Loss | Soiling Station | MET12_MODBUS.TransmissionLoss | Transmission Loss | 1184 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL011 | Dagget 3_SUB1_SOIL011_Transmission Loss | Soiling Station | MET11_MODBUS.TransmissionLoss | Transmission Loss | 1185 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL065 | Dagget 3_SUB1_SOIL065_Transmission Loss | Soiling Station | MET65_MODBUS.TransmissionLoss | Transmission Loss | 1186 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL044 | Dagget 3_SUB1_SOIL044_Transmission Loss | Soiling Station | MET44_MODBUS.TransmissionLoss | Transmission Loss | 1187 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL050 | Dagget 3_SUB1_SOIL050_Transmission Loss | Soiling Station | MET50_MODBUS.TransmissionLoss | Transmission Loss | 1188 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL019 | Dagget 3_SUB1_SOIL019_Transmission Loss | Soiling Station | MET19_MODBUS.TransmissionLoss | Transmission Loss | 1189 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL008 | Dagget 3_SUB1_SOIL008_Transmission Loss | Soiling Station | MET08_MODBUS.TransmissionLoss | Transmission Loss | 1190 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL023 | Dagget 3_SUB1_SOIL023_Transmission Loss | Soiling Station | MET23_MODBUS.TransmissionLoss | Transmission Loss | 1191 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL034 | Dagget 3_SUB1_SOIL034_Transmission Loss | Soiling Station | MET34_MODBUS.TransmissionLoss | Transmission Loss | 1192 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL031 | Dagget 3_SUB1_SOIL031_Transmission Loss | Soiling Station | MET31_MODBUS.TransmissionLoss | Transmission Loss | 1193 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL042 | Dagget 3_SUB1_SOIL042_Transmission Loss | Soiling Station | MET42_MODBUS.TransmissionLoss | Transmission Loss | 1194 | % | Requested-Available | 0 | 100 | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Real Power-AC | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0000_Real_Power_AC | AC Real Power | 1195 | MW | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Reactive Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0001_Reactive_Power | AC Reactive Power | 1196 | MVAR | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0002_Power_Factor | Power Factor | 1197 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage A-B | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0003_Voltage_A_B | Phase-Phase Voltages | 1198 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage B-C | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0004_Voltage_B_C | Phase-Phase Voltages | 1199 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage C-A | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0005_Voltage_C_A | Phase-Phase Voltages | 1200 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Current A | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0006_Current_A | Phase Currents | 1201 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Current B | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0007_Current_B | Phase Currents | 1202 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Current C | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0008_Current_C | Phase Currents | 1203 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Frequency | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0009_Frequency | Frequency | 1204 | Hz | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0010_A_Phase_Power | Phase Power | 1205 | MW | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0011_B_Phase_Power | Phase Power | 1206 | MW | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0012_C_Phase_Power | Phase Power | 1207 | MW | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage A-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0013_Voltage_A_N | L-N Phase Voltages | 1208 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage B-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0014_Voltage_B_N | L-N Phase Voltages | 1209 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage C-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0015_Voltage_C_N | L-N Phase Voltages | 1210 | kV | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0016_A_Phase_Apparent_Power | Phase Apparent Power | 1211 | MVA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0017_B_Phase_Apparent_Power | Phase Apparent Power | 1212 | MVA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0018_C_Phase_Apparent_Power | Phase Apparent Power | 1213 | MVA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0019_A_Phase_Power_Factor | Phase Power Factor | 1214 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0020_B_Phase_Power_Factor | Phase Power Factor | 1215 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0021_C_Phase_Power_Factor | Phase Power Factor | 1216 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Real Power-AC | Line Relay | SEL_411L_87L1S_SEL.F_METER2_P | AC Real Power | 1217 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Reactive Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_Q | AC Reactive Power | 1218 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PF | Power Factor | 1219 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage A-B | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VAB | Phase-Phase Voltages | 1220 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage B-C | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VBC | Phase-Phase Voltages | 1221 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage C-A | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VCA | Phase-Phase Voltages | 1222 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Current A | Line Relay | SEL_411L_87L1S_SEL.FM_INST_IAB | Phase Currents | 1223 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Current B | Line Relay | SEL_411L_87L1S_SEL.FM_INST_IBC | Phase Currents | 1224 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Current C | Line Relay | SEL_411L_87L1S_SEL.FM_INST_ICA | Phase Currents | 1225 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Frequency | Line Relay | SEL_411L_87L1S_SEL.FM_INST_FREQ | Frequency | 1226 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PA | Phase Power | 1227 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PB | Phase Power | 1228 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PC | Phase Power | 1229 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage A-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VA | L-N Phase Voltages | 1230 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage B-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VB | L-N Phase Voltages | 1231 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage C-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VC | L-N Phase Voltages | 1232 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SA | Phase Apparent Power | 1233 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SB | Phase Apparent Power | 1234 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SC | Phase Apparent Power | 1235 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFA | Phase Power Factor | 1236 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFB | Phase Power Factor | 1237 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFC | Phase Power Factor | 1238 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Real Power-AC | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0000_Real_Power_AC | AC Real Power | 1239 | W | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Reactive Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0001_Reactive_Power | AC Reactive Power | 1240 | VAR | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0002_Power_Factor | Power Factor | 1241 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage A-B | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0003_Voltage_A_B | Phase-Phase Voltages | 1242 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage B-C | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0004_Voltage_B_C | Phase-Phase Voltages | 1243 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage C-A | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0005_Voltage_C_A | Phase-Phase Voltages | 1244 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Current A | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0006_Current_A | Phase Currents | 1245 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Current B | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0007_Current_B | Phase Currents | 1246 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Current C | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0008_Current_C | Phase Currents | 1247 | A | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Frequency | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0009_Frequency | Frequency | 1248 | Hz | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0010_A_Phase_Power | Phase Power | 1249 | W | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0011_B_Phase_Power | Phase Power | 1250 | W | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0012_C_Phase_Power | Phase Power | 1251 | W | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage A-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0013_Voltage_A_N | L-N Phase Voltages | 1252 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage B-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0014_Voltage_B_N | L-N Phase Voltages | 1253 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage C-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0015_Voltage_C_N | L-N Phase Voltages | 1254 | V | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0016_A_Phase_Apparent_Power | Phase Apparent Power | 1255 | VA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0017_B_Phase_Apparent_Power | Phase Apparent Power | 1256 | VA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0018_C_Phase_Apparent_Power | Phase Apparent Power | 1257 | VA | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0019_A_Phase_Power_Factor | Phase Power Factor | 1258 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0020_B_Phase_Power_Factor | Phase Power Factor | 1259 | Unitless | Requested-Available |  |  | 1
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0021_C_Phase_Power_Factor | Phase Power Factor | 1260 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Real Power-AC | Line Relay | SEL_411L_87L2S_SEL.F_METER2_P | AC Real Power | 1261 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Reactive Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_Q | AC Reactive Power | 1262 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PF | Power Factor | 1263 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage A-B | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VAB | Phase-Phase Voltages | 1264 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage B-C | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VBC | Phase-Phase Voltages | 1265 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage C-A | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VCA | Phase-Phase Voltages | 1266 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Current A | Line Relay | SEL_411L_87L2S_SEL.FM_INST_IA1 | Phase Currents | 1267 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Current B | Line Relay | SEL_411L_87L2S_SEL.FM_INST_IB1 | Phase Currents | 1268 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Current C | Line Relay | SEL_411L_87L2S_SEL.FM_INST_IC1 | Phase Currents | 1269 | A | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Frequency | Line Relay | SEL_411L_87L2S_SEL.FM_INST_FREQ | Frequency | 1270 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PA | Phase Power | 1271 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PB | Phase Power | 1272 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PC | Phase Power | 1273 | W | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage A-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VA | L-N Phase Voltages | 1274 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage B-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VB | L-N Phase Voltages | 1275 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage C-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VC | L-N Phase Voltages | 1276 | V | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SA | Phase Apparent Power | 1277 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SB | Phase Apparent Power | 1278 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SC | Phase Apparent Power | 1279 | VA | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFA | Phase Power Factor | 1280 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFB | Phase Power Factor | 1281 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFC | Phase Power Factor | 1282 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Real Power-AC | Transformer Relay | SEL_487E_87T1P_SEL.FPP_3_004 | AC Real Power | 1283 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_4_004 | AC Reactive Power | 1284 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_004 | Power Factor | 1285 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage A-B | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1286 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage B-C | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1287 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage C-A | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1288 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Current A | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY1 | Phase Currents | 1289 | A | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Current B | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY2 | Phase Currents | 1290 | A | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Current C | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY3 | Phase Currents |  | A | Requested-Not Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Frequency | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_FREQ | Frequency | 1291 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_001 | Phase Power | 1292 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_002 | Phase Power | 1293 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_003 | Phase Power | 1294 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage A-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VAZ | L-N Phase Voltages | 1295 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage B-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VBZ | L-N Phase Voltages | 1296 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage C-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VCZ | L-N Phase Voltages | 1297 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_001 | Phase Apparent Power | 1298 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_002 | Phase Apparent Power | 1299 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_003 | Phase Apparent Power | 1300 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_001 | Phase Power Factor | 1301 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_002 | Phase Power Factor | 1302 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_003 | Phase Power Factor | 1303 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Real Power-AC | Transformer Relay |  | AC Real Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Power | Transformer Relay |  | AC Reactive Power |  | VAR | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Power Factor | Transformer Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage A-B | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage B-C | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage C-A | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Current A | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IA1 | Phase Currents | 1304 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Current B | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IB1 | Phase Currents | 1305 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Current C | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IC1 | Phase Currents | 1306 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Frequency | Transformer Relay |  | Frequency |  | Hz | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage A-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage B-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage C-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Real Power-AC | Transformer Relay | SEL_487E_87T2P_SEL.FPP_3_004 | AC Real Power | 1307 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_4_004 | AC Reactive Power | 1308 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Current A | Bus Relay | SEL_587Z_87BT1_SEL.F_METER_IA | Phase Currents | 1309 | A | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Current B | Bus Relay | SEL_587Z_87BT1_SEL.F_METER_IB | Phase Currents | 1310 | A | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Current C | Bus Relay | SEL_587Z_87BT1_SEL.F_METER_IC | Phase Currents | 1311 | A | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Current A | Bus Relay | SEL_587Z_87BT2_SEL.F_METER_IA | Phase Currents | 1312 | A | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Current B | Bus Relay | SEL_587Z_87BT2_SEL.F_METER_IB | Phase Currents | 1313 | A | Requested-Available |  |  | 1
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Current C | Bus Relay | SEL_587Z_87BT2_SEL.F_METER_IC | Phase Currents | 1314 | A | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_004 | Power Factor | 1315 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage A-B | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1316 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage B-C | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1317 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage C-A | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1318 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Current A | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY1 | Phase Currents | 1319 | A | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Current B | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY2 | Phase Currents | 1320 | A | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Current C | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY3 | Phase Currents |  | A | Requested-Not Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Frequency | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_FREQ | Frequency | 1321 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_001 | Phase Power | 1322 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_002 | Phase Power | 1323 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_003 | Phase Power | 1324 | W | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage A-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VAZ | L-N Phase Voltages | 1325 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage B-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VBZ | L-N Phase Voltages | 1326 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage C-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VCZ | L-N Phase Voltages | 1327 | V | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_001 | Phase Apparent Power | 1328 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_002 | Phase Apparent Power | 1329 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_003 | Phase Apparent Power | 1330 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_001 | Phase Power Factor | 1331 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_002 | Phase Power Factor | 1332 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_003 | Phase Power Factor | 1333 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Real Power-AC | Transformer Relay |  | AC Real Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Power | Transformer Relay |  | AC Reactive Power |  | VAR | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Power Factor | Transformer Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage A-B | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage B-C | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage C-A | Transformer Relay |  | Phase-Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Current A | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IA1 | Phase Currents | 1334 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Current B | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IB1 | Phase Currents | 1335 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Current C | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IC1 | Phase Currents | 1336 | A | Requested-Available |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Frequency | Transformer Relay |  | Frequency |  | Hz | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Power | Transformer Relay |  | Phase Power |  | W | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage A-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage B-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage C-N | Transformer Relay |  | L-N Phase Voltages |  | V | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Apparent Power | Transformer Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Power Factor | Transformer Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Real Power-AC | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_P_WATTS | AC Real Power | 1337 | W | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Reactive Power | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_Q_VARS | AC Reactive Power | 1338 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage A-B | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VAB | Phase-Phase Voltages | 1339 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage B-C | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VBC | Phase-Phase Voltages | 1340 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage C-A | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VCA | Phase-Phase Voltages | 1341 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Current A | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IA | Phase Currents | 1342 | A | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Current B | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IB | Phase Currents | 1343 | A | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Current C | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IC | Phase Currents | 1344 | A | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Frequency | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_FREQ | Frequency | 1345 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Power | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_PA_WATTS | Phase Power | 1346 | W | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Power | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_PB_WATTS | Phase Power | 1347 | W | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Power | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_PC_WATTS | Phase Power | 1348 | W | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage A-N | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VA | L-N Phase Voltages | 1349 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage B-N | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VB | L-N Phase Voltages | 1350 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Voltage C-N | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_VC | L-N Phase Voltages | 1351 | V | Requested-Available |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Real Power-AC | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_P_WATTS | AC Real Power | 1352 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Reactive Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_Q_VARS | AC Reactive Power | 1353 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage A-B | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VAB | Phase-Phase Voltages | 1354 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage B-C | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VBC | Phase-Phase Voltages | 1355 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage C-A | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VCA | Phase-Phase Voltages | 1356 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Current A | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IA | Phase Currents | 1357 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Current B | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IB | Phase Currents | 1358 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Current C | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IC | Phase Currents | 1359 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Frequency | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_FREQ | Frequency | 1360 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PA_WATTS | Phase Power | 1361 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PB_WATTS | Phase Power | 1362 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PC_WATTS | Phase Power | 1363 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage A-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VA | L-N Phase Voltages | 1364 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage B-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VB | L-N Phase Voltages | 1365 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Voltage C-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VC | L-N Phase Voltages | 1366 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Real Power-AC | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_P_WATTS | AC Real Power | 1367 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Reactive Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_Q_VARS | AC Reactive Power | 1368 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage A-B | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VAB | Phase-Phase Voltages | 1369 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage B-C | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VBC | Phase-Phase Voltages | 1370 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage C-A | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VCA | Phase-Phase Voltages | 1371 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Current A | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IA | Phase Currents | 1372 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Current B | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IB | Phase Currents | 1373 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Current C | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IC | Phase Currents | 1374 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Frequency | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_FREQ | Frequency | 1375 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PA_WATTS | Phase Power | 1376 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PB_WATTS | Phase Power | 1377 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PC_WATTS | Phase Power | 1378 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage A-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VA | L-N Phase Voltages | 1379 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage B-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VB | L-N Phase Voltages | 1380 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Voltage C-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VC | L-N Phase Voltages | 1381 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Real Power-AC | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_P_WATTS | AC Real Power | 1382 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Reactive Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_Q_VARS | AC Reactive Power | 1383 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage A-B | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VAB | Phase-Phase Voltages | 1384 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage B-C | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VBC | Phase-Phase Voltages | 1385 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage C-A | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VCA | Phase-Phase Voltages | 1386 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Current A | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IA | Phase Currents | 1387 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Current B | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IB | Phase Currents | 1388 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Current C | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IC | Phase Currents | 1389 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Frequency | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_FREQ | Frequency | 1390 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _A Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PA_WATTS | Phase Power | 1391 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _B Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PB_WATTS | Phase Power | 1392 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _C Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PC_WATTS | Phase Power | 1393 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage A-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VA | L-N Phase Voltages | 1394 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage B-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VB | L-N Phase Voltages | 1395 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _Voltage C-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VC | L-N Phase Voltages | 1396 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3 _C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Real Power-AC | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_P_WATTS | AC Real Power | 1397 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Reactive Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_Q_VARS | AC Reactive Power | 1398 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage A-B | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VAB | Phase-Phase Voltages | 1399 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage B-C | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VBC | Phase-Phase Voltages | 1400 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage C-A | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VCA | Phase-Phase Voltages | 1401 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Current A | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IA | Phase Currents | 1402 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Current B | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IB | Phase Currents | 1403 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Current C | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IC | Phase Currents | 1404 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Frequency | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_FREQ | Frequency | 1405 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PA_WATTS | Phase Power | 1406 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PB_WATTS | Phase Power | 1407 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PC_WATTS | Phase Power | 1408 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage A-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VA | L-N Phase Voltages | 1409 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage B-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VB | L-N Phase Voltages | 1410 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Voltage C-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VC | L-N Phase Voltages | 1411 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Real Power-AC | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_P_WATTS | AC Real Power | 1412 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Reactive Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_Q_VARS | AC Reactive Power | 1413 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage A-B | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VAB | Phase-Phase Voltages | 1414 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage B-C | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VBC | Phase-Phase Voltages | 1415 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage C-A | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VCA | Phase-Phase Voltages | 1416 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Current A | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IA | Phase Currents | 1417 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Current B | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IB | Phase Currents | 1418 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Current C | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IC | Phase Currents | 1419 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Frequency | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_FREQ | Frequency | 1420 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _A Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PA_WATTS | Phase Power | 1421 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _B Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PB_WATTS | Phase Power | 1422 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _C Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PC_WATTS | Phase Power | 1423 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage A-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VA | L-N Phase Voltages | 1424 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage B-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VB | L-N Phase Voltages | 1425 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _Voltage C-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VC | L-N Phase Voltages | 1426 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5 _C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Real Power-AC | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_P_WATTS | AC Real Power | 1427 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Reactive Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_Q_VARS | AC Reactive Power | 1428 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage A-B | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VAB | Phase-Phase Voltages | 1429 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage B-C | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VBC | Phase-Phase Voltages | 1430 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage C-A | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VCA | Phase-Phase Voltages | 1431 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Current A | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IA | Phase Currents | 1432 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Current B | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IB | Phase Currents | 1433 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Current C | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IC | Phase Currents | 1434 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Frequency | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_FREQ | Frequency | 1435 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _A Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PA_WATTS | Phase Power | 1436 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _B Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PB_WATTS | Phase Power | 1437 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _C Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PC_WATTS | Phase Power | 1438 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage A-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VA | L-N Phase Voltages | 1439 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage B-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VB | L-N Phase Voltages | 1440 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _Voltage C-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VC | L-N Phase Voltages | 1441 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6 _C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Real Power-AC | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_P_WATTS | AC Real Power | 1442 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Reactive Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_Q_VARS | AC Reactive Power | 1443 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage A-B | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VAB | Phase-Phase Voltages | 1444 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage B-C | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VBC | Phase-Phase Voltages | 1445 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage C-A | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VCA | Phase-Phase Voltages | 1446 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Current A | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IA | Phase Currents | 1447 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Current B | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IB | Phase Currents | 1448 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Current C | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IC | Phase Currents | 1449 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Frequency | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_FREQ | Frequency | 1450 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PA_WATTS | Phase Power | 1451 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PB_WATTS | Phase Power | 1452 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PC_WATTS | Phase Power | 1453 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage A-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VA | L-N Phase Voltages | 1454 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage B-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VB | L-N Phase Voltages | 1455 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Voltage C-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VC | L-N Phase Voltages | 1456 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Real Power-AC | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_P_WATTS | AC Real Power | 1457 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Reactive Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_Q_VARS | AC Reactive Power | 1458 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage A-B | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VAB | Phase-Phase Voltages | 1459 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage B-C | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VBC | Phase-Phase Voltages | 1460 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage C-A | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VCA | Phase-Phase Voltages | 1461 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Current A | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IA | Phase Currents | 1462 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Current B | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IB | Phase Currents | 1463 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Current C | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IC | Phase Currents | 1464 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Frequency | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_FREQ | Frequency | 1465 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PA_WATTS | Phase Power | 1466 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PB_WATTS | Phase Power | 1467 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PC_WATTS | Phase Power | 1468 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage A-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VA | L-N Phase Voltages | 1469 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage B-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VB | L-N Phase Voltages | 1470 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Voltage C-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VC | L-N Phase Voltages | 1471 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Real Power-AC | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_P_WATTS | AC Real Power | 1472 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Reactive Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_Q_VARS | AC Reactive Power | 1473 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage A-B | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VAB | Phase-Phase Voltages | 1474 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage B-C | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VBC | Phase-Phase Voltages | 1475 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage C-A | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VCA | Phase-Phase Voltages | 1476 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Current A | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IA | Phase Currents | 1477 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Current B | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IB | Phase Currents | 1478 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Current C | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IC | Phase Currents | 1479 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Frequency | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_FREQ | Frequency | 1480 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PA_WATTS | Phase Power | 1481 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PB_WATTS | Phase Power | 1482 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PC_WATTS | Phase Power | 1483 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage A-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VA | L-N Phase Voltages | 1484 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage B-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VB | L-N Phase Voltages | 1485 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Voltage C-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VC | L-N Phase Voltages | 1486 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Real Power-AC | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_P_WATTS | AC Real Power | 1487 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Reactive Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_Q_VARS | AC Reactive Power | 1488 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage A-B | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VAB | Phase-Phase Voltages | 1489 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage B-C | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VBC | Phase-Phase Voltages | 1490 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage C-A | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VCA | Phase-Phase Voltages | 1491 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Current A | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IA | Phase Currents | 1492 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Current B | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IB | Phase Currents | 1493 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Current C | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IC | Phase Currents | 1494 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Frequency | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_FREQ | Frequency | 1495 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PA_WATTS | Phase Power | 1496 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PB_WATTS | Phase Power | 1497 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PC_WATTS | Phase Power | 1498 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage A-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VA | L-N Phase Voltages | 1499 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage B-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VB | L-N Phase Voltages | 1500 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Voltage C-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VC | L-N Phase Voltages | 1501 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Real Power-AC | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_P_WATTS | AC Real Power | 1502 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Reactive Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_Q_VARS | AC Reactive Power | 1503 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage A-B | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VAB | Phase-Phase Voltages | 1504 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage B-C | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VBC | Phase-Phase Voltages | 1505 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage C-A | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VCA | Phase-Phase Voltages | 1506 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Current A | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IA | Phase Currents | 1507 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Current B | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IB | Phase Currents | 1508 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Current C | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IC | Phase Currents | 1509 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Frequency | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_FREQ | Frequency | 1510 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PA_WATTS | Phase Power | 1511 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PB_WATTS | Phase Power | 1512 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PC_WATTS | Phase Power | 1513 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage A-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VA | L-N Phase Voltages | 1514 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage B-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VB | L-N Phase Voltages | 1515 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Voltage C-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VC | L-N Phase Voltages | 1516 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Real Power-AC | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_P_WATTS | AC Real Power | 1517 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Reactive Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_Q_VARS | AC Reactive Power | 1518 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage A-B | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VAB | Phase-Phase Voltages | 1519 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage B-C | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VBC | Phase-Phase Voltages | 1520 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage C-A | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VCA | Phase-Phase Voltages | 1521 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Current A | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IA | Phase Currents | 1522 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Current B | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IB | Phase Currents | 1523 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Current C | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IC | Phase Currents | 1524 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Frequency | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_FREQ | Frequency | 1525 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PA_WATTS | Phase Power | 1526 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PB_WATTS | Phase Power | 1527 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PC_WATTS | Phase Power | 1528 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage A-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VA | L-N Phase Voltages | 1529 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage B-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VB | L-N Phase Voltages | 1530 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Voltage C-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VC | L-N Phase Voltages | 1531 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Real Power-AC | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_P_WATTS | AC Real Power | 1532 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Reactive Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_Q_VARS | AC Reactive Power | 1533 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage A-B | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VAB | Phase-Phase Voltages | 1534 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage B-C | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VBC | Phase-Phase Voltages | 1535 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage C-A | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VCA | Phase-Phase Voltages | 1536 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Current A | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IA | Phase Currents | 1537 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Current B | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IB | Phase Currents | 1538 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Current C | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IC | Phase Currents | 1539 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Frequency | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_FREQ | Frequency | 1540 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PA_WATTS | Phase Power | 1541 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PB_WATTS | Phase Power | 1542 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PC_WATTS | Phase Power | 1543 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage A-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VA | L-N Phase Voltages | 1544 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage B-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VB | L-N Phase Voltages | 1545 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Voltage C-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VC | L-N Phase Voltages | 1546 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Real Power-AC | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_P_WATTS | AC Real Power | 1547 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Reactive Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_Q_VARS | AC Reactive Power | 1548 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage A-B | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VAB | Phase-Phase Voltages | 1549 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage B-C | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VBC | Phase-Phase Voltages | 1550 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage C-A | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VCA | Phase-Phase Voltages | 1551 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Current A | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IA | Phase Currents | 1552 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Current B | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IB | Phase Currents | 1553 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Current C | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IC | Phase Currents | 1554 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Frequency | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_FREQ | Frequency | 1555 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PA_WATTS | Phase Power | 1556 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PB_WATTS | Phase Power | 1557 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PC_WATTS | Phase Power | 1558 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage A-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VA | L-N Phase Voltages | 1559 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage B-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VB | L-N Phase Voltages | 1560 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Voltage C-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VC | L-N Phase Voltages | 1561 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Real Power-AC | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_P_WATTS | AC Real Power | 1562 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Reactive Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_Q_VARS | AC Reactive Power | 1563 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage A-B | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VAB | Phase-Phase Voltages | 1564 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage B-C | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VBC | Phase-Phase Voltages | 1565 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage C-A | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VCA | Phase-Phase Voltages | 1566 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Current A | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IA | Phase Currents | 1567 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Current B | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IB | Phase Currents | 1568 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Current C | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IC | Phase Currents | 1569 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Frequency | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_FREQ | Frequency | 1570 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PA_WATTS | Phase Power | 1571 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PB_WATTS | Phase Power | 1572 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PC_WATTS | Phase Power | 1573 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage A-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VA | L-N Phase Voltages | 1574 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage B-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VB | L-N Phase Voltages | 1575 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Voltage C-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VC | L-N Phase Voltages | 1576 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Real Power-AC | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_P_WATTS | AC Real Power | 1577 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Reactive Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_Q_VARS | AC Reactive Power | 1578 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage A-B | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VAB | Phase-Phase Voltages | 1579 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage B-C | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VBC | Phase-Phase Voltages | 1580 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage C-A | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VCA | Phase-Phase Voltages | 1581 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Current A | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IA | Phase Currents | 1582 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Current B | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IB | Phase Currents | 1583 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Current C | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IC | Phase Currents | 1584 | A | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Frequency | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_FREQ | Frequency | 1585 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PA_WATTS | Phase Power | 1586 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PB_WATTS | Phase Power | 1587 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PC_WATTS | Phase Power | 1588 | W | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage A-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VA | L-N Phase Voltages | 1589 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage B-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VB | L-N Phase Voltages | 1590 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Voltage C-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VC | L-N Phase Voltages | 1591 | V | Requested-Available |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | VA | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Applicable |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_1 MVAR Contribution | Reactive Power Relay | RTAC_LOGIC.87VC1P_MVAR_Contribution | MVAR Contribution | 1592 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Real Power-AC | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_P3W | AC Real Power | 1593 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Reactive Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_Q3W | AC Reactive Power | 1594 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_004 | Power Factor | 1595 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage A-B | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1596 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage B-C | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1597 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage C-A | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1598 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Current A | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_IAW | Phase Currents | 1599 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Current B | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_IBW | Phase Currents | 1600 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Current C | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_ICW | Phase Currents | 1601 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Frequency | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_FREQ | Frequency | 1602 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_A Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PAW | Phase Power | 1603 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_B Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PBW | Phase Power | 1604 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PCW | Phase Power | 1605 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage A-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VAZ | L-N Phase Voltages | 1606 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage B-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VBZ | L-N Phase Voltages | 1607 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Voltage C-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VCZ | L-N Phase Voltages | 1608 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_A Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SAW | Phase Apparent Power | 1609 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_B Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SBW | Phase Apparent Power | 1610 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SCW | Phase Apparent Power | 1611 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_A Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_001 | Phase Power Factor | 1612 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_B Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_002 | Phase Power Factor | 1613 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_003 | Phase Power Factor | 1614 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_1 MVAR Contribution | Reactive Power Relay | RTAC_LOGIC.87VC2P_MVAR_Contribution | MVAR Contribution | 1615 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Real Power-AC | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_P3W | AC Real Power | 1616 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Reactive Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_Q3W | AC Reactive Power | 1617 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_004 | Power Factor | 1618 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage A-B | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1619 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage B-C | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1620 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage C-A | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1621 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Current A | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_IAW | Phase Currents | 1622 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Current B | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_IBW | Phase Currents | 1623 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Current C | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_ICW | Phase Currents | 1624 | A | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Frequency | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_FREQ | Frequency | 1625 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_A Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PAW | Phase Power | 1626 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_B Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PBW | Phase Power | 1627 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PCW | Phase Power | 1628 | W | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage A-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VAZ | L-N Phase Voltages | 1629 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage B-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VBZ | L-N Phase Voltages | 1630 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Voltage C-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VCZ | L-N Phase Voltages | 1631 | V | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_A Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SAW | Phase Apparent Power | 1632 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_B Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SBW | Phase Apparent Power | 1633 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SCW | Phase Apparent Power | 1634 | VA | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_A Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_001 | Phase Power Factor | 1635 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_B Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_002 | Phase Power Factor | 1636 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_003 | Phase Power Factor | 1637 | Unitless | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Real Power-AC | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1638 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1639 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1640 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage A-B | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1641 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage B-C | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1642 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage C-A | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1643 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1644 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1645 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1646 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Frequency | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1647 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1648 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Current THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1649 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1650 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1651 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1652 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage A-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1653 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage B-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1654 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage C-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1655 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1656 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1657 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1658 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1659 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1660 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1661 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Real Power-AC | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1662 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1663 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1664 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage A-B | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1665 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage B-C | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1666 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage C-A | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1667 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1668 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1669 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1670 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Frequency | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1671 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1672 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Current THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1673 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1674 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1675 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1676 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage A-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1677 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage B-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1678 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage C-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1679 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1680 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1681 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1682 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1683 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1684 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1685 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Real Power-AC | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1686 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1687 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1688 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage A-B | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1689 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage B-C | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1690 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage C-A | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1691 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1692 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1693 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1694 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Frequency | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1695 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage THD | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1696 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Current THD | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1697 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1698 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1699 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1700 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage A-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1701 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage B-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1702 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage C-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1703 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1704 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1705 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1706 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1707 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1708 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1709 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Real Power-AC | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1710 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1711 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1712 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage A-B | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1713 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage B-C | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1714 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage C-A | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1715 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1716 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1717 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1718 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Frequency | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1719 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage THD | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1720 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Current THD | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1721 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1722 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1723 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1724 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage A-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1725 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage B-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1726 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage C-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1727 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1728 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1729 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1730 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1731 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1732 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1733 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Real Power-AC | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1734 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1735 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1736 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage A-B | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1737 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage B-C | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1738 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage C-A | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1739 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1740 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1741 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1742 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Frequency | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1743 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage THD | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1744 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Current THD | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1745 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1746 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1747 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1748 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage A-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1749 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage B-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1750 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage C-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1751 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1752 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1753 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1754 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1755 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1756 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1757 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Real Power-AC | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1758 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1759 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1760 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage A-B | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1761 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage B-C | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1762 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage C-A | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1763 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1764 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1765 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1766 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Frequency | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1767 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage THD | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1768 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Current THD | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1769 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1770 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1771 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1772 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage A-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1773 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage B-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1774 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage C-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1775 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1776 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1777 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1778 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1779 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1780 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1781 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Real Power-AC | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1782 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1783 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1784 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage A-B | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1785 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage B-C | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1786 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage C-A | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1787 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1788 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1789 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1790 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Frequency | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1791 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage THD | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1792 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Current THD | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1793 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1794 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1795 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1796 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage A-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1797 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage B-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1798 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage C-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1799 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1800 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1801 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1802 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1803 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1804 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1805 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Real Power-AC | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1806 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1807 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1808 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage A-B | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1809 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage B-C | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1810 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage C-A | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1811 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1812 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1813 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1814 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Frequency | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1815 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage THD | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1816 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Current THD | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1817 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1818 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1819 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1820 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage A-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1821 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage B-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1822 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage C-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1823 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1824 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1825 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1826 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1827 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1828 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1829 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Real Power-AC | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1830 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1831 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1832 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage A-B | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1833 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage B-C | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1834 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage C-A | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1835 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1836 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1837 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1838 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Frequency | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1839 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage THD | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1840 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Current THD | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1841 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1842 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1843 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1844 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage A-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1845 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage B-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1846 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage C-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1847 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1848 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1849 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1850 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1851 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1852 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1853 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Real Power-AC | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1854 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1855 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1856 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage A-B | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1857 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage B-C | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1858 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage C-A | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1859 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1860 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1861 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1862 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Frequency | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1863 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage THD | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1864 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Current THD | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1865 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1866 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1867 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1868 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage A-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1869 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage B-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1870 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage C-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1871 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1872 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1873 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1874 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1875 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1876 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1877 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Real Power-AC | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1878 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1879 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1880 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage A-B | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1881 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage B-C | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1882 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage C-A | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1883 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1884 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1885 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1886 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Frequency | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1887 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage THD | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1888 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Current THD | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1889 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1890 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1891 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1892 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage A-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1893 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage B-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1894 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage C-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1895 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1896 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1897 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1898 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1899 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1900 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1901 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Real Power-AC | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1902 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1903 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1904 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage A-B | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1905 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage B-C | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1906 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage C-A | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1907 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1908 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1909 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1910 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Frequency | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1911 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage THD | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1912 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Current THD | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1913 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1914 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1915 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1916 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage A-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1917 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage B-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1918 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage C-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1919 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1920 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1921 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1922 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1923 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1924 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1925 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Real Power-AC | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 1926 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 1927 | VAR | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 1928 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage A-B | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1929 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage B-C | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1930 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage C-A | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 1931 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 1932 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 1933 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 1934 | A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Frequency | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 1935 | Hz | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage THD | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 1936 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Current THD | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 1937 | % | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 1938 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 1939 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 1940 | W | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage A-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1941 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage B-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1942 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage C-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 1943 | V | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 1944 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 1945 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 1946 | VA | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 1947 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 1948 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 1949 | N/A | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Fan Stage | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_000_FAN_STAGE | Stage fan status | 1950 | 0,1,2 | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Temperature Oil | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_001_TEMPERATURE_OIL | Oil Temperature | 1951 | °C | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Temperature Winding | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_002_TEMPERATURE_WINDING | Winding Temperature | 1952 | °C | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Pressure | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_003_PRESSURE | Pressure | 1953 | hPa | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Oil Level | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_004_OIL_LEVEL | Oil Level | 1954 | % | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Tap Position | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.ANALOG_INPUT_005_TAP_POSITION | Transformer Tap Position |  | Tap Number | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Fan Stage | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_000_FAN_STAGE | Stage fan status |  | 0,1,2 | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Temperature Oil | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_001_TEMPERATURE_OIL | Oil Temperature |  | °C | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Temperature Winding | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_002_TEMPERATURE_WINDING | Winding Temperature |  | °C | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Pressure | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_003_PRESSURE | Pressure |  | hPa | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Oil Level | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_004_OIL_LEVEL | Oil Level |  | % | Requested-Not Applicable |  |  | 1
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Tap Position | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.ANALOG_INPUT_005_TAP_POSITION | Transformer Tap Position | 1955 | Tap Number | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Fan Stage | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_000_FAN_STAGE | Stage fan status | 1956 | 0,1,2 | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Temperature Oil | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_001_TEMPERATURE_OIL | Oil Temperature | 1957 | °C | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Temperature Winding | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_002_TEMPERATURE_WINDING | Winding Temperature | 1958 | °C | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Pressure | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_003_PRESSURE | Pressure | 1959 | hPa | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Oil Level | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_004_OIL_LEVEL | Oil Level | 1960 | % | Requested-Available |  |  | 1
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Tap Position | Medium-High Voltage Transformer | SEL_2414_T2_DNP.ANALOG_INPUT_005_TAP_POSITION | Transformer Tap Position |  | Tap Number | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Fan Stage | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_000_FAN_STAGE | Stage fan status |  | 0,1,2 | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Temperature Oil | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_001_TEMPERATURE_OIL | Oil Temperature |  | °C | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Temperature Winding | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_002_TEMPERATURE_WINDING | Winding Temperature |  | °C | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Pressure | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_003_PRESSURE | Pressure |  | hPa | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Oil Level | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_004_OIL_LEVEL | Oil Level |  | % | Requested-Not Applicable |  |  | 1
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Tap Position | Medium-High Voltage Transformer | BECKWITH_M_2001C_T2_90_DNP.ANALOG_INPUT_005_TAP_POSITION | Transformer Tap Position | 1961 | Tap Number | Requested-Available |  |  | 1
Digital Inputs
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 1 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 0 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 1 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 2 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 3 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 4 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 5 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 6 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 7 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Invalid GMS Unit 1 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 8 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 9 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 10 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 11 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 12 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 13 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 14 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 15 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 16 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 17 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 18 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 19 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 20 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 21 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 22 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 23 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 24 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 25 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 26 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 27 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 28 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 29 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 30 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 3rdParty Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 31 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Breaker Closed | PPC |  | BESS Site Breaker Status Indicator | 32 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Relay Faulted | PPC |  | BESS Site Protection Relay Fault Indictor | 33 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Auto Operation Enabled | PPC |  | BESS Site Auto-operation Indicator | 34 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Locked | PPC |  | BESS Site ESS Lock Indicator | 35 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Running | PPC |  | BESS Site ESS Run Indicator | 36 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Auto Start Enabled | PPC |  | BESS Site ESS Auto-start Indicator | 37 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Remote Control Enabled | PPC |  | BESS Site ESS Remote Control Indicator | 38 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Warning | PPC |  | BESS Site ESS Warning Indicator | 39 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Faulted | PPC |  | BESS Site ESS Fault Indicator | 40 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 41 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Running | PPC |  | BESS Site ESS Unit Run Indicator | 42 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 43 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 44 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 45 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 46 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 47 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 48 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 49 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 50 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 51 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Running | PPC |  | BESS Site ESS Unit Run Indicator | 52 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 53 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 54 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 55 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 56 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 57 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 58 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 59 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 60 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 61 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Running | PPC |  | BESS Site ESS Unit Run Indicator | 62 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 63 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 64 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 65 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 66 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 67 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 68 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 69 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 70 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 71 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Running | PPC |  | BESS Site ESS Unit Run Indicator | 72 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 73 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 74 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 75 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 76 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 77 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 78 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 79 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 80 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 81 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Running | PPC |  | BESS Site ESS Unit Run Indicator | 82 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 83 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 84 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 85 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 86 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 87 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 88 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 89 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 90 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 91 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Running | PPC |  | BESS Site ESS Unit Run Indicator | 92 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 93 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 94 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 95 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 96 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 97 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 98 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 99 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 100 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 101 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Running | PPC |  | BESS Site ESS Unit Run Indicator | 102 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 103 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 104 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 105 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 106 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 107 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 108 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 109 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 110 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 111 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Running | PPC |  | BESS Site ESS Unit Run Indicator | 112 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 113 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 114 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 115 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 116 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 117 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 118 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 119 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 120 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 121 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Running | PPC |  | BESS Site ESS Unit Run Indicator | 122 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 123 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 124 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 125 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 126 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 127 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 128 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 129 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 130 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 131 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Running | PPC |  | BESS Site ESS Unit Run Indicator | 132 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 133 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 134 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 135 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 136 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 137 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 138 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 139 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 140 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 141 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Running | PPC |  | BESS Site ESS Unit Run Indicator | 142 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 143 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 144 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 145 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 146 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 147 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 148 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 149 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 150 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 151 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Running | PPC |  | BESS Site ESS Unit Run Indicator | 152 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 153 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 154 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 155 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 156 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 157 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 158 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 159 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 160 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 161 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Running | PPC |  | BESS Site ESS Unit Run Indicator | 162 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 163 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 164 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 165 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 166 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 167 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 168 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 169 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 170 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 171 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Running | PPC |  | BESS Site ESS Unit Run Indicator | 172 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 173 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 174 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 175 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 176 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 177 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 178 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 179 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 180 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 181 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Running | PPC |  | BESS Site ESS Unit Run Indicator | 182 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 183 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 184 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 185 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 186 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 187 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 188 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 189 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 190 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 191 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Running | PPC |  | BESS Site ESS Unit Run Indicator | 192 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 193 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 194 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 195 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 196 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 197 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 198 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 199 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 200 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 201 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Running | PPC |  | BESS Site ESS Unit Run Indicator | 202 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 203 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 204 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 205 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 206 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 207 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 208 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 209 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 210 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 211 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Running | PPC |  | BESS Site ESS Unit Run Indicator | 212 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 213 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 214 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 215 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 216 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 217 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 218 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 219 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 220 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 221 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Running | PPC |  | BESS Site ESS Unit Run Indicator | 222 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 223 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 224 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 225 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 226 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 227 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 228 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 229 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 230 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 231 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Running | PPC |  | BESS Site ESS Unit Run Indicator | 232 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 233 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 234 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 235 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 236 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 237 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 238 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 239 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 240 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 2 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 241 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 242 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 243 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 244 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 245 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 246 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 247 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 248 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Invalid GMS Unit 2 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 249 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 250 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 251 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 252 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 253 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 254 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 255 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 256 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 257 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 258 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 259 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 260 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 261 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 262 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 263 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 264 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 265 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 266 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 267 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 268 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 269 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 270 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 271 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 3rdParty Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 272 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Breaker Closed | PPC |  | BESS Site Breaker Status Indicator | 273 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Relay Faulted | PPC |  | BESS Site Protection Relay Fault Indictor | 274 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Auto Operation Enabled | PPC |  | BESS Site Auto-operation Indicator | 275 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Locked | PPC |  | BESS Site ESS Lock Indicator | 276 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Running | PPC |  | BESS Site ESS Run Indicator | 277 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Auto Start Enabled | PPC |  | BESS Site ESS Auto-start Indicator | 278 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Remote Control Enabled | PPC |  | BESS Site ESS Remote Control Indicator | 279 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Warning | PPC |  | BESS Site ESS Warning Indicator | 280 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Faulted | PPC |  | BESS Site ESS Fault Indicator | 281 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 282 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Running | PPC |  | BESS Site ESS Unit Run Indicator | 283 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 284 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 285 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 286 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 287 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 288 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 289 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 290 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 291 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 292 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Running | PPC |  | BESS Site ESS Unit Run Indicator | 293 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 294 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 295 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 296 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 297 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 298 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 299 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 300 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 301 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 3 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 302 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 303 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 304 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 305 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 306 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 307 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 308 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 309 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Invalid GMS Unit 3 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 310 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 311 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 312 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 313 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 314 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 315 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 316 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 317 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 318 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 319 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 320 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 321 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 322 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 323 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 324 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 325 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 326 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 327 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 328 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 329 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 330 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 331 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 332 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 3rdParty Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 333 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Breaker Closed | PPC |  | BESS Site Breaker Status Indicator | 334 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Relay Faulted | PPC |  | BESS Site Protection Relay Fault Indictor | 335 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Auto Operation Enabled | PPC |  | BESS Site Auto-operation Indicator | 336 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Locked | PPC |  | BESS Site ESS Lock Indicator | 337 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Running | PPC |  | BESS Site ESS Run Indicator | 338 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Auto Start Enabled | PPC |  | BESS Site ESS Auto-start Indicator | 339 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Remote Control Enabled | PPC |  | BESS Site ESS Remote Control Indicator | 340 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Warning | PPC |  | BESS Site ESS Warning Indicator | 341 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Faulted | PPC |  | BESS Site ESS Fault Indicator | 342 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 343 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Running | PPC |  | BESS Site ESS Unit Run Indicator | 344 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 345 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 346 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 347 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 348 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 349 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 350 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 351 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 352 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 353 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Running | PPC |  | BESS Site ESS Unit Run Indicator | 354 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 355 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 356 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 357 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 358 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 359 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 360 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 361 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 362 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 4 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 363 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 364 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 365 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 366 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 367 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 368 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 369 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 370 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Invalid GMS Unit 4 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 371 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 372 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 373 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 374 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 375 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 376 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 377 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 378 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 379 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 380 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 381 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 382 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 383 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 384 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 385 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 386 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 387 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 388 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 389 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 390 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 391 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 392 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 393 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 3rdParty Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 394 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Breaker Closed | PPC |  | BESS Site Breaker Status Indicator | 395 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Relay Faulted | PPC |  | BESS Site Protection Relay Fault Indictor | 396 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Auto Operation Enabled | PPC |  | BESS Site Auto-operation Indicator | 397 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Locked | PPC |  | BESS Site ESS Lock Indicator | 398 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Running | PPC |  | BESS Site ESS Run Indicator | 399 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Auto Start Enabled | PPC |  | BESS Site ESS Auto-start Indicator | 400 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Remote Control Enabled | PPC |  | BESS Site ESS Remote Control Indicator | 401 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Warning | PPC |  | BESS Site ESS Warning Indicator | 402 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Faulted | PPC |  | BESS Site ESS Fault Indicator | 403 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 404 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Running | PPC |  | BESS Site ESS Unit Run Indicator | 405 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 406 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 407 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 408 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 409 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 410 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 411 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 412 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 413 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 414 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Running | PPC |  | BESS Site ESS Unit Run Indicator | 415 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 416 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 417 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 418 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 419 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 420 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 421 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 422 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 423 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 424 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Running | PPC |  | BESS Site ESS Unit Run Indicator | 425 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 426 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 427 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 428 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 429 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 430 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 431 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 432 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 433 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 434 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Running | PPC |  | BESS Site ESS Unit Run Indicator | 435 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 436 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 437 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 438 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 439 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 440 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 441 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 442 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 443 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 444 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Running | PPC |  | BESS Site ESS Unit Run Indicator | 445 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 446 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 447 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 448 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 449 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 450 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 451 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 452 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 453 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 5 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 454 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 455 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 456 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 457 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 458 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 459 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 460 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 461 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Invalid GMS Unit 5 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 462 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 463 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 464 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 465 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 466 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 467 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 468 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 469 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 470 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 471 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 472 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 473 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 474 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 475 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 476 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 477 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 478 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 479 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 480 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 481 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 482 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 483 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 484 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 3rdParty Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 485 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Breaker Closed | PPC |  | BESS Site Breaker Status Indicator | 486 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Relay Faulted | PPC |  | BESS Site Protection Relay Fault Indictor | 487 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Auto Operation Enabled | PPC |  | BESS Site Auto-operation Indicator | 488 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Locked | PPC |  | BESS Site ESS Lock Indicator | 489 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Running | PPC |  | BESS Site ESS Run Indicator | 490 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Auto Start Enabled | PPC |  | BESS Site ESS Auto-start Indicator | 491 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Remote Control Enabled | PPC |  | BESS Site ESS Remote Control Indicator | 492 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Warning | PPC |  | BESS Site ESS Warning Indicator | 493 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Faulted | PPC |  | BESS Site ESS Fault Indicator | 494 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 495 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Running | PPC |  | BESS Site ESS Unit Run Indicator | 496 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 497 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 498 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 499 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 500 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 501 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 502 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 503 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 504 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 505 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Running | PPC |  | BESS Site ESS Unit Run Indicator | 506 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 507 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 508 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 509 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 510 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 511 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 512 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 513 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 514 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 515 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Running | PPC |  | BESS Site ESS Unit Run Indicator | 516 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 517 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 518 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 519 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 520 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 521 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 522 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 523 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 524 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 525 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Running | PPC |  | BESS Site ESS Unit Run Indicator | 526 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 527 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 528 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 529 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 530 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 531 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 532 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 533 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 534 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 535 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Running | PPC |  | BESS Site ESS Unit Run Indicator | 536 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 537 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 538 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 539 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 540 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 541 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 542 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 543 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 544 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 545 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Running | PPC |  | BESS Site ESS Unit Run Indicator | 546 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 547 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 548 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 549 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 550 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 551 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 552 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 553 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 554 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 555 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Running | PPC |  | BESS Site ESS Unit Run Indicator | 556 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 557 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 558 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 559 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 560 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 561 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 562 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 563 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 564 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 565 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Running | PPC |  | BESS Site ESS Unit Run Indicator | 566 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 567 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 568 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 569 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 570 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 571 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 572 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 573 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 574 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 575 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Running | PPC |  | BESS Site ESS Unit Run Indicator | 576 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 577 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 578 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 579 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 580 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 581 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 582 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 583 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 584 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 585 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Running | PPC |  | BESS Site ESS Unit Run Indicator | 586 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 587 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 588 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 589 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 590 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 591 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 592 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 593 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 594 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 595 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Running | PPC |  | BESS Site ESS Unit Run Indicator | 596 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 597 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 598 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 599 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 600 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 601 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 602 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 603 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 604 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 605 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Running | PPC |  | BESS Site ESS Unit Run Indicator | 606 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 607 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 608 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 609 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 610 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 611 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 612 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 613 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 614 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 615 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Running | PPC |  | BESS Site ESS Unit Run Indicator | 616 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 617 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 618 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 619 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 620 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 621 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 622 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 623 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 624 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 625 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Running | PPC |  | BESS Site ESS Unit Run Indicator | 626 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 627 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 628 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 629 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 630 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 631 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 632 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 633 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 634 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 635 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Running | PPC |  | BESS Site ESS Unit Run Indicator | 636 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 637 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 638 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 639 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 640 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 641 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 642 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 643 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 644 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 645 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Running | PPC |  | BESS Site ESS Unit Run Indicator | 646 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 647 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 648 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 649 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 650 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 651 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 652 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 653 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 654 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 655 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Running | PPC |  | BESS Site ESS Unit Run Indicator | 656 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 657 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 658 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 659 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 660 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 661 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 662 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 663 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 664 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Locked | PPC |  | BESS Site ESS Unit Lock Indicator | 665 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Running | PPC |  | BESS Site ESS Unit Run Indicator | 666 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Participating | PPC |  | BESS Site ESS Unit Site Participation Indicator | 667 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Warning | PPC |  | BESS Site ESS Unit Warning Indicator | 668 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Faulted | PPC |  | BESS Site ESS Unit Fault Indicator | 669 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Fire Warning | PPC |  | BESS Site ESS BOP Fire Alarm Warning Indicator | 670 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Fire Faulted | PPC |  | BESS Site ESS BOP Fire Alarm Fault Indicator | 671 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Door Warning | PPC |  | BESS Site ESS BOP Door Safety Warning Indicator | 672 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Door Faulted | PPC |  | BESS Site ESS BOP Door Safety Fault Indicator | 673 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Estop Faulted | PPC |  | BESS Site ESS BOP Estop Fault Indicator | 674 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV001 Control Status | PPC | PPC.status.inv001_enabled | Inverter Control Status | 675 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV002 Control Status | PPC | PPC.status.inv002_enabled | Inverter Control Status | 676 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV003 Control Status | PPC | PPC.status.inv003_enabled | Inverter Control Status | 677 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV004 Control Status | PPC | PPC.status.inv004_enabled | Inverter Control Status | 678 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV005 Control Status | PPC | PPC.status.inv005_enabled | Inverter Control Status | 679 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV006 Control Status | PPC | PPC.status.inv006_enabled | Inverter Control Status | 680 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV007 Control Status | PPC | PPC.status.inv007_enabled | Inverter Control Status | 681 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV008 Control Status | PPC | PPC.status.inv008_enabled | Inverter Control Status | 682 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV009 Control Status | PPC | PPC.status.inv009_enabled | Inverter Control Status | 683 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV010 Control Status | PPC | PPC.status.inv010_enabled | Inverter Control Status | 684 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV011 Control Status | PPC | PPC.status.inv011_enabled | Inverter Control Status | 685 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV012 Control Status | PPC | PPC.status.inv012_enabled | Inverter Control Status | 686 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV013 Control Status | PPC | PPC.status.inv013_enabled | Inverter Control Status | 687 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV014 Control Status | PPC | PPC.status.inv014_enabled | Inverter Control Status | 688 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV015 Control Status | PPC | PPC.status.inv015_enabled | Inverter Control Status | 689 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV016 Control Status | PPC | PPC.status.inv016_enabled | Inverter Control Status | 690 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV017 Control Status | PPC | PPC.status.inv017_enabled | Inverter Control Status | 691 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV018 Control Status | PPC | PPC.status.inv018_enabled | Inverter Control Status | 692 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV019 Control Status | PPC | PPC.status.inv019_enabled | Inverter Control Status | 693 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV020 Control Status | PPC | PPC.status.inv020_enabled | Inverter Control Status | 694 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV021 Control Status | PPC | PPC.status.inv021_enabled | Inverter Control Status | 695 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV022 Control Status | PPC | PPC.status.inv022_enabled | Inverter Control Status | 696 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV023 Control Status | PPC | PPC.status.inv023_enabled | Inverter Control Status | 697 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV024 Control Status | PPC | PPC.status.inv024_enabled | Inverter Control Status | 698 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV025 Control Status | PPC | PPC.status.inv025_enabled | Inverter Control Status | 699 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV026 Control Status | PPC | PPC.status.inv026_enabled | Inverter Control Status | 700 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV027 Control Status | PPC | PPC.status.inv027_enabled | Inverter Control Status | 701 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV028 Control Status | PPC | PPC.status.inv028_enabled | Inverter Control Status | 702 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV029 Control Status | PPC | PPC.status.inv029_enabled | Inverter Control Status | 703 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV030 Control Status | PPC | PPC.status.inv030_enabled | Inverter Control Status | 704 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV031 Control Status | PPC | PPC.status.inv031_enabled | Inverter Control Status | 705 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV032 Control Status | PPC | PPC.status.inv032_enabled | Inverter Control Status | 706 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV033 Control Status | PPC | PPC.status.inv033_enabled | Inverter Control Status | 707 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV034 Control Status | PPC | PPC.status.inv034_enabled | Inverter Control Status | 708 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV035 Control Status | PPC | PPC.status.inv035_enabled | Inverter Control Status | 709 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV036 Control Status | PPC | PPC.status.inv036_enabled | Inverter Control Status | 710 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV037 Control Status | PPC | PPC.status.inv037_enabled | Inverter Control Status | 711 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV038 Control Status | PPC | PPC.status.inv038_enabled | Inverter Control Status | 712 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV039 Control Status | PPC | PPC.status.inv039_enabled | Inverter Control Status | 713 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV040 Control Status | PPC | PPC.status.inv040_enabled | Inverter Control Status | 714 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV041 Control Status | PPC | PPC.status.inv041_enabled | Inverter Control Status | 715 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV042 Control Status | PPC | PPC.status.inv042_enabled | Inverter Control Status | 716 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV043 Control Status | PPC | PPC.status.inv043_enabled | Inverter Control Status | 717 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV044 Control Status | PPC | PPC.status.inv044_enabled | Inverter Control Status | 718 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV045 Control Status | PPC | PPC.status.inv045_enabled | Inverter Control Status | 719 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV046 Control Status | PPC | PPC.status.inv046_enabled | Inverter Control Status | 720 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV047 Control Status | PPC | PPC.status.inv047_enabled | Inverter Control Status | 721 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV048 Control Status | PPC | PPC.status.inv048_enabled | Inverter Control Status | 722 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV049 Control Status | PPC | PPC.status.inv049_enabled | Inverter Control Status | 723 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV050 Control Status | PPC | PPC.status.inv050_enabled | Inverter Control Status | 724 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV051 Control Status | PPC | PPC.status.inv051_enabled | Inverter Control Status | 725 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV052 Control Status | PPC | PPC.status.inv052_enabled | Inverter Control Status | 726 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV053 Control Status | PPC | PPC.status.inv053_enabled | Inverter Control Status | 727 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV054 Control Status | PPC | PPC.status.inv054_enabled | Inverter Control Status | 728 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV055 Control Status | PPC | PPC.status.inv055_enabled | Inverter Control Status | 729 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV056 Control Status | PPC | PPC.status.inv056_enabled | Inverter Control Status | 730 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV057 Control Status | PPC | PPC.status.inv057_enabled | Inverter Control Status | 731 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV058 Control Status | PPC | PPC.status.inv058_enabled | Inverter Control Status | 732 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV059 Control Status | PPC | PPC.status.inv059_enabled | Inverter Control Status | 733 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV060 Control Status | PPC | PPC.status.inv060_enabled | Inverter Control Status | 734 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV061 Control Status | PPC | PPC.status.inv061_enabled | Inverter Control Status | 735 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV062 Control Status | PPC | PPC.status.inv062_enabled | Inverter Control Status | 736 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV063 Control Status | PPC | PPC.status.inv063_enabled | Inverter Control Status | 737 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV064 Control Status | PPC | PPC.status.inv064_enabled | Inverter Control Status | 738 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV065 Control Status | PPC | PPC.status.inv065_enabled | Inverter Control Status | 739 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV066 Control Status | PPC | PPC.status.inv066_enabled | Inverter Control Status | 740 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV067 Control Status | PPC | PPC.status.inv067_enabled | Inverter Control Status | 741 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV068 Control Status | PPC | PPC.status.inv068_enabled | Inverter Control Status | 742 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV069 Control Status | PPC | PPC.status.inv069_enabled | Inverter Control Status | 743 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV070 Control Status | PPC | PPC.status.inv070_enabled | Inverter Control Status | 744 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV071 Control Status | PPC | PPC.status.inv071_enabled | Inverter Control Status | 745 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV072 Control Status | PPC | PPC.status.inv072_enabled | Inverter Control Status | 746 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV073 Control Status | PPC | PPC.status.inv073_enabled | Inverter Control Status | 747 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV074 Control Status | PPC | PPC.status.inv074_enabled | Inverter Control Status | 748 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV075 Control Status | PPC | PPC.status.inv075_enabled | Inverter Control Status | 749 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV076 Control Status | PPC | PPC.status.inv076_enabled | Inverter Control Status | 750 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV077 Control Status | PPC | PPC.status.inv077_enabled | Inverter Control Status | 751 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV078 Control Status | PPC | PPC.status.inv078_enabled | Inverter Control Status | 752 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV079 Control Status | PPC | PPC.status.inv079_enabled | Inverter Control Status | 753 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV080 Control Status | PPC | PPC.status.inv080_enabled | Inverter Control Status | 754 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV081 Control Status | PPC | PPC.status.inv081_enabled | Inverter Control Status | 755 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV082 Control Status | PPC | PPC.status.inv082_enabled | Inverter Control Status | 756 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV083 Control Status | PPC | PPC.status.inv083_enabled | Inverter Control Status | 757 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV084 Control Status | PPC | PPC.status.inv084_enabled | Inverter Control Status | 758 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV085 Control Status | PPC | PPC.status.inv085_enabled | Inverter Control Status | 759 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV086 Control Status | PPC | PPC.status.inv086_enabled | Inverter Control Status | 760 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV087 Control Status | PPC | PPC.status.inv087_enabled | Inverter Control Status | 761 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV088 Control Status | PPC | PPC.status.inv088_enabled | Inverter Control Status | 762 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV089 Control Status | PPC | PPC.status.inv089_enabled | Inverter Control Status | 763 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV090 Control Status | PPC | PPC.status.inv090_enabled | Inverter Control Status | 764 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV091 Control Status | PPC | PPC.status.inv091_enabled | Inverter Control Status | 765 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV092 Control Status | PPC | PPC.status.inv092_enabled | Inverter Control Status | 766 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV093 Control Status | PPC | PPC.status.inv093_enabled | Inverter Control Status | 767 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV094 Control Status | PPC | PPC.status.inv094_enabled | Inverter Control Status | 768 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_INV095 Control Status | PPC | PPC.status.inv095_enabled | Inverter Control Status | 769 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | SOIL094 | Dagget 3_SUB1_SOIL094_Communication Status | Soiling Station | MET94_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL087 | Dagget 3_SUB1_SOIL087_Communication Status | Soiling Station | MET87_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL083 | Dagget 3_SUB1_SOIL083_Communication Status | Soiling Station | MET83_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL075 | Dagget 3_SUB1_SOIL075_Communication Status | Soiling Station | MET75_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL068 | Dagget 3_SUB1_SOIL068_Communication Status | Soiling Station | MET68_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL052 | Dagget 3_SUB1_SOIL052_Communication Status | Soiling Station | MET52_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL012 | Dagget 3_SUB1_SOIL012_Communication Status | Soiling Station | MET12_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL011 | Dagget 3_SUB1_SOIL011_Communication Status | Soiling Station | MET11_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL065 | Dagget 3_SUB1_SOIL065_Communication Status | Soiling Station | MET65_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL044 | Dagget 3_SUB1_SOIL044_Communication Status | Soiling Station | MET44_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL050 | Dagget 3_SUB1_SOIL050_Communication Status | Soiling Station | MET50_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL019 | Dagget 3_SUB1_SOIL019_Communication Status | Soiling Station | MET19_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL008 | Dagget 3_SUB1_SOIL008_Communication Status | Soiling Station | MET08_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL023 | Dagget 3_SUB1_SOIL023_Communication Status | Soiling Station | MET23_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL034 | Dagget 3_SUB1_SOIL034_Communication Status | Soiling Station | MET34_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL031 | Dagget 3_SUB1_SOIL031_Communication Status | Soiling Station | MET31_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL042 | Dagget 3_SUB1_SOIL042_Communication Status | Soiling Station | MET42_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Communications Status | Line Relay | GE_L90_87L1P_DNP_POU.Offline | Communication Status | 770 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Relay Enabled | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00000_ENABLED | Relay Online | 771 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Software Alarm | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00001_TROUBLE | Software Alarm | 772 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Hardware Alarm | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00002_ALARM | Hardware Alarm | 773 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Breaker Fail Initiate | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00003_OUT_H3 | Breaker Fail Initiate | 774 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Line Comm Cutout | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00004_Line_Relaying_Comm_Cutout | Line Relaying Comm Cutout | 775 | 0 = Normal, 1 = Cutout | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Line Comm Failure | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00005_Line_Relaying_Comm_Failure | Line Relaying Comm Failure | 776 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Direct Transfer Trip | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00006_Direct_Transfer_Trip | Direct Transfer Trip | 777 | 0 = Normal, 1 = Trip | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Communications Status | Line Relay | SEL_411L_87L1S_SEL_POU.Offline | Communication Status | 778 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Relay Enabled | Line Relay | SEL_411L_87L1S_SEL_POU.EN | Relay Online | 779 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Software Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_SALARM | Software Alarm | 780 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Hardware Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_HALARM | Hardware Alarm | 781 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Breaker Fail Initiate | Line Relay | SEL_411L_87L1S_SEL.FM_INST_OUT203 | Breaker Fail Initiate | 782 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Line Comm Cutout | Line Relay |  | Line Relaying Comm Cutout |  | 0 = Normal, 1 = Cutout | Requested-Not Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Line Comm Failure | Line Relay |  | Line Relaying Comm Failure |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ Direct Transfer Trip | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 783 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 52L1 Breaker Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 784 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 87L Enable/Disable | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 785 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 89L11 MOD Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 786 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 89L12 MOD Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 787 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 89L11 Remote/Local | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 788 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_ 89L12 Remote/Local | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 789 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Communications Status | Line Relay | GE_L90_87L2P_DNP_POU.Offline | Communication Status | 790 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Relay Enabled | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00000_ENABLED | Relay Online | 791 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Software Alarm | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00001_TROUBLE | Software Alarm | 792 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Hardware Alarm | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00002_ALARM | Hardware Alarm | 793 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Breaker Fail Initiate | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00003_OUT_H3 | Breaker Fail Initiate | 794 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Line Comm Cutout | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00004_Line_Relaying_Comm_Cutout | Line Relaying Comm Cutout | 795 | 0 = Normal, 1 = Cutout | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Line Comm Failure | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00005_Line_Relaying_Comm_Failure | Line Relaying Comm Failure | 796 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Direct Transfer Trip | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00006_Direct_Transfer_Trip | Direct Transfer Trip | 797 | 0 = Normal, 1 = Trip | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_52L1 Breaker Status | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00007_52L1_Breaker_Status | Hard Wired Contacts | 798 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_52T1 Breaker Status | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00008_52T1_Breaker_Status | Hard Wired Contacts | 799 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_52T2 Breaker Status | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00009_52T2_Breaker_Status | Hard Wired Contacts | 800 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_DTT Send | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00010_DTT_Send | Hard Wired Contacts | 801 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_87L Enable/Disable | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00022_87L_Enable/Disable | Hard Wired Contacts | 802 | 0 = Enabled, 1 = Disabled | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Communications Status | Line Relay | SEL_411L_87L1S_SEL_POU.Offline | Communication Status | 803 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Relay Enabled | Line Relay | SEL_411L_87L1S_SEL_POU.EN | Relay Online | 804 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Software Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_SALARM | Software Alarm | 805 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Hardware Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_HALARM | Hardware Alarm | 806 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Breaker Fail Initiate | Line Relay | SEL_411L_87L1S_SEL.FM_INST_OUT203 | Breaker Fail Initiate | 807 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Line Comm Cutout | Line Relay |  | Line Relaying Comm Cutout |  | 0 = Normal, 1 = Cutout | Requested-Not Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Line Comm Failure | Line Relay |  | Line Relaying Comm Failure |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Direct Transfer Trip | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 808 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52L1 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 809 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52T1 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 810 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52T2 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 811 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_87L Enable/Disable | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 812 | 0 = Enabled, 1 = Disabled | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L21 MOD Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 813 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L21 Remote/Local | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 814 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Communications Status | Transformer Relay | SEL_487E_87T1P_SEL_POU.Offline | Communication Status | 815 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Relay Enabled | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_EN | Relay Online | 816 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Software Alarm | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_SALARM | Software Alarm | 817 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Hardware Alarm | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_HALARM | Hardware Alarm | 818 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Breaker Fail Initiate | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN206 | Breaker Fail Initiate | 819 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Rapid Pressure Rise | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN101 | Hard Wired Contacts | 820 | 0 = Normal, 1 = Rise | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Pressure Relief Device Trip | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN102 | Hard Wired Contacts | 821 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Buchholz Fault Pressure Trip | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN103 | Hard Wired Contacts | 822 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_LTC Protective Relay Trip | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN104 | Hard Wired Contacts | 823 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Oil Temp Trip | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN105 | Hard Wired Contacts | 824 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86T1P TRIP IND | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN106 | Hard Wired Contacts | 825 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86T1P Coil Fail Status | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN107 | Hard Wired Contacts | 826 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_94T11 Trip Status | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 827 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_94T12 TRIP IND | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 828 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 Breaker Status | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 829 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86BFT1 Trip Status | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 830 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86BFT1 Coil Fail Status | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 831 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_89T1 Remote/Local In Control House | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 832 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 MCB Trip | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN208 | Hard Wired Contacts | 833 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 Low SF6 Gas Lockout | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN209 | Hard Wired Contacts | 834 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 TCM1 | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN213 | Hard Wired Contacts | 835 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 TCM2 | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN214 | Hard Wired Contacts | 836 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F1 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN216 | Hard Wired Contacts | 837 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F2 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN217 | Hard Wired Contacts | 838 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F3 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN218 | Hard Wired Contacts | 839 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F4 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN219 | Hard Wired Contacts | 840 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F5 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN220 | Hard Wired Contacts | 841 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F6 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN221 | Hard Wired Contacts | 842 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F7 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN222 | Hard Wired Contacts | 843 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F8 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN223 | Hard Wired Contacts | 844 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F9 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN224 | Hard Wired Contacts | 845 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F10 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN225 | Hard Wired Contacts | 846 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_51F11 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN226 | Hard Wired Contacts | 847 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_87C1 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.F_TARGET2_IN227 | Hard Wired Contacts | 848 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Communications Status | Transformer Relay | SEL_387A_87T1S_SEL_POU.Offline | Communication Status | 849 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Relay Enabled | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_EN | Relay Online | 850 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Software Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_NOTALM | Software Alarm | 851 | 0 = Alarm, 1 = Normal | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Hardware Alarm | Transformer Relay |  | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Breaker Fail Initiate | Transformer Relay |  | Breaker Fail Initiate |  | 0 = Normal, 1 = BFI | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_86T1S Trip Status | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN101 | Hard Wired Contacts | 852 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_86T1S Coil Fail Satus | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN102 | Hard Wired Contacts | 853 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_DC Supply 125 VDC Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN103 | Hard Wired Contacts | 854 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_AC Supply 120 VAC Failure Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN103 | Hard Wired Contacts | 855 | 2 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_AC Supply 240 VAC Failure Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN103 | Hard Wired Contacts | 856 | 3 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Main Tank Oil Level High Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN104 | Hard Wired Contacts | 857 | 4 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_LTC Tank Oil Level Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN105 | Hard Wired Contacts | 858 | 5 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Top Oil Temp Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN106 | Hard Wired Contacts | 859 | 6 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Winding Temp Hot Spot Alarm | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN201 | Hard Wired Contacts | 860 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Sudden Pressure Relay Alarm 1 | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN202 | Hard Wired Contacts | 861 | 8 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Sudden Pressure Relay Alarm 2 | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IN203 | Hard Wired Contacts | 862 | 9 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Communications Status | Transformer Relay | SEL_487E_87T2P_SEL_POU.Offline | Communication Status | 863 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Relay Enabled | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_EN | Relay Online | 864 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Software Alarm | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_SALARM | Software Alarm | 865 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Hardware Alarm | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_HALARM | Hardware Alarm | 866 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Breaker Fail Initiate | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_IN206 | Breaker Fail Initiate | 867 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Rapid Pressure Rise | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN101 | Hard Wired Contacts | 868 | 0 = Normal, 1 = Rise | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Pressure Relief Device Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN102 | Hard Wired Contacts | 869 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Buchholz Pressure Rise Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN103 | Hard Wired Contacts | 870 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_LTC Protective Relay Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN104 | Hard Wired Contacts | 871 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86T2P Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN106 | Hard Wired Contacts | 872 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86T2P Coil Fail Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN107 | Hard Wired Contacts | 873 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_94T21 Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 874 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_94T22 Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 875 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 Breaker Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 876 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86BFT2 Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 877 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86BFT2 Coil Fail Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 878 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_89T1 Remote/Local At Breaker | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 879 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 MCB Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN208 | Hard Wired Contacts | 880 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 Low SF6 Gas Lockout | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN209 | Hard Wired Contacts | 881 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 TCM1 | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN213 | Hard Wired Contacts | 882 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 TCM2 | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN214 | Hard Wired Contacts | 883 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F12 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN216 | Hard Wired Contacts | 884 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F13 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN217 | Hard Wired Contacts | 885 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F14 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN218 | Hard Wired Contacts | 886 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F15 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN219 | Hard Wired Contacts | 887 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F16 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN220 | Hard Wired Contacts | 888 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_87C2 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN221 | Hard Wired Contacts | 889 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Communications Status | Transformer Relay | SEL_387A_87T2S_SEL_POU.Offline | Communication Status | 890 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_ Relay Enabled | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_EN | Relay Online | 891 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Software Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_NOTALM | Software Alarm | 892 | 0 = Alarm, 1 = Normal | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Hardware Alarm | Transformer Relay |  | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Breaker Fail Initiate | Transformer Relay |  | Breaker Fail Initiate |  | 0 = Normal, 1 = BFI | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_86T2S Trip Status | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN101 | Hard Wired Contacts | 893 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_86T2S Coil Fail Satus | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN102 | Hard Wired Contacts | 894 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_DC Control Power Loss Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN103 | Hard Wired Contacts | 895 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_AC Main Power Loss Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN103 | Hard Wired Contacts | 896 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_AC Control Power Loss Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN103 | Hard Wired Contacts | 897 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_90C Relay Fail Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN104 | Hard Wired Contacts | 898 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Buchholz Relay Gas Detector | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN105 | Hard Wired Contacts | 899 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Main Tank Oil Level High Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN106 | Hard Wired Contacts | 900 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Main Tank Oil Level Low Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN107 | Hard Wired Contacts | 901 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_LTC Tank Oil Level Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN201 | Hard Wired Contacts | 902 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Top Oil Temp Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN202 | Hard Wired Contacts | 903 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Winding Temp Hot Spot Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN203 | Hard Wired Contacts | 904 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Rapid Pressure Rise | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN204 | Hard Wired Contacts | 905 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Communications Status | Bus Relay | SEL_587Z_87BT1_SEL_POU.Offline | Communication Status | 906 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Relay Enabled | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_EN | Relay Online | 907 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Software Alarm | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_ALARM | Software Alarm | 908 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Hardware Alarm | Bus Relay |  | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_86BT1 Trip Status | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_IN1 | Hard Wired Contacts | 909 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_86BT1 Coil Fail Status | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_IN2 | Hard Wired Contacts | 910 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Communications Status | Bus Relay | SEL_587Z_87BT2_SEL_POU.Offline | Communication Status | 911 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Relay Enabled | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_EN | Relay Online | 912 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Software Alarm | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_ALARM | Software Alarm | 913 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Hardware Alarm | Bus Relay |  | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_86BT1 Trip Status | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_IN1 | Hard Wired Contacts | 914 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_86BT1 Coil Fail Status | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_IN2 | Hard Wired Contacts | 915 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Communications Status | Breaker Relay | SEL_351_50BFL1_SEL_POU.Offline | Communication Status | 916 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Relay Enabled | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_TLED11 | Relay Online | 917 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Software Alarm | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_SALARM | Software Alarm | 918 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Hardware Alarm | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_HALARM | Hardware Alarm | 919 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Breaker Status | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN101 | Hard Wired Contacts | 920 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Remote/Local In Control House | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN201 | Hard Wired Contacts | 921 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 Low SF6 Alarm | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN204 | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Breaker Fail Initiate | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN104 | Hard Wired Contacts | 922 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Direct Transfer Trip Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN105 | Hard Wired Contacts | 923 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 TCM1 | Breaker Relay |  | Hard Wired Contacts | 924 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 TCM2 | Breaker Relay |  | Hard Wired Contacts | 925 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_52L1 MCB Trip | Breaker Relay | SEL_351_50BFL1_SEL.FM_INST_IN203 | Hard Wired Contacts | 926 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Communications Status | Breaker Relay | SEL_351S_51F1_SEL_POU.Offline | Communication Status | 927 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Relay Enabled | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_TLED11 | Relay Online | 928 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Software Alarm | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_SALARM | Software Alarm | 929 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Hardware Alarm | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_HALARM | Hardware Alarm | 930 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Breaker Status | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN101 | Hard Wired Contacts | 931 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 932 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Remote/Local In Control House | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN102 | Hard Wired Contacts | 933 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 934 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 935 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 936 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 937 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 TCM1 | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN105 | Hard Wired Contacts | 938 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_52F1 TCM2 | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN106 | Hard Wired Contacts | 939 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Communications Status | Breaker Relay | SEL_351S_51F2_SEL_POU.Offline | Communication Status | 940 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Relay Enabled | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_TLED11 | Relay Online | 941 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Software Alarm | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_SALARM | Software Alarm | 942 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Hardware Alarm | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_HALARM | Hardware Alarm | 943 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Breaker Status | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN101 | Hard Wired Contacts | 944 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 945 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Remote/Local In Control House | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN102 | Hard Wired Contacts | 946 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 TCM1 | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN105 | Hard Wired Contacts | 947 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_52F2 TCM2 | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN106 | Hard Wired Contacts | 948 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Communications Status | Breaker Relay | SEL_351S_51F3_SEL_POU.Offline | Communication Status | 949 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Relay Enabled | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_TLED11 | Relay Online | 950 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Software Alarm | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_SALARM | Software Alarm | 951 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Hardware Alarm | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_HALARM | Hardware Alarm | 952 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Breaker Status | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN101 | Hard Wired Contacts | 953 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Remote/Local In Control House | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN102 | Hard Wired Contacts | 954 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 955 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 956 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 957 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 958 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 TCM1 | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN105 | Hard Wired Contacts | 959 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_52F3 TCM2 | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN106 | Hard Wired Contacts | 960 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Communications Status | Breaker Relay | SEL_351S_51F4_SEL_POU.Offline | Communication Status | 961 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Relay Enabled | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_TLED11 | Relay Online | 962 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Software Alarm | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_SALARM | Software Alarm | 963 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Hardware Alarm | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_HALARM | Hardware Alarm | 964 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Breaker Status | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN101 | Hard Wired Contacts | 965 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Remote/Local In Control House | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN102 | Hard Wired Contacts | 966 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 TCM1 | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN105 | Hard Wired Contacts | 967 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_52F4 TCM2 | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN106 | Hard Wired Contacts | 968 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Communications Status | Breaker Relay | SEL_351S_51F5_SEL_POU.Offline | Communication Status | 969 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Relay Enabled | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_TLED11 | Relay Online | 970 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Software Alarm | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_SALARM | Software Alarm | 971 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Hardware Alarm | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_HALARM | Hardware Alarm | 972 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Breaker Status | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN101 | Hard Wired Contacts | 973 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Remote/Local In Control House | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN102 | Hard Wired Contacts | 974 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 975 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 976 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 977 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 978 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 TCM1 | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN105 | Hard Wired Contacts | 979 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_52F5 TCM2 | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN106 | Hard Wired Contacts | 980 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Communications Status | Breaker Relay | SEL_351S_51F6_SEL_POU.Offline | Communication Status | 981 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Relay Enabled | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_TLED11 | Relay Online | 982 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Software Alarm | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_SALARM | Software Alarm | 983 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Hardware Alarm | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_HALARM | Hardware Alarm | 984 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Breaker Status | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN101 | Hard Wired Contacts | 985 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 986 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Remote/Local In Control House | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN102 | Hard Wired Contacts | 987 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 988 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 989 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 990 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 991 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 TCM1 | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN105 | Hard Wired Contacts | 992 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_52F6 TCM2 | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN106 | Hard Wired Contacts | 993 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Communications Status | Breaker Relay | SEL_351S_51F7_SEL_POU.Offline | Communication Status | 994 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Relay Enabled | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_TLED11 | Relay Online | 995 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Software Alarm | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_SALARM | Software Alarm | 996 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Hardware Alarm | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_HALARM | Hardware Alarm | 997 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Breaker Status | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN101 | Hard Wired Contacts | 998 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 999 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Remote/Local In Control House | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN102 | Hard Wired Contacts | 1000 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 1001 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 1002 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 1003 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 1004 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 TCM1 | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN105 | Hard Wired Contacts | 1005 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_52F7 TCM2 | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN106 | Hard Wired Contacts | 1006 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Communications Status | Breaker Relay | SEL_351S_51F8_SEL_POU.Offline | Communication Status | 1007 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Relay Enabled | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_TLED11 | Relay Online | 1008 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Software Alarm | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_SALARM | Software Alarm | 1009 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Hardware Alarm | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_HALARM | Hardware Alarm | 1010 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Breaker Status | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN101 | Hard Wired Contacts | 1011 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1012 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Remote/Local In Control House | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN102 | Hard Wired Contacts | 1013 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 1014 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 1015 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 1016 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 1017 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 TCM1 | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN105 | Hard Wired Contacts | 1018 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_52F8 TCM2 | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN106 | Hard Wired Contacts | 1019 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Communications Status | Breaker Relay | SEL_351S_51F9_SEL_POU.Offline | Communication Status | 1020 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Relay Enabled | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_TLED11 | Relay Online | 1021 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Software Alarm | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_SALARM | Software Alarm | 1022 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Hardware Alarm | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_HALARM | Hardware Alarm | 1023 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Breaker Status | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN101 | Hard Wired Contacts | 1024 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Remote/Local In Control House | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN102 | Hard Wired Contacts | 1025 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 TCM1 | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN105 | Hard Wired Contacts | 1026 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_52F9 TCM2 | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN106 | Hard Wired Contacts | 1027 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Communications Status | Breaker Relay | SEL_351S_51F10_SEL_POU.Offline | Communication Status | 1028 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Relay Enabled | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_TLED11 | Relay Online | 1029 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Software Alarm | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_SALARM | Software Alarm | 1030 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Hardware Alarm | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_HALARM | Hardware Alarm | 1031 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Breaker Status | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN101 | Hard Wired Contacts | 1032 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Remote/Local In Control House | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN102 | Hard Wired Contacts | 1033 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 TCM1 | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN105 | Hard Wired Contacts | 1034 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_52F10 TCM2 | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN106 | Hard Wired Contacts | 1035 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Communications Status | Breaker Relay | SEL_351S_51F11_SEL_POU.Offline | Communication Status | 1036 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Relay Enabled | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_TLED11 | Relay Online | 1037 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Software Alarm | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_SALARM | Software Alarm | 1038 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Hardware Alarm | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_HALARM | Hardware Alarm | 1039 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Breaker Status | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN101 | Hard Wired Contacts | 1040 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Remote/Local In Control House | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN102 | Hard Wired Contacts | 1041 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 1042 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 1043 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 1044 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 TCM1 | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN105 | Hard Wired Contacts | 1045 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_52F11 TCM2 | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN106 | Hard Wired Contacts | 1046 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Communications Status | Breaker Relay | SEL_351S_51F12_SEL_POU.Offline | Communication Status | 1047 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Relay Enabled | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_TLED11 | Relay Online | 1048 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Software Alarm | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_SALARM | Software Alarm | 1049 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Hardware Alarm | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_HALARM | Hardware Alarm | 1050 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Breaker Status | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN101 | Hard Wired Contacts | 1051 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Remote/Local In Control House | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN102 | Hard Wired Contacts | 1052 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 TCM1 | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN105 | Hard Wired Contacts | 1053 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_52F12 TCM2 | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN106 | Hard Wired Contacts | 1054 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Communications Status | Breaker Relay | SEL_351S_51F13_SEL_POU.Offline | Communication Status | 1055 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Relay Enabled | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_TLED11 | Relay Online | 1056 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Software Alarm | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_SALARM | Software Alarm | 1057 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Hardware Alarm | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_HALARM | Hardware Alarm | 1058 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Breaker Status | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN101 | Hard Wired Contacts | 1059 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Remote/Local In Control House | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN102 | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 TCM1 | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN105 | Hard Wired Contacts | 1060 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_52F13 TCM2 | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN106 | Hard Wired Contacts | 1061 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Communications Status | Breaker Relay | SEL_351S_51F14_SEL_POU.Offline | Communication Status | 1062 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Relay Enabled | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_TLED11 | Relay Online | 1063 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Software Alarm | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_SALARM | Software Alarm | 1064 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Hardware Alarm | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_HALARM | Hardware Alarm | 1065 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Breaker Status | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN101 | Hard Wired Contacts | 1066 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Remote/Local In Control House | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN102 | Hard Wired Contacts | 1067 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 TCM1 | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN105 | Hard Wired Contacts | 1068 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_52F14 TCM2 | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN106 | Hard Wired Contacts | 1069 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Communications Status | Breaker Relay | SEL_351S_51F15_SEL_POU.Offline | Communication Status | 1070 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Relay Enabled | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_TLED11 | Relay Online | 1071 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Software Alarm | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_SALARM | Software Alarm | 1072 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Hardware Alarm | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_HALARM | Hardware Alarm | 1073 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Breaker Status | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN101 | Hard Wired Contacts | 1074 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Remote/Local In Control House | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN102 | Hard Wired Contacts | 1075 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 TCM1 | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN105 | Hard Wired Contacts | 1076 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_52F15 TCM2 | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN106 | Hard Wired Contacts | 1077 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Communications Status | Breaker Relay | SEL_351S_51F16_SEL_POU.Offline | Communication Status | 1078 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Relay Enabled | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_TLED11 | Relay Online | 1079 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Software Alarm | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_SALARM | Software Alarm | 1080 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Hardware Alarm | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_HALARM | Hardware Alarm | 1081 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Breaker Status | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN101 | Hard Wired Contacts | 1082 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Remote/Local In Control House | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN102 | Hard Wired Contacts | 1083 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 TCM1 | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN105 | Hard Wired Contacts | 1084 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_52F16 TCM2 | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN106 | Hard Wired Contacts | 1085 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Communications Status | Reactive Power Relay | SEL_487V_87C1_SEL_POU.Offline | Communications Status | 1086 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Relay Enabled | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_EN | Relay Online | 1087 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Software Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_SALARM | Software Alarm | 1088 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_Hardware Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_HALARM | Hardware Alarm | 1089 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Breaker Status | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN101 | Hard Wired Contacts | 1090 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Remote/Local In Control House | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN102 | Hard Wired Contacts | 1091 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Switch Status | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Open, 1 = Closed | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_C1 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 TCM1 | Reactive Power Relay |  | Hard Wired Contacts | 1092 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C1 TCM2 | Reactive Power Relay |  | Hard Wired Contacts | 1093 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Status | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN204 | Hard Wired Contacts | 1094 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts | 1095 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts | 1096 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN207 | Hard Wired Contacts | 1097 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN207 | Hard Wired Contacts | 1098 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN205 | Hard Wired Contacts | 1099 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN206 | Hard Wired Contacts | 1100 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Status | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN208 | Hard Wired Contacts | 1101 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts | 1102 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts | 1103 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN211 | Hard Wired Contacts | 1104 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN211 | Hard Wired Contacts | 1105 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN209 | Hard Wired Contacts | 1106 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_IN210 | Hard Wired Contacts | 1107 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Communications Status | Reactive Power Relay | SEL_487V_87C2_SEL_POU.Offline | Communications Status | 1108 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Relay Enabled | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_EN | Relay Online | 1109 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Software Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_SALARM | Software Alarm | 1110 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_Hardware Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_HALARM | Hardware Alarm | 1111 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Breaker Status | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN101 | Hard Wired Contacts | 1112 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Remote/Local In Control House | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN102 | Hard Wired Contacts | 1113 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Switch Status | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Open, 1 = Closed | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_C2 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 TCM1 | Reactive Power Relay |  | Hard Wired Contacts | 1114 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 TCM2 | Reactive Power Relay |  | Hard Wired Contacts | 1115 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Status | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN204 | Hard Wired Contacts | 1116 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN207 | Hard Wired Contacts | 1117 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN207 | Hard Wired Contacts | 1118 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN205 | Hard Wired Contacts | 1119 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN206 | Hard Wired Contacts | 1120 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Status | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN208 | Hard Wired Contacts | 1121 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts | 1122 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Remote/Local In Control House | Reactive Power Relay |  | Hard Wired Contacts | 1123 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN211 | Hard Wired Contacts | 1124 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN211 | Hard Wired Contacts | 1125 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN209 | Hard Wired Contacts | 1126 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_IN210 | Hard Wired Contacts | 1127 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Communications Status | Discrete I/O | SEL_2440_DPAC_1_SEL_POU.Offline | Communication Status | 1128 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 2 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN101 | Hard Wired Contacts | 1129 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 3 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN102 | Hard Wired Contacts | 1130 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 7 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN103 | Hard Wired Contacts | 1131 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 8 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN104 | Hard Wired Contacts | 1132 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 9 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN105 | Hard Wired Contacts | 1133 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 10 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN106 | Hard Wired Contacts | 1134 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 11 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN107 | Hard Wired Contacts | 1135 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack C1 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN108 | Hard Wired Contacts | 1136 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F1 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN109 | Hard Wired Contacts | 1137 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F2 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN110 | Hard Wired Contacts | 1138 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F3 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN111 | Hard Wired Contacts | 1139 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F4 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN112 | Hard Wired Contacts | 1140 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F5 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN113 | Hard Wired Contacts | 1141 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F6 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN114 | Hard Wired Contacts | 1142 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F7 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN115 | Hard Wired Contacts | 1143 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F8 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN116 | Hard Wired Contacts | 1144 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F9 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN201 | Hard Wired Contacts | 1145 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F10 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN202 | Hard Wired Contacts | 1146 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F11 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN203 | Hard Wired Contacts | 1147 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52C1 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN204 | Hard Wired Contacts | 1148 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F12 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN205 | Hard Wired Contacts | 1149 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F13 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN206 | Hard Wired Contacts | 1150 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F14 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN207 | Hard Wired Contacts | 1151 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F15 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN208 | Hard Wired Contacts | 1152 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F16 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN209 | Hard Wired Contacts | 1153 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52C2 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN210 | Hard Wired Contacts | 1154 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1A Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN211 | Hard Wired Contacts | 1155 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1A Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN212 | Hard Wired Contacts | 1156 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1B Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN213 | Hard Wired Contacts | 1157 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1B Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN214 | Hard Wired Contacts | 1158 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-2A Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN215 | Hard Wired Contacts | 1159 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-2A Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN216 | Hard Wired Contacts | 1160 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-2B Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN301 | Hard Wired Contacts | 1161 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-2B Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN302 | Hard Wired Contacts | 1162 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L11 89b Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN303 | Hard Wired Contacts | 1163 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L12 89b Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN304 | Hard Wired Contacts | 1164 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89T1 89b Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN305 | Hard Wired Contacts | 1165 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L21 89b Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN306 | Hard Wired Contacts | 1166 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89T2 89b Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN307 | Hard Wired Contacts | 1167 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Communications Status | Discrete I/O | SEL_2440_DPAC_2_SEL_POU.Offline | Communication Status | 1168 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Smoke/Heat Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN101 | Hard Wired Contacts | 1169 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Hydrogen 1 Percent Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN102 | Hard Wired Contacts | 1170 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Hydrogen 2 Percent Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN103 | Hard Wired Contacts | 1171 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Door Alarms | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN104 | Hard Wired Contacts | 1172 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC Lockout Alarms | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN105 | Hard Wired Contacts | 1173 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC Low Temp | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN106 | Hard Wired Contacts | 1174 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC High Temp | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN107 | Hard Wired Contacts | 1175 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Normal Source Available 1 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN108 | Hard Wired Contacts | 1176 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Normal / Emergency 1 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN109 | Hard Wired Contacts | 1177 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Normal Source Available 2 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN110 | Hard Wired Contacts | 1178 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Normal / Emergency 2 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN111 | Hard Wired Contacts | 1179 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_Communications Status | Discrete I/O | SEL_2523_ANN_1_SEL_POU.Offline | Communication Status | 1180 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A1 | Hard Wired Contacts | 1181 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Low SF6 Gas Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A2 | Hard Wired Contacts | 1182 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A3 | Hard Wired Contacts | 1183 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A4 | Hard Wired Contacts | 1184 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Low SF6 Gas Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A5 | Hard Wired Contacts | 1185 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A6 | Hard Wired Contacts | 1186 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_XFMR T1 Trouble | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B1 | Hard Wired Contacts | 1187 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B2 | Hard Wired Contacts | 1188 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F1 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B3 | Hard Wired Contacts | 1189 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F2 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B4 | Hard Wired Contacts | 1190 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F2 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B5 | Hard Wired Contacts | 1191 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F3 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B6 | Hard Wired Contacts | 1192 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F3 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C1 | Hard Wired Contacts | 1193 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F4 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C2 | Hard Wired Contacts | 1194 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F4 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C3 | Hard Wired Contacts | 1195 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F5 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C4 | Hard Wired Contacts | 1196 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F5 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C5 | Hard Wired Contacts | 1197 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F6 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C6 | Hard Wired Contacts | 1198 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F6 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D1 | Hard Wired Contacts | 1199 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F7 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D2 | Hard Wired Contacts | 1200 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F7 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D3 | Hard Wired Contacts | 1201 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F8 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D4 | Hard Wired Contacts | 1202 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F8 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D5 | Hard Wired Contacts | 1203 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F9 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D6 | Hard Wired Contacts | 1204 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F9 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E1 | Hard Wired Contacts | 1205 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F10 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E2 | Hard Wired Contacts | 1206 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F10 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E3 | Hard Wired Contacts | 1207 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F11 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E4 | Hard Wired Contacts | 1208 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F11 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E5 | Hard Wired Contacts | 1209 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52C1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E6 | Hard Wired Contacts | 1210 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52C1 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_F1 | Hard Wired Contacts | 1211 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_Communications Status | Discrete I/O | SEL_2523_ANN_2_SEL_POU.Offline | Communication Status | 1212 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A1 | Hard Wired Contacts | 1213 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Low SF6 Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A2 | Hard Wired Contacts | 1214 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A3 | Hard Wired Contacts | 1215 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_XFMR T2 Trouble | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A4 | Hard Wired Contacts | 1216 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F12 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A5 | Hard Wired Contacts | 1217 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F12 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A6 | Hard Wired Contacts | 1218 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F13 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B1 | Hard Wired Contacts | 1219 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F13 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B2 | Hard Wired Contacts | 1220 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F14 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B3 | Hard Wired Contacts | 1221 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F14 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B4 | Hard Wired Contacts | 1222 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F15 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B5 | Hard Wired Contacts | 1223 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F15 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B6 | Hard Wired Contacts | 1224 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F16 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C1 | Hard Wired Contacts | 1225 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F16 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C2 | Hard Wired Contacts | 1226 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52C2 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C3 | Hard Wired Contacts | 1227 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52C2 Spring Charge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C4 | Hard Wired Contacts | 1228 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Communications Status | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1229 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Relay Enabled | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1230 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Software Alarm | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1231 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Hardware Alarm | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1232 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Communications Status | Meter | SEL_735_OCM1_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1233 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Relay Enabled | Meter | SEL_735_OCM1_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1234 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Software Alarm | Meter | SEL_735_OCM1_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1235 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Hardware Alarm | Meter | SEL_735_OCM1_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1236 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Communications Status | Meter | SEL_735_OCM3_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1237 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Relay Enabled | Meter | SEL_735_OCM3_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1238 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Software Alarm | Meter | SEL_735_OCM3_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1239 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Hardware Alarm | Meter | SEL_735_OCM3_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1240 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Communications Status | Meter | SEL_735_OCM4_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1241 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Relay Enabled | Meter | SEL_735_OCM4_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1242 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Software Alarm | Meter | SEL_735_OCM4_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1243 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Hardware Alarm | Meter | SEL_735_OCM4_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1244 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Communications Status | Meter | SEL_735_OCM5_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1245 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Relay Enabled | Meter | SEL_735_OCM5_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1246 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Software Alarm | Meter | SEL_735_OCM5_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1247 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Hardware Alarm | Meter | SEL_735_OCM5_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1248 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Communications Status | Meter | SEL_735_OCM6_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1249 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Relay Enabled | Meter | SEL_735_OCM6_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1250 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Software Alarm | Meter | SEL_735_OCM6_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1251 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Hardware Alarm | Meter | SEL_735_OCM6_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1252 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Communications Status | Meter | SEL_735_OCM7_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1253 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Relay Enabled | Meter | SEL_735_OCM7_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1254 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Software Alarm | Meter | SEL_735_OCM7_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1255 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Hardware Alarm | Meter | SEL_735_OCM7_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1256 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Communications Status | Meter | SEL_735_OCM8_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1257 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Relay Enabled | Meter | SEL_735_OCM8_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1258 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Software Alarm | Meter | SEL_735_OCM8_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1259 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Hardware Alarm | Meter | SEL_735_OCM8_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1260 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_ Communications Status | Meter | SEL_735_OCM9_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1261 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_ Relay Enabled | Meter | SEL_735_OCM9_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1262 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_ Software Alarm | Meter | SEL_735_OCM9_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1263 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_ Hardware Alarm | Meter | SEL_735_OCM9_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1264 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Communications Status | Meter | SEL_735_OCM10_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1265 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Relay Enabled | Meter | SEL_735_OCM10_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1266 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Software Alarm | Meter | SEL_735_OCM10_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1267 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Hardware Alarm | Meter | SEL_735_OCM10_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1268 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Communications Status | Meter | SEL_735_OCM11_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1269 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Relay Enabled | Meter | SEL_735_OCM11_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1270 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Software Alarm | Meter | SEL_735_OCM11_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1271 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Hardware Alarm | Meter | SEL_735_OCM11_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1272 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Communications Status | Meter | SEL_735_OCM12_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1273 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Relay Enabled | Meter | SEL_735_OCM12_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1274 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Software Alarm | Meter | SEL_735_OCM12_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1275 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Hardware Alarm | Meter | SEL_735_OCM12_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1276 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Communications Status | Meter | SEL_735_OCM13_LS_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1277 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Relay Enabled | Meter | SEL_735_OCM13_LS_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1278 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Software Alarm | Meter | SEL_735_OCM13_LS_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1279 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Hardware Alarm | Meter | SEL_735_OCM13_LS_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1280 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Communications Status | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1281 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Oil Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00001_Oil_Temperature_High_Alarm | Transformer Alarms | 1282 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Winding Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00002_Winding_Temperature_High_Alarm | Transformer Alarms | 1283 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_High Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00003_High_Pressure_Alarm | Transformer Alarms | 1284 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Low Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00004_Low_Pressure_Alarm | Transformer Alarms | 1285 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Low Vacuum Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00005_Low_Vacuum_Alarm | Transformer Alarms | 1286 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Oil Level Low Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00006_Oil_Level_Low_Alarm | Transformer Alarms | 1287 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Sudden Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00007_Sudden_Pressure_Alarm | Transformer Alarms | 1288 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Loss Of Cooling Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00008_Loss_Of_Cooling_Alarm | Transformer Alarms | 1289 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Pressure Relief Device | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00010_Pressure_Relief_Device | Pressure Relief Device | 1290 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_AC Supply Fail | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00011_AC_Supply_Fail | AC Supply Fail | 1291 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_DC Supply Fail | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00012_DC_Supply_Fail | DC Supply Fail | 1292 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Buchholz Relay Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00013_Buchholz_Relay_Alarm | Buchholz Relay Alarm | 1293 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_OLTC Protect Relay | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00014_OLTC_Protect_Relay | OLTC Protect Relay | 1294 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Fans Failure | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00015_Fans_Failure | Fans Failure | 1295 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Communications Status | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1296 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Oil Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Winding Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_High Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Low Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Low Vacuum Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Oil Level Low Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Sudden Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Loss Of Cooling Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Communications Status | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1297 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Oil Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00001_Oil_Temperature_High_Alarm | Transformer Alarms | 1298 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Winding Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00002_Winding_Temperature_High_Alarm | Transformer Alarms | 1299 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_High Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00003_High_Pressure_Alarm | Transformer Alarms | 1300 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Low Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00004_Low_Pressure_Alarm | Transformer Alarms | 1301 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Low Vacuum Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00005_Low_Vacuum_Alarm | Transformer Alarms | 1302 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Oil Level Low Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00006_Oil_Level_Low_Alarm | Transformer Alarms | 1303 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Sudden Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00007_Sudden_Pressure_Alarm | Transformer Alarms | 1304 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Loss Of Cooling Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00008_Loss_Of_Cooling_Alarm | Transformer Alarms | 1305 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Buchholz Relay Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00009_Buchholz_Relay_Alarm | Buchholz Relay Alarm | 1306 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_OLTC Protect Relay | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00010_OLTC_Protect_Relay | OLTC Protect Relay | 1307 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_LTC Tank Over Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00011_LTC_Tank_Over_Pressure_Alarm | LTC Tank Over Pressure Alarm | 1308 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_LTC Tank Low Level Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00012_LTC_Tank_Low_Level_Alarm | LTC Tank Low Level Alarm | 1309 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Cooling Control Loss of AC Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00013_Cooling_Control_Loss_of_VAC_Alarm | Cooling Control Loss of VAC Alarm | 1310 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Communications Status | Medium-High Voltage Transformer | M2001C_T2_90_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1311 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Oil Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms | 1312 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Winding Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_High Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Low Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Low Vacuum Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Oil Level Low Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Sudden Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Loss Of Cooling Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
Counters
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | ROLLOVER VALUE
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Total Energy Charged | PPC |  | Total Power Plant Energy Charged To Date | 0 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Total Energy Discharged | PPC |  | Total Power Plant Energy Discharged To Date | 1 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Aux Total Energy Used | PPC |  | Total Power Plant Auxiliary Energy Used to Date | 2 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS Total Energy Charged | PPC |  | Total Site ESS Energy Charged To Date | 3 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS Total Energy Discharged | PPC |  | Total Site ESS Energy Discharged To Date | 4 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 5 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 6 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 7 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 8 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 9 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 10 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 11 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 12 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 13 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 14 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 15 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 16 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 17 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 18 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 19 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 20 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 21 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 22 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 23 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 24 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 25 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 26 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 27 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 28 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 29 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 30 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 31 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 32 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 33 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 34 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 35 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 36 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 37 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 38 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 39 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 40 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 41 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 42 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 43 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 44 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Total Energy Charged | PPC |  | Total Power Plant Energy Charged To Date | 45 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Total Energy Discharged | PPC |  | Total Power Plant Energy Discharged To Date | 46 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Aux Total Energy Used | PPC |  | Total Power Plant Auxiliary Energy Used to Date | 47 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS Total Energy Charged | PPC |  | Total Site ESS Energy Charged To Date | 48 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS Total Energy Discharged | PPC |  | Total Site ESS Energy Discharged To Date | 49 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 50 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 51 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 52 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 53 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Total Energy Charged | PPC |  | Total Power Plant Energy Charged To Date | 54 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Total Energy Discharged | PPC |  | Total Power Plant Energy Discharged To Date | 55 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Aux Total Energy Used | PPC |  | Total Power Plant Auxiliary Energy Used to Date | 56 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS Total Energy Charged | PPC |  | Total Site ESS Energy Charged To Date | 57 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS Total Energy Discharged | PPC |  | Total Site ESS Energy Discharged To Date | 58 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 59 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 60 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 61 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 62 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Total Energy Charged | PPC |  | Total Power Plant Energy Charged To Date | 63 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Total Energy Discharged | PPC |  | Total Power Plant Energy Discharged To Date | 64 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Aux Total Energy Used | PPC |  | Total Power Plant Auxiliary Energy Used to Date | 65 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS Total Energy Charged | PPC |  | Total Site ESS Energy Charged To Date | 66 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS Total Energy Discharged | PPC |  | Total Site ESS Energy Discharged To Date | 67 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 68 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 69 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 70 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 71 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 72 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 73 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 74 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 75 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 76 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 77 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Total Energy Charged | PPC |  | Total Power Plant Energy Charged To Date | 78 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Total Energy Discharged | PPC |  | Total Power Plant Energy Discharged To Date | 79 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Aux Total Energy Used | PPC |  | Total Power Plant Auxiliary Energy Used to Date | 80 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS Total Energy Charged | PPC |  | Total Site ESS Energy Charged To Date | 81 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS Total Energy Discharged | PPC |  | Total Site ESS Energy Discharged To Date | 82 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 83 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 84 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 85 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 86 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 87 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 88 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 89 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 90 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 91 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 92 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 93 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 94 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 95 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 96 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 97 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 98 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 99 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 100 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 101 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 102 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 103 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 104 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 105 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 106 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 107 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 108 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 109 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 110 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 111 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 112 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 113 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 114 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 115 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 116 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Total Energy Charged | PPC |  | Total ESS Unit Energy Charged To Date | 117 | KWh | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Total Energy Discharged | PPC |  | Total ESS Unit Energy Discharged To Date | 118 | KWh | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Energy Received | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3PWP_MWH | Energy Received | 119 |  | Requested-Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Energy Delivered | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3PXP_MWH | Energy Delivered | 120 |  | Requested-Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Energy Received | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3QWP_MVARH | Reactive Energy Received | 121 |  | Requested-Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Energy Delivered | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3QWXP_MVARH | Reactive Energy Delivered | 122 |  | Requested-Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Energy Received | Transformer Relay |  | Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Energy Delivered | Transformer Relay |  | Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Energy Received | Transformer Relay |  | Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Energy Delivered | Transformer Relay |  | Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Energy Received | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3PWP_MWH | Energy Received | 123 |  | Requested-Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Energy Delivered | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3PXP_MWH | Energy Delivered | 124 |  | Requested-Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Energy Received | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3QWP_MVARH | Reactive Energy Received | 125 |  | Requested-Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Energy Delivered | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3QWXP_MVARH | Reactive Energy Delivered | 126 |  | Requested-Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Energy Received | Transformer Relay |  | Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Energy Delivered | Transformer Relay |  | Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Energy Received | Transformer Relay |  | Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Energy Delivered | Transformer Relay |  | Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  |  | Requested-Not Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_P3_POS | Energy Received | 127 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_P3_NEG | Energy Delivered | 128 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Reactive Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 129 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_Reactive Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 130 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PA_POS | Phase Energy Received | 131 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PA_NEG | Phase Energy Received | 132 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PB_POS | Phase Energy Received | 133 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 134 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 135 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 136 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Reactive Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 137 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Reactive Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 138 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Reactive Energy Received | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 139 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 140 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 141 |  | Requested-Available | 0
SUB1 | SEL-351-50BFL1 | DAGGETT3_SUB1_SEL-351-50BFL1_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351_50BFL1_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 142 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_P3_POS | Energy Received | 143 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_P3_NEG | Energy Delivered | 144 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 145 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 146 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PA_POS | Phase Energy Received | 147 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PA_NEG | Phase Energy Received | 148 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PB_POS | Phase Energy Received | 149 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 150 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 151 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 152 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 153 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 154 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 155 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 156 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 157 |  | Requested-Available | 0
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 158 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_P3_POS | Energy Received | 159 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_P3_NEG | Energy Delivered | 160 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 161 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 162 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PA_POS | Phase Energy Received | 163 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PA_NEG | Phase Energy Received | 164 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PB_POS | Phase Energy Received | 165 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 166 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 167 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 168 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 169 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 170 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 171 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 172 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 173 |  | Requested-Available | 0
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 174 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_P3_POS | Energy Received | 175 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_P3_NEG | Energy Delivered | 176 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 177 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 178 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_A Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PA_POS | Phase Energy Received | 179 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_B Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PA_NEG | Phase Energy Received | 180 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_C Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PB_POS | Phase Energy Received | 181 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 182 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 183 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 184 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 185 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 186 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 187 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 188 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 189 |  | Requested-Available | 0
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 190 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_P3_POS | Energy Received | 191 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_P3_NEG | Energy Delivered | 192 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 193 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 194 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PA_POS | Phase Energy Received | 195 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PA_NEG | Phase Energy Received | 196 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PB_POS | Phase Energy Received | 197 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 198 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 199 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 200 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 201 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 202 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 203 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 204 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 205 |  | Requested-Available | 0
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 206 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_P3_POS | Energy Received | 207 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_P3_NEG | Energy Delivered | 208 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 209 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 210 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_A Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PA_POS | Phase Energy Received | 211 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_B Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PA_NEG | Phase Energy Received | 212 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_C Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PB_POS | Phase Energy Received | 213 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 214 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 215 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 216 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 217 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 218 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 219 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 220 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 221 |  | Requested-Available | 0
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 222 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_P3_POS | Energy Received | 223 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_P3_NEG | Energy Delivered | 224 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 225 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 226 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_A Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PA_POS | Phase Energy Received | 227 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_B Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PA_NEG | Phase Energy Received | 228 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_C Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PB_POS | Phase Energy Received | 229 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 230 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 231 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 232 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 233 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 234 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 235 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 236 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 237 |  | Requested-Available | 0
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 238 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_P3_POS | Energy Received | 239 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_P3_NEG | Energy Delivered | 240 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 241 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 242 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PA_POS | Phase Energy Received | 243 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PA_NEG | Phase Energy Received | 244 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PB_POS | Phase Energy Received | 245 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 246 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 247 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 248 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 249 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 250 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 251 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 252 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 253 |  | Requested-Available | 0
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 254 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_P3_POS | Energy Received | 255 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_P3_NEG | Energy Delivered | 256 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 257 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 258 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PA_POS | Phase Energy Received | 259 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PA_NEG | Phase Energy Received | 260 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PB_POS | Phase Energy Received | 261 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 262 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 263 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 264 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 265 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 266 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 267 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 268 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 269 |  | Requested-Available | 0
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 270 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_P3_POS | Energy Received | 271 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_P3_NEG | Energy Delivered | 272 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 273 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 274 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PA_POS | Phase Energy Received | 275 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PA_NEG | Phase Energy Received | 276 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PB_POS | Phase Energy Received | 277 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 278 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 279 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 280 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 281 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 282 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 283 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 284 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 285 |  | Requested-Available | 0
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 286 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_P3_POS | Energy Received | 287 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_P3_NEG | Energy Delivered | 288 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 289 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 290 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PA_POS | Phase Energy Received | 291 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PA_NEG | Phase Energy Received | 292 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PB_POS | Phase Energy Received | 293 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 294 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 295 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 296 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 297 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 298 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 299 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 300 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 301 |  | Requested-Available | 0
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 302 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_P3_POS | Energy Received | 303 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_P3_NEG | Energy Delivered | 304 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 305 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 306 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PA_POS | Phase Energy Received | 307 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PA_NEG | Phase Energy Received | 308 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PB_POS | Phase Energy Received | 309 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 310 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 311 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 312 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 313 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 314 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 315 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 316 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 317 |  | Requested-Available | 0
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 318 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_P3_POS | Energy Received | 319 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_P3_NEG | Energy Delivered | 320 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 321 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 322 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PA_POS | Phase Energy Received | 323 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PA_NEG | Phase Energy Received | 324 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PB_POS | Phase Energy Received | 325 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 326 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 327 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 328 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 329 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 330 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 331 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 332 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 333 |  | Requested-Available | 0
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 334 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_P3_POS | Energy Received | 335 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_P3_NEG | Energy Delivered | 336 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 337 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 338 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PA_POS | Phase Energy Received | 339 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PA_NEG | Phase Energy Received | 340 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PB_POS | Phase Energy Received | 341 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 342 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 343 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 344 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 345 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 346 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 347 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 348 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 349 |  | Requested-Available | 0
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 350 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_P3_POS | Energy Received | 351 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_P3_NEG | Energy Delivered | 352 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 353 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 354 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PA_POS | Phase Energy Received | 355 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PA_NEG | Phase Energy Received | 356 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PB_POS | Phase Energy Received | 357 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 358 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 359 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 360 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 361 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 362 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 363 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 364 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 365 |  | Requested-Available | 0
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 366 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_P3_POS | Energy Received | 367 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_P3_NEG | Energy Delivered | 368 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 369 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 370 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PA_POS | Phase Energy Received | 371 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PA_NEG | Phase Energy Received | 372 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PB_POS | Phase Energy Received | 373 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 374 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 375 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 376 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 377 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 378 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 379 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 380 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 381 |  | Requested-Available | 0
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 382 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_P3_POS | Energy Received | 383 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_P3_NEG | Energy Delivered | 384 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_Q3_POS | Reactive Energy Received | 385 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_Q3_NEG | Reactive Energy Delivered | 386 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PA_POS | Phase Energy Received | 387 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PA_NEG | Phase Energy Received | 388 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PB_POS | Phase Energy Received | 389 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PB_NEG | Phase Energy Delivered | 390 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PC_POS | Phase Energy Delivered | 391 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_PC_NEG | Phase Energy Delivered | 392 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QA_POS | Phase Reactive Energy Received | 393 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QB_POS | Phase Reactive Energy Received | 394 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QC_POS | Phase Reactive Energy Received | 395 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QA_NEG | Phase Reactive Energy Delivered | 396 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QB_NEG | Phase Reactive Energy Delivered | 397 |  | Requested-Available | 0
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FM_DEM_QC_NEG | Phase Reactive Energy Delivered | 398 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 399 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 400 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 401 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 402 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 403 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 404 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 405 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 406 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 407 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 408 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 409 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 410 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00012_Energy_Received | Energy Received | 411 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 412 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 413 |  | Requested-Available | 0
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 414 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 415 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 416 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 417 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 418 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 419 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 420 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 421 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 422 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 423 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 424 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 425 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 426 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 427 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 428 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Energy Received | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 429 |  | Requested-Available | 0
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Energy Delivered | Meter | SEL_735_OCM1_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 430 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 431 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 432 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 433 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 434 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 435 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 436 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 437 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 438 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 439 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 440 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 441 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 442 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 443 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 444 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Energy Received | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 445 |  | Requested-Available | 0
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Energy Delivered | Meter | SEL_735_OCM3_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 446 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 447 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 448 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 449 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 450 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 451 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 452 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 453 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 454 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 455 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 456 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 457 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 458 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 459 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 460 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Energy Received | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 461 |  | Requested-Available | 0
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Energy Delivered | Meter | SEL_735_OCM4_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 462 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 463 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 464 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 465 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 466 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 467 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 468 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 469 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 470 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 471 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 472 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 473 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 474 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 475 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 476 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Energy Received | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 477 |  | Requested-Available | 0
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Energy Delivered | Meter | SEL_735_OCM5_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 478 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 479 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 480 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 481 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 482 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 483 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 484 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 485 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 486 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 487 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 488 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 489 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 490 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 491 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 492 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Energy Received | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 493 |  | Requested-Available | 0
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Energy Delivered | Meter | SEL_735_OCM6_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 494 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 495 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 496 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 497 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 498 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 499 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 500 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 501 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 502 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 503 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 504 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 505 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 506 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 507 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 508 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Energy Received | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 509 |  | Requested-Available | 0
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Energy Delivered | Meter | SEL_735_OCM7_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 510 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 511 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 512 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 513 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 514 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 515 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 516 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 517 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 518 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 519 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 520 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 521 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 522 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 523 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 524 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Energy Received | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 525 |  | Requested-Available | 0
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Energy Delivered | Meter | SEL_735_OCM8_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 526 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 527 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 528 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 529 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 530 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 531 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 532 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 533 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 534 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 535 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 536 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 537 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 538 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 539 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 540 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Energy Received | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 541 |  | Requested-Available | 0
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Energy Delivered | Meter | SEL_735_OCM9_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 542 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 543 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 544 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 545 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 546 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 547 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 548 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 549 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 550 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 551 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 552 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 553 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 554 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 555 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 556 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Energy Received | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 557 |  | Requested-Available | 0
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Energy Delivered | Meter | SEL_735_OCM10_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 558 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 559 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 560 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 561 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 562 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 563 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 564 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 565 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 566 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 567 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 568 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 569 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 570 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 571 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 572 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Energy Received | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 573 |  | Requested-Available | 0
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Energy Delivered | Meter | SEL_735_OCM11_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 574 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 575 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 576 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 577 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 578 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 579 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 580 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 581 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 582 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 583 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 584 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 585 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 586 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 587 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 588 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Energy Received | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 589 |  | Requested-Available | 0
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Energy Delivered | Meter | SEL_735_OCM12_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 590 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00000_A_Phase_Energy_Received | Phase Energy Received | 591 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00001_B_Phase_Energy_Received | Phase Energy Received | 592 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00002_C_Phase_Energy_Received | Phase Energy Received | 593 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00003_A_Phase_Energy_Delivered | Phase Energy Delivered | 594 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00004_B_Phase_Energy_Delivered | Phase Energy Delivered | 595 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00005_C_Phase_Energy_Delivered | Phase Energy Delivered | 596 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00006_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 597 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00007_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 598 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00008_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 599 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00009_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 600 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00010_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 601 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00011_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 602 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00012_Energy_Received | Energy Received | 603 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00013_Energy_Delivered | Energy Delivered | 604 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Energy Received | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00014_Reactive_Energy_Received | Reactive Energy Received | 605 |  | Requested-Available | 0
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Energy Delivered | Meter | SEL_735_OCM13_LS_DNP.COUNTER_00015_Reactive_Energy_Delivered | Reactive Energy Delivered | 606 |  | Requested-Available | 0
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 1 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 0 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 1 | MVAR | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 2 | PF | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 3 | KV | Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 4 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 5 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Real Power Command | PPC |  | BESS Site Real Power Command | 6 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Reactive Power Command | PPC |  | BESS Site Reactive Power Command | 7 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site RTU Heartbeat | PPC |  | BESS Site Rtu Heartbeat | 8 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Operation Code | PPC |  | BESS Site Operation Code | 9 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 2 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 10 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 11 | MVAR | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 12 | PF | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 13 | KV | Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 14 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 15 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Real Power Command | PPC |  | BESS Site Real Power Command | 16 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Reactive Power Command | PPC |  | BESS Site Reactive Power Command | 17 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site RTU Heartbeat | PPC |  | BESS Site Rtu Heartbeat | 18 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Operation Code | PPC |  | BESS Site Operation Code | 19 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 3 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 20 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 21 | MVAR | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 22 | PF | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 23 | KV | Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 24 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 25 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Real Power Command | PPC |  | BESS Site Real Power Command | 26 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Reactive Power Command | PPC |  | BESS Site Reactive Power Command | 27 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site RTU Heartbeat | PPC |  | BESS Site Rtu Heartbeat | 28 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Operation Code | PPC |  | BESS Site Operation Code | 29 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 4 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 30 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 31 | MVAR | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 32 | PF | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 33 | KV | Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 34 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 35 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Real Power Command | PPC |  | BESS Site Real Power Command | 36 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Reactive Power Command | PPC |  | BESS Site Reactive Power Command | 37 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site RTU Heartbeat | PPC |  | BESS Site Rtu Heartbeat | 38 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Operation Code | PPC |  | BESS Site Operation Code | 39 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_GMS Unit 5 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 40 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 41 | MVAR | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 42 | PF | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 43 | KV | Requested-Available | 210 | 250 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 44 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 45 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Real Power Command | PPC |  | BESS Site Real Power Command | 46 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Reactive Power Command | PPC |  | BESS Site Reactive Power Command | 47 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site RTU Heartbeat | PPC |  | BESS Site Rtu Heartbeat | 48 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Operation Code | PPC |  | BESS Site Operation Code | 49 | N/A | Not Requested-Available | 0 | 16 | 1
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 52F9 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 0 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 52F10 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 1 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 52F11 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 2 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 52F1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 3 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 52F2 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 4 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F1LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 5 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F1LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 6 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F2LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 7 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F2LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 8 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F9LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 9 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F9LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 10 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F10LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 11 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F10LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 12 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F11LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 13 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS 89F11LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 14 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 079 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 15 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 080 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 16 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 076 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 17 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 073 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 18 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 070 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 19 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 081 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 20 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 078 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 21 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 075 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 22 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 072 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 23 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 071 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 24 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 068 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 25 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 069 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 26 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 093 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 27 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 094 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 28 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 095 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 29 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 092 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 30 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 091 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 31 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 087 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 32 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 088 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 33 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 090 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 34 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 089 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 35 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 086 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 36 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 082 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 37 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 083 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 38 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 084 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 39 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 085 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 40 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 077 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 41 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 074 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 42 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 067 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 43 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 054 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 44 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 053 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 45 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 052 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 46 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 059 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 47 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 058 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 48 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 006 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 49 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 012 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 50 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 005 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 51 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 004 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 52 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Inverter 003 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 53 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Turbine 001 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Unit 1 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 54 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 55 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 56 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 57 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 58 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 59 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Auto Control | PPC |  | Site Auto-operation Control | 60 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Lock Control | PPC |  | Site ESS Lock Control | 61 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Auto Start Control | PPC |  | Site ESS Auto-start Control | 62 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Remote Control | PPC |  | Site ESS Remote Control Control | 63 | Off = Local, On = Remote | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Discharging Enable | PPC |  | Site Ess Discharging Enabled | 64 | Off = Disable, On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS Site Fault Reset | PPC |  | Site ESS Fault Reset | 65 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Lock Control | PPC |  | ESS Unit 1 Lock Control | 66 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Participate Control | PPC |  | ESS Unit 1 Site Participation Control | 67 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS01 Fault Reset | PPC |  | ESS Unit 1 Fault Reset | 68 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP01 Fault Reset | PPC |  | ESS BOP Fault Reset | 69 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Lock Control | PPC |  | ESS Unit 2 Lock Control | 70 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Participate Control | PPC |  | ESS Unit 2 Site Participation Control | 71 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS02 Fault Reset | PPC |  | ESS Unit 2 Fault Reset | 72 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP02 Fault Reset | PPC |  | ESS BOP Fault Reset | 73 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Lock Control | PPC |  | ESS Unit 3 Lock Control | 74 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Participate Control | PPC |  | ESS Unit 3 Site Participation Control | 75 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS03 Fault Reset | PPC |  | ESS Unit 3 Fault Reset | 76 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP03 Fault Reset | PPC |  | ESS BOP Fault Reset | 77 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Lock Control | PPC |  | ESS Unit 4 Lock Control | 78 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Participate Control | PPC |  | ESS Unit 4 Site Participation Control | 79 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS04 Fault Reset | PPC |  | ESS Unit 4 Fault Reset | 80 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP04 Fault Reset | PPC |  | ESS BOP Fault Reset | 81 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Lock Control | PPC |  | ESS Unit 5 Lock Control | 82 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Participate Control | PPC |  | ESS Unit 5 Site Participation Control | 83 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS05 Fault Reset | PPC |  | ESS Unit 5 Fault Reset | 84 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP05 Fault Reset | PPC |  | ESS BOP Fault Reset | 85 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Lock Control | PPC |  | ESS Unit 6 Lock Control | 86 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Participate Control | PPC |  | ESS Unit 6 Site Participation Control | 87 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS06 Fault Reset | PPC |  | ESS Unit 6 Fault Reset | 88 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP06 Fault Reset | PPC |  | ESS BOP Fault Reset | 89 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Lock Control | PPC |  | ESS Unit 7 Lock Control | 90 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Participate Control | PPC |  | ESS Unit 7 Site Participation Control | 91 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS07 Fault Reset | PPC |  | ESS Unit 7 Fault Reset | 92 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP07 Fault Reset | PPC |  | ESS BOP Fault Reset | 93 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Lock Control | PPC |  | ESS Unit 8 Lock Control | 94 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Participate Control | PPC |  | ESS Unit 8 Site Participation Control | 95 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS08 Fault Reset | PPC |  | ESS Unit 8 Fault Reset | 96 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP08 Fault Reset | PPC |  | ESS BOP Fault Reset | 97 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Lock Control | PPC |  | ESS Unit 9 Lock Control | 98 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Participate Control | PPC |  | ESS Unit 9 Site Participation Control | 99 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS09 Fault Reset | PPC |  | ESS Unit 9 Fault Reset | 100 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP09 Fault Reset | PPC |  | ESS BOP Fault Reset | 101 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Lock Control | PPC |  | ESS Unit 10 Lock Control | 102 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Participate Control | PPC |  | ESS Unit 10 Site Participation Control | 103 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS10 Fault Reset | PPC |  | ESS Unit 10 Fault Reset | 104 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP10 Fault Reset | PPC |  | ESS BOP Fault Reset | 105 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Lock Control | PPC |  | ESS Unit 11 Lock Control | 106 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Participate Control | PPC |  | ESS Unit 11 Site Participation Control | 107 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS11 Fault Reset | PPC |  | ESS Unit 11 Fault Reset | 108 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP11 Fault Reset | PPC |  | ESS BOP Fault Reset | 109 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Lock Control | PPC |  | ESS Unit 12 Lock Control | 110 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Participate Control | PPC |  | ESS Unit 12 Site Participation Control | 111 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS12 Fault Reset | PPC |  | ESS Unit 12 Fault Reset | 112 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP12 Fault Reset | PPC |  | ESS BOP Fault Reset | 113 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Lock Control | PPC |  | ESS Unit 13 Lock Control | 114 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Participate Control | PPC |  | ESS Unit 13 Site Participation Control | 115 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS13 Fault Reset | PPC |  | ESS Unit 13 Fault Reset | 116 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP13 Fault Reset | PPC |  | ESS BOP Fault Reset | 117 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Lock Control | PPC |  | ESS Unit 14 Lock Control | 118 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Participate Control | PPC |  | ESS Unit 14 Site Participation Control | 119 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS14 Fault Reset | PPC |  | ESS Unit 14 Fault Reset | 120 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP14 Fault Reset | PPC |  | ESS BOP Fault Reset | 121 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Lock Control | PPC |  | ESS Unit 15 Lock Control | 122 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Participate Control | PPC |  | ESS Unit 15 Site Participation Control | 123 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS15 Fault Reset | PPC |  | ESS Unit 15 Fault Reset | 124 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP15 Fault Reset | PPC |  | ESS BOP Fault Reset | 125 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Lock Control | PPC |  | ESS Unit 16 Lock Control | 126 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Participate Control | PPC |  | ESS Unit 16 Site Participation Control | 127 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS16 Fault Reset | PPC |  | ESS Unit 16 Fault Reset | 128 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP16 Fault Reset | PPC |  | ESS BOP Fault Reset | 129 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Lock Control | PPC |  | ESS Unit 17 Lock Control | 130 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Participate Control | PPC |  | ESS Unit 17 Site Participation Control | 131 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS17 Fault Reset | PPC |  | ESS Unit 17 Fault Reset | 132 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP17 Fault Reset | PPC |  | ESS BOP Fault Reset | 133 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Lock Control | PPC |  | ESS Unit 18 Lock Control | 134 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Participate Control | PPC |  | ESS Unit 18 Site Participation Control | 135 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS18 Fault Reset | PPC |  | ESS Unit 18 Fault Reset | 136 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP18 Fault Reset | PPC |  | ESS BOP Fault Reset | 137 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Lock Control | PPC |  | ESS Unit 19 Lock Control | 138 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Participate Control | PPC |  | ESS Unit 19 Site Participation Control | 139 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS19 Fault Reset | PPC |  | ESS Unit 19 Fault Reset | 140 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP19 Fault Reset | PPC |  | ESS BOP Fault Reset | 141 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Lock Control | PPC |  | ESS Unit 20 Lock Control | 142 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Participate Control | PPC |  | ESS Unit 20 Site Participation Control | 143 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS ESS20 Fault Reset | PPC |  | ESS Unit 20 Fault Reset | 144 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 1 BESS BOP20 Fault Reset | PPC |  | ESS BOP Fault Reset | 145 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS 52F3 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 146 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS 52F4 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 147 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS 89F3LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 148 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS 89F3LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 149 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS 89F6LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 150 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 061 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 151 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 062 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 152 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 057 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 153 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 056 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 154 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 055 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 155 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 013 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 156 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 011 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 157 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Inverter 010 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 158 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Turbine 002 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Unit 2 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 159 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 160 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 161 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 162 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 163 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 164 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Auto Control | PPC |  | Site Auto-operation Control | 165 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Lock Control | PPC |  | Site ESS Lock Control | 166 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Auto Start Control | PPC |  | Site ESS Auto-start Control | 167 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Remote Control | PPC |  | Site ESS Remote Control Control | 168 | Off = Local, On = Remote | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Discharging Enable | PPC |  | Site Ess Discharging Enabled | 169 | Off = Disable, On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS Site Fault Reset | PPC |  | Site ESS Fault Reset | 170 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Lock Control | PPC |  | ESS Unit 1 Lock Control | 171 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Participate Control | PPC |  | ESS Unit 1 Site Participation Control | 172 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS01 Fault Reset | PPC |  | ESS Unit 1 Fault Reset | 173 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP01 Fault Reset | PPC |  | ESS BOP Fault Reset | 174 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Lock Control | PPC |  | ESS Unit 2 Lock Control | 175 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Participate Control | PPC |  | ESS Unit 2 Site Participation Control | 176 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS ESS02 Fault Reset | PPC |  | ESS Unit 2 Fault Reset | 177 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 2 BESS BOP02 Fault Reset | PPC |  | ESS BOP Fault Reset | 178 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS 52F4 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 179 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS 52F7 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 180 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS 89F4LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 181 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS 89F4LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 182 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS 89F7LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 183 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 066 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 184 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 065 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 185 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 064 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 186 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 063 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 187 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 060 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 188 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 047 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 189 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 046 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 190 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Inverter 044 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 191 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Turbine 003 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Unit 3 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 192 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 193 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 194 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 195 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 196 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 197 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Auto Control | PPC |  | Site Auto-operation Control | 198 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Lock Control | PPC |  | Site ESS Lock Control | 199 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Auto Start Control | PPC |  | Site ESS Auto-start Control | 200 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Remote Control | PPC |  | Site ESS Remote Control Control | 201 | Off = Local, On = Remote | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Discharging Enable | PPC |  | Site Ess Discharging Enabled | 202 | Off = Disable, On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS Site Fault Reset | PPC |  | Site ESS Fault Reset | 203 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Lock Control | PPC |  | ESS Unit 1 Lock Control | 204 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Participate Control | PPC |  | ESS Unit 1 Site Participation Control | 205 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS01 Fault Reset | PPC |  | ESS Unit 1 Fault Reset | 206 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP01 Fault Reset | PPC |  | ESS BOP Fault Reset | 207 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Lock Control | PPC |  | ESS Unit 3 Lock Control | 208 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Participate Control | PPC |  | ESS Unit 3 Site Participation Control | 209 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS ESS02 Fault Reset | PPC |  | ESS Unit 3 Fault Reset | 210 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 3 BESS BOP02 Fault Reset | PPC |  | ESS BOP Fault Reset | 211 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS 52F5 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 212 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS 52F8 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 213 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS 89F5LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 214 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS 89F5LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 215 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS 89F8LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 216 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Inverter 051 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 217 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Inverter 050 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 218 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Inverter 019 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 219 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Inverter 020 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 220 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Inverter 021 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 221 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Turbine 004 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Unit 4 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 222 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 223 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 224 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 225 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 226 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 227 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Auto Control | PPC |  | Site Auto-operation Control | 228 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Lock Control | PPC |  | Site ESS Lock Control | 229 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Auto Start Control | PPC |  | Site ESS Auto-start Control | 230 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Remote Control | PPC |  | Site ESS Remote Control Control | 231 | Off = Local, On = Remote | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Discharging Enable | PPC |  | Site Ess Discharging Enabled | 232 | Off = Disable, On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS Site Fault Reset | PPC |  | Site ESS Fault Reset | 233 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Lock Control | PPC |  | ESS Unit 4 Lock Control | 234 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Participate Control | PPC |  | ESS Unit 4 Site Participation Control | 235 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS01 Fault Reset | PPC |  | ESS Unit 4 Fault Reset | 236 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP01 Fault Reset | PPC |  | ESS BOP Fault Reset | 237 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Lock Control | PPC |  | ESS Unit 2 Lock Control | 238 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Participate Control | PPC |  | ESS Unit 2 Site Participation Control | 239 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS02 Fault Reset | PPC |  | ESS Unit 2 Fault Reset | 240 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP02 Fault Reset | PPC |  | ESS BOP Fault Reset | 241 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Lock Control | PPC |  | ESS Unit 3 Lock Control | 242 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Participate Control | PPC |  | ESS Unit 3 Site Participation Control | 243 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS03 Fault Reset | PPC |  | ESS Unit 3 Fault Reset | 244 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP03 Fault Reset | PPC |  | ESS BOP Fault Reset | 245 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Lock Control | PPC |  | ESS Unit 4 Lock Control | 246 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Participate Control | PPC |  | ESS Unit 4 Site Participation Control | 247 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS04 Fault Reset | PPC |  | ESS Unit 4 Fault Reset | 248 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP04 Fault Reset | PPC |  | ESS BOP Fault Reset | 249 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Lock Control | PPC |  | ESS Unit 5 Lock Control | 250 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Participate Control | PPC |  | ESS Unit 5 Site Participation Control | 251 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS ESS05 Fault Reset | PPC |  | ESS Unit 5 Fault Reset | 252 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 4 BESS BOP05 Fault Reset | PPC |  | ESS BOP Fault Reset | 253 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 52F12 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 254 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 52F13 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 255 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 52F14 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 256 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 52F15 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 257 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 52F16 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 258 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F12LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 259 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F12LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 260 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F13LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 261 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F13LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 262 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F15LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 263 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F15LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 264 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F16LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 265 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F16LB MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 266 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS 89F14LA MOD Control | PPC | PPC.gms.rly89 | Breaker Controls | 267 | Latch Off = Open, Latch On = Close | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 018 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 268 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 017 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 269 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 007 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 270 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 001 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 271 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 002 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 272 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 008 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 273 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 009 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 274 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 027 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 275 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 026 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 276 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 025 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 277 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 024 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 278 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 016 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 279 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 015 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 280 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 014 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 281 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 045 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 282 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 023 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 283 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 022 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 284 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 028 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 285 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 033 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 286 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 034 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 287 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 036 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 288 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 049 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 289 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 048 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 290 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 032 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 291 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 031 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 292 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 030 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 293 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 029 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 294 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 035 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 295 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 037 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 296 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 038 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 297 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 039 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 298 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 040 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 299 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 041 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 300 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 042 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 301 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Inverter 043 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 302 | Latch On = Reset | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Turbine 005 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Unit 5 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 303 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 304 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 305 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 306 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 307 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 308 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Auto Control | PPC |  | Site Auto-operation Control | 309 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Lock Control | PPC |  | Site ESS Lock Control | 310 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Auto Start Control | PPC |  | Site ESS Auto-start Control | 311 | Off = Manual, On = Auto | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Remote Control | PPC |  | Site ESS Remote Control Control | 312 | Off = Local, On = Remote | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Discharging Enable | PPC |  | Site Ess Discharging Enabled | 313 | Off = Disable, On = Enable | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS Site Fault Reset | PPC |  | Site ESS Fault Reset | 314 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Lock Control | PPC |  | ESS Unit 5 Lock Control | 315 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Participate Control | PPC |  | ESS Unit 5 Site Participation Control | 316 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS01 Fault Reset | PPC |  | ESS Unit 5 Fault Reset | 317 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP01 Fault Reset | PPC |  | ESS BOP Fault Reset | 318 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Lock Control | PPC |  | ESS Unit 2 Lock Control | 319 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Participate Control | PPC |  | ESS Unit 2 Site Participation Control | 320 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS02 Fault Reset | PPC |  | ESS Unit 2 Fault Reset | 321 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP02 Fault Reset | PPC |  | ESS BOP Fault Reset | 322 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Lock Control | PPC |  | ESS Unit 3 Lock Control | 323 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Participate Control | PPC |  | ESS Unit 3 Site Participation Control | 324 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS03 Fault Reset | PPC |  | ESS Unit 3 Fault Reset | 325 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP03 Fault Reset | PPC |  | ESS BOP Fault Reset | 326 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Lock Control | PPC |  | ESS Unit 4 Lock Control | 327 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Participate Control | PPC |  | ESS Unit 4 Site Participation Control | 328 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS04 Fault Reset | PPC |  | ESS Unit 4 Fault Reset | 329 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP04 Fault Reset | PPC |  | ESS BOP Fault Reset | 330 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Lock Control | PPC |  | ESS Unit 5 Lock Control | 331 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Participate Control | PPC |  | ESS Unit 5 Site Participation Control | 332 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS05 Fault Reset | PPC |  | ESS Unit 5 Fault Reset | 333 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP05 Fault Reset | PPC |  | ESS BOP Fault Reset | 334 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Lock Control | PPC |  | ESS Unit 6 Lock Control | 335 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Participate Control | PPC |  | ESS Unit 6 Site Participation Control | 336 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS06 Fault Reset | PPC |  | ESS Unit 6 Fault Reset | 337 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP06 Fault Reset | PPC |  | ESS BOP Fault Reset | 338 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Lock Control | PPC |  | ESS Unit 7 Lock Control | 339 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Participate Control | PPC |  | ESS Unit 7 Site Participation Control | 340 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS07 Fault Reset | PPC |  | ESS Unit 7 Fault Reset | 341 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP07 Fault Reset | PPC |  | ESS BOP Fault Reset | 342 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Lock Control | PPC |  | ESS Unit 8 Lock Control | 343 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Participate Control | PPC |  | ESS Unit 8 Site Participation Control | 344 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS08 Fault Reset | PPC |  | ESS Unit 8 Fault Reset | 345 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP08 Fault Reset | PPC |  | ESS BOP Fault Reset | 346 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Lock Control | PPC |  | ESS Unit 9 Lock Control | 347 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Participate Control | PPC |  | ESS Unit 9 Site Participation Control | 348 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS09 Fault Reset | PPC |  | ESS Unit 9 Fault Reset | 349 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP09 Fault Reset | PPC |  | ESS BOP Fault Reset | 350 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Lock Control | PPC |  | ESS Unit 50 Lock Control | 351 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Participate Control | PPC |  | ESS Unit 50 Site Participation Control | 352 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS10 Fault Reset | PPC |  | ESS Unit 50 Fault Reset | 353 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP10 Fault Reset | PPC |  | ESS BOP Fault Reset | 354 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Lock Control | PPC |  | ESS Unit 51 Lock Control | 355 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Participate Control | PPC |  | ESS Unit 51 Site Participation Control | 356 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS11 Fault Reset | PPC |  | ESS Unit 51 Fault Reset | 357 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP11 Fault Reset | PPC |  | ESS BOP Fault Reset | 358 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Lock Control | PPC |  | ESS Unit 52 Lock Control | 359 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Participate Control | PPC |  | ESS Unit 52 Site Participation Control | 360 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS12 Fault Reset | PPC |  | ESS Unit 52 Fault Reset | 361 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP12 Fault Reset | PPC |  | ESS BOP Fault Reset | 362 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Lock Control | PPC |  | ESS Unit 53 Lock Control | 363 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Participate Control | PPC |  | ESS Unit 53 Site Participation Control | 364 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS13 Fault Reset | PPC |  | ESS Unit 53 Fault Reset | 365 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP13 Fault Reset | PPC |  | ESS BOP Fault Reset | 366 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Lock Control | PPC |  | ESS Unit 54 Lock Control | 367 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Participate Control | PPC |  | ESS Unit 54 Site Participation Control | 368 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS14 Fault Reset | PPC |  | ESS Unit 54 Fault Reset | 369 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP14 Fault Reset | PPC |  | ESS BOP Fault Reset | 370 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Lock Control | PPC |  | ESS Unit 55 Lock Control | 371 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Participate Control | PPC |  | ESS Unit 55 Site Participation Control | 372 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS15 Fault Reset | PPC |  | ESS Unit 55 Fault Reset | 373 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP15 Fault Reset | PPC |  | ESS BOP Fault Reset | 374 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Lock Control | PPC |  | ESS Unit 56 Lock Control | 375 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Participate Control | PPC |  | ESS Unit 56 Site Participation Control | 376 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS16 Fault Reset | PPC |  | ESS Unit 56 Fault Reset | 377 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP16 Fault Reset | PPC |  | ESS BOP Fault Reset | 378 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Lock Control | PPC |  | ESS Unit 57 Lock Control | 379 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Participate Control | PPC |  | ESS Unit 57 Site Participation Control | 380 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS17 Fault Reset | PPC |  | ESS Unit 57 Fault Reset | 381 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP17 Fault Reset | PPC |  | ESS BOP Fault Reset | 382 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Lock Control | PPC |  | ESS Unit 58 Lock Control | 383 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Participate Control | PPC |  | ESS Unit 58 Site Participation Control | 384 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS ESS18 Fault Reset | PPC |  | ESS Unit 58 Fault Reset | 385 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Dagget 3_SUB1_PPC_Unit 5 BESS BOP18 Fault Reset | PPC |  | ESS BOP Fault Reset | 386 | Off = False, On = Reset | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L1 SCADA OPEN | Line Relay | SEL_411L_87L1S_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 387 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L2 SCADA OPEN | Line Relay | SEL_411L_87L1S_SEL.FO_RB_RB3_4.operPulse | SCADA OPEN/CLOSE | 388 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L1 SCADA OPEN | Line Relay | SEL_411L_87L2S_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 389 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-487E-87T1P_89T1 SCADA OPEN | Transformer Relay | SEL_487E_89T1_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 390 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-487E-87T2P_89T2 SCADA OPEN | Transformer Relay | SEL_487E_89T2_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 391 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F1 | DAGGETT3_SUB1_SEL-351S-51F1_SCADA TRIP | Breaker Relay | SEL_351S_51F1_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 392 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F2 | DAGGETT3_SUB1_SEL-351S-51F2_SCADA TRIP | Breaker Relay | SEL_351S_51F2_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 393 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F3 | DAGGETT3_SUB1_SEL-351S-51F3_SCADA TRIP | Breaker Relay | SEL_351S_51F3_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 394 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F4 | DAGGETT3_SUB1_SEL-351S-51F4_SCADA TRIP | Breaker Relay | SEL_351S_51F4_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 395 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F5 | DAGGETT3_SUB1_SEL-351S-51F5_SCADA TRIP | Breaker Relay | SEL_351S_51F5_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 396 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F6 | DAGGETT3_SUB1_SEL-351S-51F6_SCADA TRIP | Breaker Relay | SEL_351S_51F6_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 397 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F7 | DAGGETT3_SUB1_SEL-351S-51F7_SCADA TRIP | Breaker Relay | SEL_351S_51F7_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 398 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F8 | DAGGETT3_SUB1_SEL-351S-51F8_SCADA TRIP | Breaker Relay | SEL_351S_51F8_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 399 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F9 | DAGGETT3_SUB1_SEL-351S-51F9_SCADA TRIP | Breaker Relay | SEL_351S_51F9_SEL.FO_RB_RB1_2.operPulse | SCADA OPEN/CLOSE | 400 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F10 | DAGGETT3_SUB1_SEL-351S-51F10_SCADA TRIP | Breaker Relay | SEL_351S_51F10_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 401 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F11 | DAGGETT3_SUB1_SEL-351S-51F11_SCADA TRIP | Breaker Relay | SEL_351S_51F11_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 402 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F12 | DAGGETT3_SUB1_SEL-351S-51F12_SCADA TRIP | Breaker Relay | SEL_351S_51F12_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 403 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F13 | DAGGETT3_SUB1_SEL-351S-51F13_SCADA TRIP | Breaker Relay | SEL_351S_51F13_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 404 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F14 | DAGGETT3_SUB1_SEL-351S-51F14_SCADA TRIP | Breaker Relay | SEL_351S_51F14_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 405 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F15 | DAGGETT3_SUB1_SEL-351S-51F15_SCADA TRIP | Breaker Relay | SEL_351S_51F15_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 406 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-351S-51F16 | DAGGETT3_SUB1_SEL-351S-51F16_SCADA TRIP | Breaker Relay | SEL_351S_51F16_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 407 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_52C2 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC1P_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 408 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC11 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC1P_SEL.FO_RB_RB3_4.operPulse | SCADA TRIP/CLOSE | 409 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC1P | DAGGETT3_SUB1_SEL-487V-87VC1P_CSC12 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC1P_SEL.FO_RB_RB5_6.operPulse | SCADA TRIP/CLOSE | 410 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_52C2 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC2P_SEL.FO_RB_RB1_2.operPulse | SCADA TRIP/CLOSE | 411 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC21 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC2P_SEL.FO_RB_RB3_4.operPulse | SCADA TRIP/CLOSE | 412 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87VC2P | DAGGETT3_SUB1_SEL-487V-87VC2P_CSC22 SCADA TRIP | Reactive Power Relay | SEL_487V_87VC2P_SEL.FO_RB_RB5_6.operPulse | SCADA TRIP/CLOSE | 413 | LatchOff/LatchOn | Not Requested-Available

## 2
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | 10.75.32.2 |  | DNP Server | 10.75.32.2
DNP Server Port# | 20002 |  | DNP Server Port# | 20010 (PROD); 20011 (QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 2 |  | RTAC DNP Server address | 2
| Data Type | DNP Event Class | Event Obj/Var | Static Obj/Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30/5
Digitals | Status with Flags | 1 | 2/2 | 1/2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20/1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband of 0.01 for all points except 0.001 for Frequency and Power Factor
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | INV001 | Dagget 3_SUB1_INV001_A Phase Current | Inverter | Inverter001_MODBUS.HR1004_i1_A | A Phase Current | 0 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_B Phase Current | Inverter | Inverter001_MODBUS.HR1005_i2_A | B Phase Current | 1 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_C Phase Current | Inverter | Inverter001_MODBUS.HR1006_i3_A | C Phase Current | 2 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Bus Voltage | Inverter | Inverter001_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV001 | Dagget 3_SUB1_INV001_Apparent Power | Inverter | Inverter001_MODBUS.HR1010_s3_VA | Apparent Power | 4 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input1 | Inverter | Inverter001_MODBUS.HR5005_m1_idc_A | Current DC Input# | 5 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC Input 1 | Inverter | Inverter001_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 6 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input2 | Inverter | Inverter001_MODBUS.HR5037_m2_idc_A | Current DC Input# | 7 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC input 2 | Inverter | Inverter001_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 8 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input3 | Inverter | Inverter001_MODBUS.HR5069_m3_idc_A | Current DC Input# | 9 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC input 3 | Inverter | Inverter001_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 10 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input4 | Inverter | Inverter001_MODBUS.HR5101_m4_idc_A | Current DC Input# | 11 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC input 4 | Inverter | Inverter001_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 12 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input5 | Inverter | Inverter001_MODBUS.HR5133_m5_idc_A | Current DC Input# | 13 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC input 5 | Inverter | Inverter001_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 14 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current DC Input6 | Inverter | Inverter001_MODBUS.HR5165_m6_idc_A | Current DC Input# | 15 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC input 6 | Inverter | Inverter001_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 16 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current-AC | Inverter | Inverter001_MODBUS.HR1007_i3Avg_A | Current-AC | 17 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Current-DC | Inverter | Inverter001_MODBUS.HR1062_idcInput_A | Current-DC | 18 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Daily Energy Delivered | Inverter | Inverter001_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 19 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power Set Point | Inverter | Inverter001_MODBUS.HR0553_pRef | Real Power Set Point | 20 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Reactive Power Set Point | Inverter | Inverter001_MODBUS.HR0558_qRef | Reactive Power Set Point | 21 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Frequency | Inverter | Inverter001_MODBUS.HR1012_f3_Hz | Frequency | 22 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV001 | Dagget 3_SUB1_INV001_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Insulation Resistance | Inverter | Inverter001_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 23 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Number of DU Channels | Inverter | Inverter001_MODBUS.HR0653_duChannels | Number of DU Channels | 24 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Number of Running Modules | Inverter | Inverter001_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 25 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Operating State | Inverter | Inverter001_MODBUS.HR1123_currentStatus | Operating State | 26 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Power Factor | Inverter | Inverter001_MODBUS.HR1011_pf3 | Power Factor | 27 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV001 | Dagget 3_SUB1_INV001_Ramp Down | Inverter | Inverter001_MODBUS.HR0286_dropGradient_p | Ramp Down | 28 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Ramp Up | Inverter | Inverter001_MODBUS.HR0282_riseGradient_p | Ramp Up | 29 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power Delivered | Inverter | Inverter001_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 30 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Reactive Power Delivered | Inverter | Inverter001_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 31 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power | 32 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Reactive Power | Inverter | Inverter001_MODBUS.HR1009_q3_kvar | Reactive Power | 33 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Reactive Power Mode | Inverter | Inverter001_MODBUS.HR0552_qControlMode | Reactive Power Mode | 34 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Reactive Power Set Point Percent | Inverter | Inverter001_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 35 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power AC Percent | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power AC Percent | 36 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power-AC | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power-AC | 37 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power-DC | Inverter | Inverter001_MODBUS.HR1061_pdcInput_W | Real Power-DC | 38 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Air Intake | Inverter | Inverter001_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 39 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Cabinet | Inverter | Inverter001_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 40 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-IGBT | Inverter | Inverter001_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 41 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Temperature-Module | Inverter | Inverter001_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 42 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage A-B | Inverter | Inverter001_MODBUS.HR1001_vRS_V | Voltage A-B | 43 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage B-C | Inverter | Inverter001_MODBUS.HR1002_vST_V | Voltage B-C | 44 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage C-A | Inverter | Inverter001_MODBUS.HR1003_vTR_V | Voltage C-A | 45 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Voltage DC | Inverter | Inverter001_MODBUS.HR1051_vdcBus_V | Voltage DC | 46 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV002 | Dagget 3_SUB1_INV002_A Phase Current | Inverter | Inverter002_MODBUS.HR1004_i1_A | A Phase Current | 47 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_B Phase Current | Inverter | Inverter002_MODBUS.HR1005_i2_A | B Phase Current | 48 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_C Phase Current | Inverter | Inverter002_MODBUS.HR1006_i3_A | C Phase Current | 49 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Bus Voltage | Inverter | Inverter002_MODBUS.HR1051_vdcBus_V | Bus Voltage | 50 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV002 | Dagget 3_SUB1_INV002_Apparent Power | Inverter | Inverter002_MODBUS.HR1010_s3_VA | Apparent Power | 51 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input1 | Inverter | Inverter002_MODBUS.HR5005_m1_idc_A | Current DC Input# | 52 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC Input 1 | Inverter | Inverter002_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 53 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input2 | Inverter | Inverter002_MODBUS.HR5037_m2_idc_A | Current DC Input# | 54 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC input 2 | Inverter | Inverter002_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 55 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input3 | Inverter | Inverter002_MODBUS.HR5069_m3_idc_A | Current DC Input# | 56 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC input 3 | Inverter | Inverter002_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 57 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input4 | Inverter | Inverter002_MODBUS.HR5101_m4_idc_A | Current DC Input# | 58 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC input 4 | Inverter | Inverter002_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 59 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input5 | Inverter | Inverter002_MODBUS.HR5133_m5_idc_A | Current DC Input# | 60 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC input 5 | Inverter | Inverter002_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 61 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current DC Input6 | Inverter | Inverter002_MODBUS.HR5165_m6_idc_A | Current DC Input# | 62 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC input 6 | Inverter | Inverter002_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 63 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current-AC | Inverter | Inverter002_MODBUS.HR1007_i3Avg_A | Current-AC | 64 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Current-DC | Inverter | Inverter002_MODBUS.HR1062_idcInput_A | Current-DC | 65 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Daily Energy Delivered | Inverter | Inverter002_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 66 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power Set Point | Inverter | Inverter002_MODBUS.HR0553_pRef | Real Power Set Point | 67 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Reactive Power Set Point | Inverter | Inverter002_MODBUS.HR0558_qRef | Reactive Power Set Point | 68 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Frequency | Inverter | Inverter002_MODBUS.HR1012_f3_Hz | Frequency | 69 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV002 | Dagget 3_SUB1_INV002_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Insulation Resistance | Inverter | Inverter002_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 70 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Number of DU Channels | Inverter | Inverter002_MODBUS.HR0653_duChannels | Number of DU Channels | 71 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Number of Running Modules | Inverter | Inverter002_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 72 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Operating State | Inverter | Inverter002_MODBUS.HR1123_currentStatus | Operating State | 73 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Power Factor | Inverter | Inverter002_MODBUS.HR1011_pf3 | Power Factor | 74 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV002 | Dagget 3_SUB1_INV002_Ramp Down | Inverter | Inverter002_MODBUS.HR0286_dropGradient_p | Ramp Down | 75 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Ramp Up | Inverter | Inverter002_MODBUS.HR0282_riseGradient_p | Ramp Up | 76 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power Delivered | Inverter | Inverter002_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 77 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Reactive Power Delivered | Inverter | Inverter002_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 78 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power | 79 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Reactive Power | Inverter | Inverter002_MODBUS.HR1009_q3_kvar | Reactive Power | 80 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Reactive Power Mode | Inverter | Inverter002_MODBUS.HR0552_qControlMode | Reactive Power Mode | 81 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Reactive Power Set Point Percent | Inverter | Inverter002_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 82 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power AC Percent | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power AC Percent | 83 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power-AC | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power-AC | 84 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power-DC | Inverter | Inverter002_MODBUS.HR1061_pdcInput_W | Real Power-DC | 85 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Air Intake | Inverter | Inverter002_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 86 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Cabinet | Inverter | Inverter002_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 87 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-IGBT | Inverter | Inverter002_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 88 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Temperature-Module | Inverter | Inverter002_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 89 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage A-B | Inverter | Inverter002_MODBUS.HR1002_vRS_V | Voltage A-B | 90 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage B-C | Inverter | Inverter002_MODBUS.HR1002_vST_V | Voltage B-C | 91 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage C-A | Inverter | Inverter002_MODBUS.HR1003_vTR_V | Voltage C-A | 92 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Voltage DC | Inverter | Inverter002_MODBUS.HR1051_vdcBus_V | Voltage DC | 93 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV003 | Dagget 3_SUB1_INV003_A Phase Current | Inverter | Inverter003_MODBUS.HR1004_i1_A | A Phase Current | 94 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_B Phase Current | Inverter | Inverter003_MODBUS.HR1005_i2_A | B Phase Current | 95 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_C Phase Current | Inverter | Inverter003_MODBUS.HR1006_i3_A | C Phase Current | 96 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Bus Voltage | Inverter | Inverter003_MODBUS.HR1051_vdcBus_V | Bus Voltage | 97 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV003 | Dagget 3_SUB1_INV003_Apparent Power | Inverter | Inverter003_MODBUS.HR1010_s3_VA | Apparent Power | 98 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input1 | Inverter | Inverter003_MODBUS.HR5005_m1_idc_A | Current DC Input# | 99 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC Input 1 | Inverter | Inverter003_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 100 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input2 | Inverter | Inverter003_MODBUS.HR5037_m2_idc_A | Current DC Input# | 101 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC input 2 | Inverter | Inverter003_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 102 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input3 | Inverter | Inverter003_MODBUS.HR5069_m3_idc_A | Current DC Input# | 103 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC input 3 | Inverter | Inverter003_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 104 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input4 | Inverter | Inverter003_MODBUS.HR5101_m4_idc_A | Current DC Input# | 105 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC input 4 | Inverter | Inverter003_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 106 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input5 | Inverter | Inverter003_MODBUS.HR5133_m5_idc_A | Current DC Input# | 107 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC input 5 | Inverter | Inverter003_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 108 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current DC Input6 | Inverter | Inverter003_MODBUS.HR5165_m6_idc_A | Current DC Input# | 109 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC input 6 | Inverter | Inverter003_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 110 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current-AC | Inverter | Inverter003_MODBUS.HR1007_i3Avg_A | Current-AC | 111 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Current-DC | Inverter | Inverter003_MODBUS.HR1062_idcInput_A | Current-DC | 112 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Daily Energy Delivered | Inverter | Inverter003_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 113 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power Set Point | Inverter | Inverter003_MODBUS.HR0553_pRef | Real Power Set Point | 114 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Reactive Power Set Point | Inverter | Inverter003_MODBUS.HR0558_qRef | Reactive Power Set Point | 115 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Frequency | Inverter | Inverter003_MODBUS.HR1012_f3_Hz | Frequency | 116 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV003 | Dagget 3_SUB1_INV003_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Insulation Resistance | Inverter | Inverter003_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 117 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Number of DU Channels | Inverter | Inverter003_MODBUS.HR0653_duChannels | Number of DU Channels | 118 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Number of Running Modules | Inverter | Inverter003_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 119 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Operating State | Inverter | Inverter003_MODBUS.HR1123_currentStatus | Operating State | 120 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Power Factor | Inverter | Inverter003_MODBUS.HR1011_pf3 | Power Factor | 121 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV003 | Dagget 3_SUB1_INV003_Ramp Down | Inverter | Inverter003_MODBUS.HR0286_dropGradient_p | Ramp Down | 122 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Ramp Up | Inverter | Inverter003_MODBUS.HR0282_riseGradient_p | Ramp Up | 123 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power Delivered | Inverter | Inverter003_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 124 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Reactive Power Delivered | Inverter | Inverter003_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 125 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power | 126 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Reactive Power | Inverter | Inverter003_MODBUS.HR1009_q3_kvar | Reactive Power | 127 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Reactive Power Mode | Inverter | Inverter003_MODBUS.HR0552_qControlMode | Reactive Power Mode | 128 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Reactive Power Set Point Percent | Inverter | Inverter003_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 129 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power AC Percent | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power AC Percent | 130 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power-AC | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power-AC | 131 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power-DC | Inverter | Inverter003_MODBUS.HR1061_pdcInput_W | Real Power-DC | 132 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Air Intake | Inverter | Inverter003_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 133 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Cabinet | Inverter | Inverter003_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 134 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-IGBT | Inverter | Inverter003_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 135 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Temperature-Module | Inverter | Inverter003_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 136 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage A-B | Inverter | Inverter003_MODBUS.HR1003_vRS_V | Voltage A-B | 137 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage B-C | Inverter | Inverter003_MODBUS.HR1002_vST_V | Voltage B-C | 138 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage C-A | Inverter | Inverter003_MODBUS.HR1003_vTR_V | Voltage C-A | 139 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Voltage DC | Inverter | Inverter003_MODBUS.HR1051_vdcBus_V | Voltage DC | 140 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV004 | Dagget 3_SUB1_INV004_A Phase Current | Inverter | Inverter004_MODBUS.HR1004_i1_A | A Phase Current | 141 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_B Phase Current | Inverter | Inverter004_MODBUS.HR1005_i2_A | B Phase Current | 142 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_C Phase Current | Inverter | Inverter004_MODBUS.HR1006_i3_A | C Phase Current | 143 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Bus Voltage | Inverter | Inverter004_MODBUS.HR1051_vdcBus_V | Bus Voltage | 144 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV004 | Dagget 3_SUB1_INV004_Apparent Power | Inverter | Inverter004_MODBUS.HR1010_s3_VA | Apparent Power | 145 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input1 | Inverter | Inverter004_MODBUS.HR5005_m1_idc_A | Current DC Input# | 146 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC Input 1 | Inverter | Inverter004_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 147 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input2 | Inverter | Inverter004_MODBUS.HR5037_m2_idc_A | Current DC Input# | 148 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC input 2 | Inverter | Inverter004_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 149 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input3 | Inverter | Inverter004_MODBUS.HR5069_m3_idc_A | Current DC Input# | 150 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC input 3 | Inverter | Inverter004_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 151 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input4 | Inverter | Inverter004_MODBUS.HR5101_m4_idc_A | Current DC Input# | 152 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC input 4 | Inverter | Inverter004_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 153 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input5 | Inverter | Inverter004_MODBUS.HR5133_m5_idc_A | Current DC Input# | 154 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC input 5 | Inverter | Inverter004_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 155 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current DC Input6 | Inverter | Inverter004_MODBUS.HR5165_m6_idc_A | Current DC Input# | 156 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC input 6 | Inverter | Inverter004_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 157 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current-AC | Inverter | Inverter004_MODBUS.HR1007_i3Avg_A | Current-AC | 158 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Current-DC | Inverter | Inverter004_MODBUS.HR1062_idcInput_A | Current-DC | 159 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Daily Energy Delivered | Inverter | Inverter004_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 160 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power Set Point | Inverter | Inverter004_MODBUS.HR0553_pRef | Real Power Set Point | 161 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Reactive Power Set Point | Inverter | Inverter004_MODBUS.HR0558_qRef | Reactive Power Set Point | 162 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Frequency | Inverter | Inverter004_MODBUS.HR1012_f3_Hz | Frequency | 163 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV004 | Dagget 3_SUB1_INV004_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Insulation Resistance | Inverter | Inverter004_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 164 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Number of DU Channels | Inverter | Inverter004_MODBUS.HR0653_duChannels | Number of DU Channels | 165 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Number of Running Modules | Inverter | Inverter004_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 166 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Operating State | Inverter | Inverter004_MODBUS.HR1123_currentStatus | Operating State | 167 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Power Factor | Inverter | Inverter004_MODBUS.HR1011_pf3 | Power Factor | 168 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV004 | Dagget 3_SUB1_INV004_Ramp Down | Inverter | Inverter004_MODBUS.HR0286_dropGradient_p | Ramp Down | 169 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Ramp Up | Inverter | Inverter004_MODBUS.HR0282_riseGradient_p | Ramp Up | 170 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power Delivered | Inverter | Inverter004_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 171 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Reactive Power Delivered | Inverter | Inverter004_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 172 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power | 173 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Reactive Power | Inverter | Inverter004_MODBUS.HR1009_q3_kvar | Reactive Power | 174 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Reactive Power Mode | Inverter | Inverter004_MODBUS.HR0552_qControlMode | Reactive Power Mode | 175 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Reactive Power Set Point Percent | Inverter | Inverter004_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 176 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power AC Percent | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power AC Percent | 177 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power-AC | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power-AC | 178 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power-DC | Inverter | Inverter004_MODBUS.HR1061_pdcInput_W | Real Power-DC | 179 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Air Intake | Inverter | Inverter004_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 180 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Cabinet | Inverter | Inverter004_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 181 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-IGBT | Inverter | Inverter004_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 182 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Temperature-Module | Inverter | Inverter004_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 183 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage A-B | Inverter | Inverter004_MODBUS.HR1004_vRS_V | Voltage A-B | 184 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage B-C | Inverter | Inverter004_MODBUS.HR1002_vST_V | Voltage B-C | 185 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage C-A | Inverter | Inverter004_MODBUS.HR1003_vTR_V | Voltage C-A | 186 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Voltage DC | Inverter | Inverter004_MODBUS.HR1051_vdcBus_V | Voltage DC | 187 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV005 | Dagget 3_SUB1_INV005_A Phase Current | Inverter | Inverter005_MODBUS.HR1004_i1_A | A Phase Current | 188 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_B Phase Current | Inverter | Inverter005_MODBUS.HR1005_i2_A | B Phase Current | 189 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_C Phase Current | Inverter | Inverter005_MODBUS.HR1006_i3_A | C Phase Current | 190 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Bus Voltage | Inverter | Inverter005_MODBUS.HR1051_vdcBus_V | Bus Voltage | 191 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV005 | Dagget 3_SUB1_INV005_Apparent Power | Inverter | Inverter005_MODBUS.HR1010_s3_VA | Apparent Power | 192 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input1 | Inverter | Inverter005_MODBUS.HR5005_m1_idc_A | Current DC Input# | 193 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC Input 1 | Inverter | Inverter005_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 194 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input2 | Inverter | Inverter005_MODBUS.HR5037_m2_idc_A | Current DC Input# | 195 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC input 2 | Inverter | Inverter005_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 196 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input3 | Inverter | Inverter005_MODBUS.HR5069_m3_idc_A | Current DC Input# | 197 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC input 3 | Inverter | Inverter005_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 198 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input4 | Inverter | Inverter005_MODBUS.HR5101_m4_idc_A | Current DC Input# | 199 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC input 4 | Inverter | Inverter005_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 200 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input5 | Inverter | Inverter005_MODBUS.HR5133_m5_idc_A | Current DC Input# | 201 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC input 5 | Inverter | Inverter005_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 202 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current DC Input6 | Inverter | Inverter005_MODBUS.HR5165_m6_idc_A | Current DC Input# | 203 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC input 6 | Inverter | Inverter005_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 204 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current-AC | Inverter | Inverter005_MODBUS.HR1007_i3Avg_A | Current-AC | 205 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Current-DC | Inverter | Inverter005_MODBUS.HR1062_idcInput_A | Current-DC | 206 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Daily Energy Delivered | Inverter | Inverter005_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 207 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power Set Point | Inverter | Inverter005_MODBUS.HR0553_pRef | Real Power Set Point | 208 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Reactive Power Set Point | Inverter | Inverter005_MODBUS.HR0558_qRef | Reactive Power Set Point | 209 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Frequency | Inverter | Inverter005_MODBUS.HR1012_f3_Hz | Frequency | 210 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV005 | Dagget 3_SUB1_INV005_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Insulation Resistance | Inverter | Inverter005_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 211 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Number of DU Channels | Inverter | Inverter005_MODBUS.HR0653_duChannels | Number of DU Channels | 212 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Number of Running Modules | Inverter | Inverter005_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 213 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Operating State | Inverter | Inverter005_MODBUS.HR1123_currentStatus | Operating State | 214 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Power Factor | Inverter | Inverter005_MODBUS.HR1011_pf3 | Power Factor | 215 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV005 | Dagget 3_SUB1_INV005_Ramp Down | Inverter | Inverter005_MODBUS.HR0286_dropGradient_p | Ramp Down | 216 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Ramp Up | Inverter | Inverter005_MODBUS.HR0282_riseGradient_p | Ramp Up | 217 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power Delivered | Inverter | Inverter005_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 218 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Reactive Power Delivered | Inverter | Inverter005_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 219 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power | 220 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Reactive Power | Inverter | Inverter005_MODBUS.HR1009_q3_kvar | Reactive Power | 221 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Reactive Power Mode | Inverter | Inverter005_MODBUS.HR0552_qControlMode | Reactive Power Mode | 222 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Reactive Power Set Point Percent | Inverter | Inverter005_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 223 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power AC Percent | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power AC Percent | 224 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power-AC | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power-AC | 225 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power-DC | Inverter | Inverter005_MODBUS.HR1061_pdcInput_W | Real Power-DC | 226 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Air Intake | Inverter | Inverter005_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 227 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Cabinet | Inverter | Inverter005_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 228 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-IGBT | Inverter | Inverter005_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 229 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Temperature-Module | Inverter | Inverter005_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 230 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage A-B | Inverter | Inverter005_MODBUS.HR1005_vRS_V | Voltage A-B | 231 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage B-C | Inverter | Inverter005_MODBUS.HR1002_vST_V | Voltage B-C | 232 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage C-A | Inverter | Inverter005_MODBUS.HR1003_vTR_V | Voltage C-A | 233 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Voltage DC | Inverter | Inverter005_MODBUS.HR1051_vdcBus_V | Voltage DC | 234 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV006 | Dagget 3_SUB1_INV006_A Phase Current | Inverter | Inverter006_MODBUS.HR1004_i1_A | A Phase Current | 235 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_B Phase Current | Inverter | Inverter006_MODBUS.HR1005_i2_A | B Phase Current | 236 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_C Phase Current | Inverter | Inverter006_MODBUS.HR1006_i3_A | C Phase Current | 237 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Bus Voltage | Inverter | Inverter006_MODBUS.HR1051_vdcBus_V | Bus Voltage | 238 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV006 | Dagget 3_SUB1_INV006_Apparent Power | Inverter | Inverter006_MODBUS.HR1010_s3_VA | Apparent Power | 239 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input1 | Inverter | Inverter006_MODBUS.HR5005_m1_idc_A | Current DC Input# | 240 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC Input 1 | Inverter | Inverter006_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 241 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input2 | Inverter | Inverter006_MODBUS.HR5037_m2_idc_A | Current DC Input# | 242 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC input 2 | Inverter | Inverter006_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 243 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input3 | Inverter | Inverter006_MODBUS.HR5069_m3_idc_A | Current DC Input# | 244 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC input 3 | Inverter | Inverter006_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 245 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input4 | Inverter | Inverter006_MODBUS.HR5101_m4_idc_A | Current DC Input# | 246 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC input 4 | Inverter | Inverter006_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 247 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input5 | Inverter | Inverter006_MODBUS.HR5133_m5_idc_A | Current DC Input# | 248 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC input 5 | Inverter | Inverter006_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 249 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current DC Input6 | Inverter | Inverter006_MODBUS.HR5165_m6_idc_A | Current DC Input# | 250 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC input 6 | Inverter | Inverter006_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 251 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current-AC | Inverter | Inverter006_MODBUS.HR1007_i3Avg_A | Current-AC | 252 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Current-DC | Inverter | Inverter006_MODBUS.HR1062_idcInput_A | Current-DC | 253 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Daily Energy Delivered | Inverter | Inverter006_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 254 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power Set Point | Inverter | Inverter006_MODBUS.HR0553_pRef | Real Power Set Point | 255 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Reactive Power Set Point | Inverter | Inverter006_MODBUS.HR0558_qRef | Reactive Power Set Point | 256 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Frequency | Inverter | Inverter006_MODBUS.HR1012_f3_Hz | Frequency | 257 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV006 | Dagget 3_SUB1_INV006_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Insulation Resistance | Inverter | Inverter006_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 258 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Number of DU Channels | Inverter | Inverter006_MODBUS.HR0653_duChannels | Number of DU Channels | 259 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Number of Running Modules | Inverter | Inverter006_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 260 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Operating State | Inverter | Inverter006_MODBUS.HR1123_currentStatus | Operating State | 261 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Power Factor | Inverter | Inverter006_MODBUS.HR1011_pf3 | Power Factor | 262 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV006 | Dagget 3_SUB1_INV006_Ramp Down | Inverter | Inverter006_MODBUS.HR0286_dropGradient_p | Ramp Down | 263 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Ramp Up | Inverter | Inverter006_MODBUS.HR0282_riseGradient_p | Ramp Up | 264 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power Delivered | Inverter | Inverter006_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 265 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Reactive Power Delivered | Inverter | Inverter006_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 266 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power | 267 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Reactive Power | Inverter | Inverter006_MODBUS.HR1009_q3_kvar | Reactive Power | 268 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Reactive Power Mode | Inverter | Inverter006_MODBUS.HR0552_qControlMode | Reactive Power Mode | 269 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Reactive Power Set Point Percent | Inverter | Inverter006_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 270 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power AC Percent | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power AC Percent | 271 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power-AC | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power-AC | 272 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power-DC | Inverter | Inverter006_MODBUS.HR1061_pdcInput_W | Real Power-DC | 273 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Air Intake | Inverter | Inverter006_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 274 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Cabinet | Inverter | Inverter006_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 275 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-IGBT | Inverter | Inverter006_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 276 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Temperature-Module | Inverter | Inverter006_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 277 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage A-B | Inverter | Inverter006_MODBUS.HR1006_vRS_V | Voltage A-B | 278 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage B-C | Inverter | Inverter006_MODBUS.HR1002_vST_V | Voltage B-C | 279 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage C-A | Inverter | Inverter006_MODBUS.HR1003_vTR_V | Voltage C-A | 280 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Voltage DC | Inverter | Inverter006_MODBUS.HR1051_vdcBus_V | Voltage DC | 281 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV007 | Dagget 3_SUB1_INV007_A Phase Current | Inverter | Inverter007_MODBUS.HR1004_i1_A | A Phase Current | 282 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_B Phase Current | Inverter | Inverter007_MODBUS.HR1005_i2_A | B Phase Current | 283 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_C Phase Current | Inverter | Inverter007_MODBUS.HR1006_i3_A | C Phase Current | 284 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Bus Voltage | Inverter | Inverter007_MODBUS.HR1051_vdcBus_V | Bus Voltage | 285 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV007 | Dagget 3_SUB1_INV007_Apparent Power | Inverter | Inverter007_MODBUS.HR1010_s3_VA | Apparent Power | 286 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input1 | Inverter | Inverter007_MODBUS.HR5005_m1_idc_A | Current DC Input# | 287 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC Input 1 | Inverter | Inverter007_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 288 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input2 | Inverter | Inverter007_MODBUS.HR5037_m2_idc_A | Current DC Input# | 289 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC input 2 | Inverter | Inverter007_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 290 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input3 | Inverter | Inverter007_MODBUS.HR5069_m3_idc_A | Current DC Input# | 291 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC input 3 | Inverter | Inverter007_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 292 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input4 | Inverter | Inverter007_MODBUS.HR5101_m4_idc_A | Current DC Input# | 293 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC input 4 | Inverter | Inverter007_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 294 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input5 | Inverter | Inverter007_MODBUS.HR5133_m5_idc_A | Current DC Input# | 295 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC input 5 | Inverter | Inverter007_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 296 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current DC Input6 | Inverter | Inverter007_MODBUS.HR5165_m6_idc_A | Current DC Input# | 297 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC input 6 | Inverter | Inverter007_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 298 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current-AC | Inverter | Inverter007_MODBUS.HR1007_i3Avg_A | Current-AC | 299 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Current-DC | Inverter | Inverter007_MODBUS.HR1062_idcInput_A | Current-DC | 300 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Daily Energy Delivered | Inverter | Inverter007_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 301 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power Set Point | Inverter | Inverter007_MODBUS.HR0553_pRef | Real Power Set Point | 302 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Reactive Power Set Point | Inverter | Inverter007_MODBUS.HR0558_qRef | Reactive Power Set Point | 303 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Frequency | Inverter | Inverter007_MODBUS.HR1012_f3_Hz | Frequency | 304 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV007 | Dagget 3_SUB1_INV007_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Insulation Resistance | Inverter | Inverter007_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 305 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Number of DU Channels | Inverter | Inverter007_MODBUS.HR0653_duChannels | Number of DU Channels | 306 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Number of Running Modules | Inverter | Inverter007_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 307 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Operating State | Inverter | Inverter007_MODBUS.HR1123_currentStatus | Operating State | 308 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Power Factor | Inverter | Inverter007_MODBUS.HR1011_pf3 | Power Factor | 309 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV007 | Dagget 3_SUB1_INV007_Ramp Down | Inverter | Inverter007_MODBUS.HR0286_dropGradient_p | Ramp Down | 310 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Ramp Up | Inverter | Inverter007_MODBUS.HR0282_riseGradient_p | Ramp Up | 311 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power Delivered | Inverter | Inverter007_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 312 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Reactive Power Delivered | Inverter | Inverter007_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 313 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power | 314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Reactive Power | Inverter | Inverter007_MODBUS.HR1009_q3_kvar | Reactive Power | 315 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Reactive Power Mode | Inverter | Inverter007_MODBUS.HR0552_qControlMode | Reactive Power Mode | 316 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Reactive Power Set Point Percent | Inverter | Inverter007_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 317 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power AC Percent | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power AC Percent | 318 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power-AC | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power-AC | 319 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power-DC | Inverter | Inverter007_MODBUS.HR1061_pdcInput_W | Real Power-DC | 320 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Air Intake | Inverter | Inverter007_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 321 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Cabinet | Inverter | Inverter007_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 322 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-IGBT | Inverter | Inverter007_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 323 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Temperature-Module | Inverter | Inverter007_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 324 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage A-B | Inverter | Inverter007_MODBUS.HR1007_vRS_V | Voltage A-B | 325 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage B-C | Inverter | Inverter007_MODBUS.HR1002_vST_V | Voltage B-C | 326 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage C-A | Inverter | Inverter007_MODBUS.HR1003_vTR_V | Voltage C-A | 327 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Voltage DC | Inverter | Inverter007_MODBUS.HR1051_vdcBus_V | Voltage DC | 328 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV008 | Dagget 3_SUB1_INV008_A Phase Current | Inverter | Inverter008_MODBUS.HR1004_i1_A | A Phase Current | 329 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_B Phase Current | Inverter | Inverter008_MODBUS.HR1005_i2_A | B Phase Current | 330 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_C Phase Current | Inverter | Inverter008_MODBUS.HR1006_i3_A | C Phase Current | 331 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Bus Voltage | Inverter | Inverter008_MODBUS.HR1051_vdcBus_V | Bus Voltage | 332 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV008 | Dagget 3_SUB1_INV008_Apparent Power | Inverter | Inverter008_MODBUS.HR1010_s3_VA | Apparent Power | 333 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input1 | Inverter | Inverter008_MODBUS.HR5005_m1_idc_A | Current DC Input# | 334 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC Input 1 | Inverter | Inverter008_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 335 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input2 | Inverter | Inverter008_MODBUS.HR5037_m2_idc_A | Current DC Input# | 336 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC input 2 | Inverter | Inverter008_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 337 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input3 | Inverter | Inverter008_MODBUS.HR5069_m3_idc_A | Current DC Input# | 338 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC input 3 | Inverter | Inverter008_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 339 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input4 | Inverter | Inverter008_MODBUS.HR5101_m4_idc_A | Current DC Input# | 340 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC input 4 | Inverter | Inverter008_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 341 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input5 | Inverter | Inverter008_MODBUS.HR5133_m5_idc_A | Current DC Input# | 342 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC input 5 | Inverter | Inverter008_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 343 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current DC Input6 | Inverter | Inverter008_MODBUS.HR5165_m6_idc_A | Current DC Input# | 344 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC input 6 | Inverter | Inverter008_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 345 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current-AC | Inverter | Inverter008_MODBUS.HR1007_i3Avg_A | Current-AC | 346 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Current-DC | Inverter | Inverter008_MODBUS.HR1062_idcInput_A | Current-DC | 347 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Daily Energy Delivered | Inverter | Inverter008_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 348 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power Set Point | Inverter | Inverter008_MODBUS.HR0553_pRef | Real Power Set Point | 349 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Reactive Power Set Point | Inverter | Inverter008_MODBUS.HR0558_qRef | Reactive Power Set Point | 350 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Frequency | Inverter | Inverter008_MODBUS.HR1012_f3_Hz | Frequency | 351 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV008 | Dagget 3_SUB1_INV008_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Insulation Resistance | Inverter | Inverter008_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 352 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Number of DU Channels | Inverter | Inverter008_MODBUS.HR0653_duChannels | Number of DU Channels | 353 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Number of Running Modules | Inverter | Inverter008_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 354 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Operating State | Inverter | Inverter008_MODBUS.HR1123_currentStatus | Operating State | 355 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Power Factor | Inverter | Inverter008_MODBUS.HR1011_pf3 | Power Factor | 356 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV008 | Dagget 3_SUB1_INV008_Ramp Down | Inverter | Inverter008_MODBUS.HR0286_dropGradient_p | Ramp Down | 357 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Ramp Up | Inverter | Inverter008_MODBUS.HR0282_riseGradient_p | Ramp Up | 358 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power Delivered | Inverter | Inverter008_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 359 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Reactive Power Delivered | Inverter | Inverter008_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 360 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power | 361 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Reactive Power | Inverter | Inverter008_MODBUS.HR1009_q3_kvar | Reactive Power | 362 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Reactive Power Mode | Inverter | Inverter008_MODBUS.HR0552_qControlMode | Reactive Power Mode | 363 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Reactive Power Set Point Percent | Inverter | Inverter008_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 364 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power AC Percent | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power AC Percent | 365 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power-AC | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power-AC | 366 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power-DC | Inverter | Inverter008_MODBUS.HR1061_pdcInput_W | Real Power-DC | 367 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Air Intake | Inverter | Inverter008_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 368 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Cabinet | Inverter | Inverter008_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 369 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-IGBT | Inverter | Inverter008_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 370 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Temperature-Module | Inverter | Inverter008_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 371 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage A-B | Inverter | Inverter008_MODBUS.HR1008_vRS_V | Voltage A-B | 372 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage B-C | Inverter | Inverter008_MODBUS.HR1002_vST_V | Voltage B-C | 373 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage C-A | Inverter | Inverter008_MODBUS.HR1003_vTR_V | Voltage C-A | 374 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Voltage DC | Inverter | Inverter008_MODBUS.HR1051_vdcBus_V | Voltage DC | 375 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV009 | Dagget 3_SUB1_INV009_A Phase Current | Inverter | Inverter009_MODBUS.HR1004_i1_A | A Phase Current | 376 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_B Phase Current | Inverter | Inverter009_MODBUS.HR1005_i2_A | B Phase Current | 377 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_C Phase Current | Inverter | Inverter009_MODBUS.HR1006_i3_A | C Phase Current | 378 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Bus Voltage | Inverter | Inverter009_MODBUS.HR1051_vdcBus_V | Bus Voltage | 379 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV009 | Dagget 3_SUB1_INV009_Apparent Power | Inverter | Inverter009_MODBUS.HR1010_s3_VA | Apparent Power | 380 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input1 | Inverter | Inverter009_MODBUS.HR5005_m1_idc_A | Current DC Input# | 381 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC Input 1 | Inverter | Inverter009_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 382 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input2 | Inverter | Inverter009_MODBUS.HR5037_m2_idc_A | Current DC Input# | 383 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC input 2 | Inverter | Inverter009_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 384 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input3 | Inverter | Inverter009_MODBUS.HR5069_m3_idc_A | Current DC Input# | 385 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC input 3 | Inverter | Inverter009_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 386 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input4 | Inverter | Inverter009_MODBUS.HR5101_m4_idc_A | Current DC Input# | 387 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC input 4 | Inverter | Inverter009_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 388 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input5 | Inverter | Inverter009_MODBUS.HR5133_m5_idc_A | Current DC Input# | 389 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC input 5 | Inverter | Inverter009_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 390 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current DC Input6 | Inverter | Inverter009_MODBUS.HR5165_m6_idc_A | Current DC Input# | 391 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC input 6 | Inverter | Inverter009_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 392 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current-AC | Inverter | Inverter009_MODBUS.HR1007_i3Avg_A | Current-AC | 393 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Current-DC | Inverter | Inverter009_MODBUS.HR1062_idcInput_A | Current-DC | 394 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Daily Energy Delivered | Inverter | Inverter009_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 395 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power Set Point | Inverter | Inverter009_MODBUS.HR0553_pRef | Real Power Set Point | 396 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Reactive Power Set Point | Inverter | Inverter009_MODBUS.HR0558_qRef | Reactive Power Set Point | 397 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Frequency | Inverter | Inverter009_MODBUS.HR1012_f3_Hz | Frequency | 398 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV009 | Dagget 3_SUB1_INV009_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Insulation Resistance | Inverter | Inverter009_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 399 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Number of DU Channels | Inverter | Inverter009_MODBUS.HR0653_duChannels | Number of DU Channels | 400 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Number of Running Modules | Inverter | Inverter009_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 401 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Operating State | Inverter | Inverter009_MODBUS.HR1123_currentStatus | Operating State | 402 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Power Factor | Inverter | Inverter009_MODBUS.HR1011_pf3 | Power Factor | 403 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV009 | Dagget 3_SUB1_INV009_Ramp Down | Inverter | Inverter009_MODBUS.HR0286_dropGradient_p | Ramp Down | 404 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Ramp Up | Inverter | Inverter009_MODBUS.HR0282_riseGradient_p | Ramp Up | 405 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power Delivered | Inverter | Inverter009_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 406 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Reactive Power Delivered | Inverter | Inverter009_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 407 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power | 408 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Reactive Power | Inverter | Inverter009_MODBUS.HR1009_q3_kvar | Reactive Power | 409 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Reactive Power Mode | Inverter | Inverter009_MODBUS.HR0552_qControlMode | Reactive Power Mode | 410 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Reactive Power Set Point Percent | Inverter | Inverter009_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 411 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power AC Percent | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power AC Percent | 412 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power-AC | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power-AC | 413 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power-DC | Inverter | Inverter009_MODBUS.HR1061_pdcInput_W | Real Power-DC | 414 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Air Intake | Inverter | Inverter009_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 415 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Cabinet | Inverter | Inverter009_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 416 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-IGBT | Inverter | Inverter009_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 417 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Temperature-Module | Inverter | Inverter009_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 418 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage A-B | Inverter | Inverter009_MODBUS.HR1009_vRS_V | Voltage A-B | 419 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage B-C | Inverter | Inverter009_MODBUS.HR1002_vST_V | Voltage B-C | 420 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage C-A | Inverter | Inverter009_MODBUS.HR1003_vTR_V | Voltage C-A | 421 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Voltage DC | Inverter | Inverter009_MODBUS.HR1051_vdcBus_V | Voltage DC | 422 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV010 | Dagget 3_SUB1_INV010_A Phase Current | Inverter | Inverter010_MODBUS.HR1004_i1_A | A Phase Current | 423 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_B Phase Current | Inverter | Inverter010_MODBUS.HR1005_i2_A | B Phase Current | 424 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_C Phase Current | Inverter | Inverter010_MODBUS.HR1006_i3_A | C Phase Current | 425 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Bus Voltage | Inverter | Inverter010_MODBUS.HR1051_vdcBus_V | Bus Voltage | 426 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV010 | Dagget 3_SUB1_INV010_Apparent Power | Inverter | Inverter010_MODBUS.HR1010_s3_VA | Apparent Power | 427 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input1 | Inverter | Inverter010_MODBUS.HR5005_m1_idc_A | Current DC Input# | 428 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC Input 1 | Inverter | Inverter010_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 429 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input2 | Inverter | Inverter010_MODBUS.HR5037_m2_idc_A | Current DC Input# | 430 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC input 2 | Inverter | Inverter010_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 431 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input3 | Inverter | Inverter010_MODBUS.HR5069_m3_idc_A | Current DC Input# | 432 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC input 3 | Inverter | Inverter010_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 433 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input4 | Inverter | Inverter010_MODBUS.HR5101_m4_idc_A | Current DC Input# | 434 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC input 4 | Inverter | Inverter010_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 435 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input5 | Inverter | Inverter010_MODBUS.HR5133_m5_idc_A | Current DC Input# | 436 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC input 5 | Inverter | Inverter010_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 437 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current DC Input6 | Inverter | Inverter010_MODBUS.HR5165_m6_idc_A | Current DC Input# | 438 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC input 6 | Inverter | Inverter010_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 439 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current-AC | Inverter | Inverter010_MODBUS.HR1007_i3Avg_A | Current-AC | 440 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Current-DC | Inverter | Inverter010_MODBUS.HR1062_idcInput_A | Current-DC | 441 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Daily Energy Delivered | Inverter | Inverter010_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 442 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power Set Point | Inverter | Inverter010_MODBUS.HR0553_pRef | Real Power Set Point | 443 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Reactive Power Set Point | Inverter | Inverter010_MODBUS.HR0558_qRef | Reactive Power Set Point | 444 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Frequency | Inverter | Inverter010_MODBUS.HR1012_f3_Hz | Frequency | 445 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV010 | Dagget 3_SUB1_INV010_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Insulation Resistance | Inverter | Inverter010_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 446 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Number of DU Channels | Inverter | Inverter010_MODBUS.HR0653_duChannels | Number of DU Channels | 447 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Number of Running Modules | Inverter | Inverter010_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 448 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Operating State | Inverter | Inverter010_MODBUS.HR1123_currentStatus | Operating State | 449 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Power Factor | Inverter | Inverter010_MODBUS.HR1011_pf3 | Power Factor | 450 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV010 | Dagget 3_SUB1_INV010_Ramp Down | Inverter | Inverter010_MODBUS.HR0286_dropGradient_p | Ramp Down | 451 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Ramp Up | Inverter | Inverter010_MODBUS.HR0282_riseGradient_p | Ramp Up | 452 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power Delivered | Inverter | Inverter010_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 453 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Reactive Power Delivered | Inverter | Inverter010_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 454 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power | 455 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Reactive Power | Inverter | Inverter010_MODBUS.HR1009_q3_kvar | Reactive Power | 456 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Reactive Power Mode | Inverter | Inverter010_MODBUS.HR0552_qControlMode | Reactive Power Mode | 457 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Reactive Power Set Point Percent | Inverter | Inverter010_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 458 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power AC Percent | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power AC Percent | 459 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power-AC | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power-AC | 460 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power-DC | Inverter | Inverter010_MODBUS.HR1061_pdcInput_W | Real Power-DC | 461 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Air Intake | Inverter | Inverter010_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 462 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Cabinet | Inverter | Inverter010_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 463 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-IGBT | Inverter | Inverter010_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 464 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Temperature-Module | Inverter | Inverter010_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 465 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage A-B | Inverter | Inverter010_MODBUS.HR1010_vRS_V | Voltage A-B | 466 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage B-C | Inverter | Inverter010_MODBUS.HR1002_vST_V | Voltage B-C | 467 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage C-A | Inverter | Inverter010_MODBUS.HR1003_vTR_V | Voltage C-A | 468 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Voltage DC | Inverter | Inverter010_MODBUS.HR1051_vdcBus_V | Voltage DC | 469 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV011 | Dagget 3_SUB1_INV011_A Phase Current | Inverter | inverter011_MODBUS.HR1004_i1_A | A Phase Current | 470 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_B Phase Current | Inverter | inverter011_MODBUS.HR1005_i2_A | B Phase Current | 471 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_C Phase Current | Inverter | inverter011_MODBUS.HR1006_i3_A | C Phase Current | 472 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Bus Voltage | Inverter | inverter011_MODBUS.HR1051_vdcBus_V | Bus Voltage | 473 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV011 | Dagget 3_SUB1_INV011_Apparent Power | Inverter | inverter011_MODBUS.HR1010_s3_VA | Apparent Power | 474 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input1 | Inverter | inverter011_MODBUS.HR5005_m1_idc_A | Current DC Input# | 475 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC Input 1 | Inverter | inverter011_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 476 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input2 | Inverter | inverter011_MODBUS.HR5037_m2_idc_A | Current DC Input# | 477 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC input 2 | Inverter | inverter011_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 478 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input3 | Inverter | inverter011_MODBUS.HR5069_m3_idc_A | Current DC Input# | 479 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC input 3 | Inverter | inverter011_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 480 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input4 | Inverter | inverter011_MODBUS.HR5101_m4_idc_A | Current DC Input# | 481 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC input 4 | Inverter | inverter011_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 482 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input5 | Inverter | inverter011_MODBUS.HR5133_m5_idc_A | Current DC Input# | 483 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC input 5 | Inverter | inverter011_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 484 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current DC Input6 | Inverter | inverter011_MODBUS.HR5165_m6_idc_A | Current DC Input# | 485 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC input 6 | Inverter | inverter011_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 486 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current-AC | Inverter | inverter011_MODBUS.HR1007_i3Avg_A | Current-AC | 487 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Current-DC | Inverter | inverter011_MODBUS.HR1062_idcInput_A | Current-DC | 488 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Daily Energy Delivered | Inverter | inverter011_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 489 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power Set Point | Inverter | inverter011_MODBUS.HR0553_pRef | Real Power Set Point | 490 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Reactive Power Set Point | Inverter | inverter011_MODBUS.HR0558_qRef | Reactive Power Set Point | 491 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Frequency | Inverter | inverter011_MODBUS.HR1012_f3_Hz | Frequency | 492 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV011 | Dagget 3_SUB1_INV011_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Insulation Resistance | Inverter | inverter011_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 493 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Number of DU Channels | Inverter | inverter011_MODBUS.HR0653_duChannels | Number of DU Channels | 494 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Number of Running Modules | Inverter | inverter011_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 495 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Operating State | Inverter | inverter011_MODBUS.HR1123_currentStatus | Operating State | 496 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Power Factor | Inverter | inverter011_MODBUS.HR1011_pf3 | Power Factor | 497 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV011 | Dagget 3_SUB1_INV011_Ramp Down | Inverter | inverter011_MODBUS.HR0286_dropGradient_p | Ramp Down | 498 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Ramp Up | Inverter | inverter011_MODBUS.HR0282_riseGradient_p | Ramp Up | 499 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power Delivered | Inverter | inverter011_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 500 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Reactive Power Delivered | Inverter | inverter011_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 501 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power | 502 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Reactive Power | Inverter | inverter011_MODBUS.HR1009_q3_kvar | Reactive Power | 503 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Reactive Power Mode | Inverter | inverter011_MODBUS.HR0552_qControlMode | Reactive Power Mode | 504 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Reactive Power Set Point Percent | Inverter | inverter011_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 505 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power AC Percent | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power AC Percent | 506 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power-AC | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power-AC | 507 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power-DC | Inverter | inverter011_MODBUS.HR1061_pdcInput_W | Real Power-DC | 508 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Air Intake | Inverter | inverter011_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 509 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Cabinet | Inverter | inverter011_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 510 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-IGBT | Inverter | inverter011_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 511 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Temperature-Module | Inverter | inverter011_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 512 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage A-B | Inverter | inverter011_MODBUS.HR1001_vRS_V | Voltage A-B | 513 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage B-C | Inverter | inverter011_MODBUS.HR1002_vST_V | Voltage B-C | 514 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage C-A | Inverter | inverter011_MODBUS.HR1003_vTR_V | Voltage C-A | 515 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Voltage DC | Inverter | inverter011_MODBUS.HR1051_vdcBus_V | Voltage DC | 516 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV012 | Dagget 3_SUB1_INV012_A Phase Current | Inverter | inverter012_MODBUS.HR1004_i1_A | A Phase Current | 517 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_B Phase Current | Inverter | inverter012_MODBUS.HR1005_i2_A | B Phase Current | 518 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_C Phase Current | Inverter | inverter012_MODBUS.HR1006_i3_A | C Phase Current | 519 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Bus Voltage | Inverter | inverter012_MODBUS.HR1051_vdcBus_V | Bus Voltage | 520 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV012 | Dagget 3_SUB1_INV012_Apparent Power | Inverter | inverter012_MODBUS.HR1010_s3_VA | Apparent Power | 521 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input1 | Inverter | inverter012_MODBUS.HR5005_m1_idc_A | Current DC Input# | 522 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC Input 1 | Inverter | inverter012_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 523 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input2 | Inverter | inverter012_MODBUS.HR5037_m2_idc_A | Current DC Input# | 524 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC input 2 | Inverter | inverter012_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 525 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input3 | Inverter | inverter012_MODBUS.HR5069_m3_idc_A | Current DC Input# | 526 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC input 3 | Inverter | inverter012_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 527 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input4 | Inverter | inverter012_MODBUS.HR5101_m4_idc_A | Current DC Input# | 528 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC input 4 | Inverter | inverter012_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 529 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input5 | Inverter | inverter012_MODBUS.HR5133_m5_idc_A | Current DC Input# | 530 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC input 5 | Inverter | inverter012_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 531 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current DC Input6 | Inverter | inverter012_MODBUS.HR5165_m6_idc_A | Current DC Input# | 532 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC input 6 | Inverter | inverter012_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 533 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current-AC | Inverter | inverter012_MODBUS.HR1007_i3Avg_A | Current-AC | 534 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Current-DC | Inverter | inverter012_MODBUS.HR1062_idcInput_A | Current-DC | 535 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Daily Energy Delivered | Inverter | inverter012_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 536 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power Set Point | Inverter | inverter012_MODBUS.HR0553_pRef | Real Power Set Point | 537 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Reactive Power Set Point | Inverter | inverter012_MODBUS.HR0558_qRef | Reactive Power Set Point | 538 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Frequency | Inverter | inverter012_MODBUS.HR1012_f3_Hz | Frequency | 539 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV012 | Dagget 3_SUB1_INV012_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Insulation Resistance | Inverter | inverter012_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 540 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Number of DU Channels | Inverter | inverter012_MODBUS.HR0653_duChannels | Number of DU Channels | 541 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Number of Running Modules | Inverter | inverter012_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 542 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Operating State | Inverter | inverter012_MODBUS.HR1123_currentStatus | Operating State | 543 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Power Factor | Inverter | inverter012_MODBUS.HR1011_pf3 | Power Factor | 544 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV012 | Dagget 3_SUB1_INV012_Ramp Down | Inverter | inverter012_MODBUS.HR0286_dropGradient_p | Ramp Down | 545 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Ramp Up | Inverter | inverter012_MODBUS.HR0282_riseGradient_p | Ramp Up | 546 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power Delivered | Inverter | inverter012_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 547 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Reactive Power Delivered | Inverter | inverter012_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 548 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power | 549 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Reactive Power | Inverter | inverter012_MODBUS.HR1009_q3_kvar | Reactive Power | 550 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Reactive Power Mode | Inverter | inverter012_MODBUS.HR0552_qControlMode | Reactive Power Mode | 551 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Reactive Power Set Point Percent | Inverter | inverter012_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 552 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power AC Percent | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power AC Percent | 553 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power-AC | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power-AC | 554 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power-DC | Inverter | inverter012_MODBUS.HR1061_pdcInput_W | Real Power-DC | 555 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Air Intake | Inverter | inverter012_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 556 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Cabinet | Inverter | inverter012_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 557 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-IGBT | Inverter | inverter012_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 558 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Temperature-Module | Inverter | inverter012_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 559 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage A-B | Inverter | inverter012_MODBUS.HR1002_vRS_V | Voltage A-B | 560 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage B-C | Inverter | inverter012_MODBUS.HR1002_vST_V | Voltage B-C | 561 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage C-A | Inverter | inverter012_MODBUS.HR1003_vTR_V | Voltage C-A | 562 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Voltage DC | Inverter | inverter012_MODBUS.HR1051_vdcBus_V | Voltage DC | 563 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV013 | Dagget 3_SUB1_INV013_A Phase Current | Inverter | inverter013_MODBUS.HR1004_i1_A | A Phase Current | 564 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_B Phase Current | Inverter | inverter013_MODBUS.HR1005_i2_A | B Phase Current | 565 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_C Phase Current | Inverter | inverter013_MODBUS.HR1006_i3_A | C Phase Current | 566 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Bus Voltage | Inverter | inverter013_MODBUS.HR1051_vdcBus_V | Bus Voltage | 567 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV013 | Dagget 3_SUB1_INV013_Apparent Power | Inverter | inverter013_MODBUS.HR1010_s3_VA | Apparent Power | 568 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input1 | Inverter | inverter013_MODBUS.HR5005_m1_idc_A | Current DC Input# | 569 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC Input 1 | Inverter | inverter013_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 570 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input2 | Inverter | inverter013_MODBUS.HR5037_m2_idc_A | Current DC Input# | 571 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC input 2 | Inverter | inverter013_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 572 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input3 | Inverter | inverter013_MODBUS.HR5069_m3_idc_A | Current DC Input# | 573 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC input 3 | Inverter | inverter013_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 574 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input4 | Inverter | inverter013_MODBUS.HR5101_m4_idc_A | Current DC Input# | 575 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC input 4 | Inverter | inverter013_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 576 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input5 | Inverter | inverter013_MODBUS.HR5133_m5_idc_A | Current DC Input# | 577 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC input 5 | Inverter | inverter013_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 578 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current DC Input6 | Inverter | inverter013_MODBUS.HR5165_m6_idc_A | Current DC Input# | 579 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC input 6 | Inverter | inverter013_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 580 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current-AC | Inverter | inverter013_MODBUS.HR1007_i3Avg_A | Current-AC | 581 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Current-DC | Inverter | inverter013_MODBUS.HR1062_idcInput_A | Current-DC | 582 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Daily Energy Delivered | Inverter | inverter013_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 583 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power Set Point | Inverter | inverter013_MODBUS.HR0553_pRef | Real Power Set Point | 584 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Reactive Power Set Point | Inverter | inverter013_MODBUS.HR0558_qRef | Reactive Power Set Point | 585 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Frequency | Inverter | inverter013_MODBUS.HR1012_f3_Hz | Frequency | 586 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV013 | Dagget 3_SUB1_INV013_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Insulation Resistance | Inverter | inverter013_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 587 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Number of DU Channels | Inverter | inverter013_MODBUS.HR0653_duChannels | Number of DU Channels | 588 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Number of Running Modules | Inverter | inverter013_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 589 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Operating State | Inverter | inverter013_MODBUS.HR1123_currentStatus | Operating State | 590 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Power Factor | Inverter | inverter013_MODBUS.HR1011_pf3 | Power Factor | 591 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV013 | Dagget 3_SUB1_INV013_Ramp Down | Inverter | inverter013_MODBUS.HR0286_dropGradient_p | Ramp Down | 592 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Ramp Up | Inverter | inverter013_MODBUS.HR0282_riseGradient_p | Ramp Up | 593 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power Delivered | Inverter | inverter013_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 594 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Reactive Power Delivered | Inverter | inverter013_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 595 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power | 596 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Reactive Power | Inverter | inverter013_MODBUS.HR1009_q3_kvar | Reactive Power | 597 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Reactive Power Mode | Inverter | inverter013_MODBUS.HR0552_qControlMode | Reactive Power Mode | 598 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Reactive Power Set Point Percent | Inverter | inverter013_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 599 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power AC Percent | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power AC Percent | 600 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power-AC | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power-AC | 601 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power-DC | Inverter | inverter013_MODBUS.HR1061_pdcInput_W | Real Power-DC | 602 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Air Intake | Inverter | inverter013_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 603 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Cabinet | Inverter | inverter013_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 604 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-IGBT | Inverter | inverter013_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 605 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Temperature-Module | Inverter | inverter013_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 606 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage A-B | Inverter | inverter013_MODBUS.HR1003_vRS_V | Voltage A-B | 607 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage B-C | Inverter | inverter013_MODBUS.HR1002_vST_V | Voltage B-C | 608 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage C-A | Inverter | inverter013_MODBUS.HR1003_vTR_V | Voltage C-A | 609 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Voltage DC | Inverter | inverter013_MODBUS.HR1051_vdcBus_V | Voltage DC | 610 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV014 | Dagget 3_SUB1_INV014_A Phase Current | Inverter | inverter014_MODBUS.HR1004_i1_A | A Phase Current | 611 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_B Phase Current | Inverter | inverter014_MODBUS.HR1005_i2_A | B Phase Current | 612 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_C Phase Current | Inverter | inverter014_MODBUS.HR1006_i3_A | C Phase Current | 613 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Bus Voltage | Inverter | inverter014_MODBUS.HR1051_vdcBus_V | Bus Voltage | 614 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV014 | Dagget 3_SUB1_INV014_Apparent Power | Inverter | inverter014_MODBUS.HR1010_s3_VA | Apparent Power | 615 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input1 | Inverter | inverter014_MODBUS.HR5005_m1_idc_A | Current DC Input# | 616 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC Input 1 | Inverter | inverter014_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 617 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input2 | Inverter | inverter014_MODBUS.HR5037_m2_idc_A | Current DC Input# | 618 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC input 2 | Inverter | inverter014_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 619 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input3 | Inverter | inverter014_MODBUS.HR5069_m3_idc_A | Current DC Input# | 620 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC input 3 | Inverter | inverter014_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 621 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input4 | Inverter | inverter014_MODBUS.HR5101_m4_idc_A | Current DC Input# | 622 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC input 4 | Inverter | inverter014_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 623 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input5 | Inverter | inverter014_MODBUS.HR5133_m5_idc_A | Current DC Input# | 624 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC input 5 | Inverter | inverter014_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 625 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current DC Input6 | Inverter | inverter014_MODBUS.HR5165_m6_idc_A | Current DC Input# | 626 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC input 6 | Inverter | inverter014_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 627 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current-AC | Inverter | inverter014_MODBUS.HR1007_i3Avg_A | Current-AC | 628 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Current-DC | Inverter | inverter014_MODBUS.HR1062_idcInput_A | Current-DC | 629 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Daily Energy Delivered | Inverter | inverter014_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 630 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power Set Point | Inverter | inverter014_MODBUS.HR0553_pRef | Real Power Set Point | 631 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Reactive Power Set Point | Inverter | inverter014_MODBUS.HR0558_qRef | Reactive Power Set Point | 632 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Frequency | Inverter | inverter014_MODBUS.HR1012_f3_Hz | Frequency | 633 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV014 | Dagget 3_SUB1_INV014_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Insulation Resistance | Inverter | inverter014_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 634 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Number of DU Channels | Inverter | inverter014_MODBUS.HR0653_duChannels | Number of DU Channels | 635 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Number of Running Modules | Inverter | inverter014_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 636 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Operating State | Inverter | inverter014_MODBUS.HR1123_currentStatus | Operating State | 637 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Power Factor | Inverter | inverter014_MODBUS.HR1011_pf3 | Power Factor | 638 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV014 | Dagget 3_SUB1_INV014_Ramp Down | Inverter | inverter014_MODBUS.HR0286_dropGradient_p | Ramp Down | 639 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Ramp Up | Inverter | inverter014_MODBUS.HR0282_riseGradient_p | Ramp Up | 640 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power Delivered | Inverter | inverter014_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 641 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Reactive Power Delivered | Inverter | inverter014_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 642 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power | 643 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Reactive Power | Inverter | inverter014_MODBUS.HR1009_q3_kvar | Reactive Power | 644 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Reactive Power Mode | Inverter | inverter014_MODBUS.HR0552_qControlMode | Reactive Power Mode | 645 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Reactive Power Set Point Percent | Inverter | inverter014_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 646 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power AC Percent | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power AC Percent | 647 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power-AC | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power-AC | 648 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power-DC | Inverter | inverter014_MODBUS.HR1061_pdcInput_W | Real Power-DC | 649 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Air Intake | Inverter | inverter014_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 650 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Cabinet | Inverter | inverter014_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 651 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-IGBT | Inverter | inverter014_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 652 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Temperature-Module | Inverter | inverter014_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 653 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage A-B | Inverter | inverter014_MODBUS.HR1004_vRS_V | Voltage A-B | 654 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage B-C | Inverter | inverter014_MODBUS.HR1002_vST_V | Voltage B-C | 655 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage C-A | Inverter | inverter014_MODBUS.HR1003_vTR_V | Voltage C-A | 656 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Voltage DC | Inverter | inverter014_MODBUS.HR1051_vdcBus_V | Voltage DC | 657 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV015 | Dagget 3_SUB1_INV015_A Phase Current | Inverter | inverter015_MODBUS.HR1004_i1_A | A Phase Current | 658 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_B Phase Current | Inverter | inverter015_MODBUS.HR1005_i2_A | B Phase Current | 659 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_C Phase Current | Inverter | inverter015_MODBUS.HR1006_i3_A | C Phase Current | 660 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Bus Voltage | Inverter | inverter015_MODBUS.HR1051_vdcBus_V | Bus Voltage | 661 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV015 | Dagget 3_SUB1_INV015_Apparent Power | Inverter | inverter015_MODBUS.HR1010_s3_VA | Apparent Power | 662 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input1 | Inverter | inverter015_MODBUS.HR5005_m1_idc_A | Current DC Input# | 663 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC Input 1 | Inverter | inverter015_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 664 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input2 | Inverter | inverter015_MODBUS.HR5037_m2_idc_A | Current DC Input# | 665 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC input 2 | Inverter | inverter015_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 666 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input3 | Inverter | inverter015_MODBUS.HR5069_m3_idc_A | Current DC Input# | 667 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC input 3 | Inverter | inverter015_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 668 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input4 | Inverter | inverter015_MODBUS.HR5101_m4_idc_A | Current DC Input# | 669 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC input 4 | Inverter | inverter015_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 670 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input5 | Inverter | inverter015_MODBUS.HR5133_m5_idc_A | Current DC Input# | 671 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC input 5 | Inverter | inverter015_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 672 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current DC Input6 | Inverter | inverter015_MODBUS.HR5165_m6_idc_A | Current DC Input# | 673 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC input 6 | Inverter | inverter015_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 674 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current-AC | Inverter | inverter015_MODBUS.HR1007_i3Avg_A | Current-AC | 675 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Current-DC | Inverter | inverter015_MODBUS.HR1062_idcInput_A | Current-DC | 676 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Daily Energy Delivered | Inverter | inverter015_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 677 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power Set Point | Inverter | inverter015_MODBUS.HR0553_pRef | Real Power Set Point | 678 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Reactive Power Set Point | Inverter | inverter015_MODBUS.HR0558_qRef | Reactive Power Set Point | 679 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Frequency | Inverter | inverter015_MODBUS.HR1012_f3_Hz | Frequency | 680 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV015 | Dagget 3_SUB1_INV015_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Insulation Resistance | Inverter | inverter015_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 681 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Number of DU Channels | Inverter | inverter015_MODBUS.HR0653_duChannels | Number of DU Channels | 682 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Number of Running Modules | Inverter | inverter015_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 683 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Operating State | Inverter | inverter015_MODBUS.HR1123_currentStatus | Operating State | 684 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Power Factor | Inverter | inverter015_MODBUS.HR1011_pf3 | Power Factor | 685 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV015 | Dagget 3_SUB1_INV015_Ramp Down | Inverter | inverter015_MODBUS.HR0286_dropGradient_p | Ramp Down | 686 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Ramp Up | Inverter | inverter015_MODBUS.HR0282_riseGradient_p | Ramp Up | 687 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power Delivered | Inverter | inverter015_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 688 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Reactive Power Delivered | Inverter | inverter015_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 689 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power | 690 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Reactive Power | Inverter | inverter015_MODBUS.HR1009_q3_kvar | Reactive Power | 691 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Reactive Power Mode | Inverter | inverter015_MODBUS.HR0552_qControlMode | Reactive Power Mode | 692 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Reactive Power Set Point Percent | Inverter | inverter015_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 693 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power AC Percent | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power AC Percent | 694 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power-AC | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power-AC | 695 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power-DC | Inverter | inverter015_MODBUS.HR1061_pdcInput_W | Real Power-DC | 696 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Air Intake | Inverter | inverter015_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 697 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Cabinet | Inverter | inverter015_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 698 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-IGBT | Inverter | inverter015_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 699 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Temperature-Module | Inverter | inverter015_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 700 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage A-B | Inverter | inverter015_MODBUS.HR1005_vRS_V | Voltage A-B | 701 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage B-C | Inverter | inverter015_MODBUS.HR1002_vST_V | Voltage B-C | 702 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage C-A | Inverter | inverter015_MODBUS.HR1003_vTR_V | Voltage C-A | 703 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Voltage DC | Inverter | inverter015_MODBUS.HR1051_vdcBus_V | Voltage DC | 704 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV016 | Dagget 3_SUB1_INV016_A Phase Current | Inverter | inverter016_MODBUS.HR1004_i1_A | A Phase Current | 705 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_B Phase Current | Inverter | inverter016_MODBUS.HR1005_i2_A | B Phase Current | 706 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_C Phase Current | Inverter | inverter016_MODBUS.HR1006_i3_A | C Phase Current | 707 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Bus Voltage | Inverter | inverter016_MODBUS.HR1051_vdcBus_V | Bus Voltage | 708 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV016 | Dagget 3_SUB1_INV016_Apparent Power | Inverter | inverter016_MODBUS.HR1010_s3_VA | Apparent Power | 709 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input1 | Inverter | inverter016_MODBUS.HR5005_m1_idc_A | Current DC Input# | 710 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC Input 1 | Inverter | inverter016_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 711 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input2 | Inverter | inverter016_MODBUS.HR5037_m2_idc_A | Current DC Input# | 712 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC input 2 | Inverter | inverter016_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 713 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input3 | Inverter | inverter016_MODBUS.HR5069_m3_idc_A | Current DC Input# | 714 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC input 3 | Inverter | inverter016_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 715 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input4 | Inverter | inverter016_MODBUS.HR5101_m4_idc_A | Current DC Input# | 716 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC input 4 | Inverter | inverter016_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 717 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input5 | Inverter | inverter016_MODBUS.HR5133_m5_idc_A | Current DC Input# | 718 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC input 5 | Inverter | inverter016_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 719 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current DC Input6 | Inverter | inverter016_MODBUS.HR5165_m6_idc_A | Current DC Input# | 720 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC input 6 | Inverter | inverter016_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 721 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current-AC | Inverter | inverter016_MODBUS.HR1007_i3Avg_A | Current-AC | 722 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Current-DC | Inverter | inverter016_MODBUS.HR1062_idcInput_A | Current-DC | 723 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Daily Energy Delivered | Inverter | inverter016_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 724 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power Set Point | Inverter | inverter016_MODBUS.HR0553_pRef | Real Power Set Point | 725 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Reactive Power Set Point | Inverter | inverter016_MODBUS.HR0558_qRef | Reactive Power Set Point | 726 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Frequency | Inverter | inverter016_MODBUS.HR1012_f3_Hz | Frequency | 727 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV016 | Dagget 3_SUB1_INV016_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Insulation Resistance | Inverter | inverter016_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 728 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Number of DU Channels | Inverter | inverter016_MODBUS.HR0653_duChannels | Number of DU Channels | 729 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Number of Running Modules | Inverter | inverter016_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 730 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Operating State | Inverter | inverter016_MODBUS.HR1123_currentStatus | Operating State | 731 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Power Factor | Inverter | inverter016_MODBUS.HR1011_pf3 | Power Factor | 732 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV016 | Dagget 3_SUB1_INV016_Ramp Down | Inverter | inverter016_MODBUS.HR0286_dropGradient_p | Ramp Down | 733 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Ramp Up | Inverter | inverter016_MODBUS.HR0282_riseGradient_p | Ramp Up | 734 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power Delivered | Inverter | inverter016_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 735 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Reactive Power Delivered | Inverter | inverter016_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 736 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power | 737 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Reactive Power | Inverter | inverter016_MODBUS.HR1009_q3_kvar | Reactive Power | 738 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Reactive Power Mode | Inverter | inverter016_MODBUS.HR0552_qControlMode | Reactive Power Mode | 739 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Reactive Power Set Point Percent | Inverter | inverter016_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 740 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power AC Percent | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power AC Percent | 741 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power-AC | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power-AC | 742 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power-DC | Inverter | inverter016_MODBUS.HR1061_pdcInput_W | Real Power-DC | 743 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Air Intake | Inverter | inverter016_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 744 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Cabinet | Inverter | inverter016_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 745 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-IGBT | Inverter | inverter016_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 746 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Temperature-Module | Inverter | inverter016_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 747 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage A-B | Inverter | inverter016_MODBUS.HR1006_vRS_V | Voltage A-B | 748 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage B-C | Inverter | inverter016_MODBUS.HR1002_vST_V | Voltage B-C | 749 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage C-A | Inverter | inverter016_MODBUS.HR1003_vTR_V | Voltage C-A | 750 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Voltage DC | Inverter | inverter016_MODBUS.HR1051_vdcBus_V | Voltage DC | 751 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV017 | Dagget 3_SUB1_INV017_A Phase Current | Inverter | inverter017_MODBUS.HR1004_i1_A | A Phase Current | 752 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_B Phase Current | Inverter | inverter017_MODBUS.HR1005_i2_A | B Phase Current | 753 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_C Phase Current | Inverter | inverter017_MODBUS.HR1006_i3_A | C Phase Current | 754 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Bus Voltage | Inverter | inverter017_MODBUS.HR1051_vdcBus_V | Bus Voltage | 755 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV017 | Dagget 3_SUB1_INV017_Apparent Power | Inverter | inverter017_MODBUS.HR1010_s3_VA | Apparent Power | 756 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input1 | Inverter | inverter017_MODBUS.HR5005_m1_idc_A | Current DC Input# | 757 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC Input 1 | Inverter | inverter017_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 758 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input2 | Inverter | inverter017_MODBUS.HR5037_m2_idc_A | Current DC Input# | 759 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC input 2 | Inverter | inverter017_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 760 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input3 | Inverter | inverter017_MODBUS.HR5069_m3_idc_A | Current DC Input# | 761 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC input 3 | Inverter | inverter017_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 762 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input4 | Inverter | inverter017_MODBUS.HR5101_m4_idc_A | Current DC Input# | 763 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC input 4 | Inverter | inverter017_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 764 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input5 | Inverter | inverter017_MODBUS.HR5133_m5_idc_A | Current DC Input# | 765 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC input 5 | Inverter | inverter017_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 766 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current DC Input6 | Inverter | inverter017_MODBUS.HR5165_m6_idc_A | Current DC Input# | 767 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC input 6 | Inverter | inverter017_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 768 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current-AC | Inverter | inverter017_MODBUS.HR1007_i3Avg_A | Current-AC | 769 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Current-DC | Inverter | inverter017_MODBUS.HR1062_idcInput_A | Current-DC | 770 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Daily Energy Delivered | Inverter | inverter017_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 771 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power Set Point | Inverter | inverter017_MODBUS.HR0553_pRef | Real Power Set Point | 772 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Reactive Power Set Point | Inverter | inverter017_MODBUS.HR0558_qRef | Reactive Power Set Point | 773 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Frequency | Inverter | inverter017_MODBUS.HR1012_f3_Hz | Frequency | 774 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV017 | Dagget 3_SUB1_INV017_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Insulation Resistance | Inverter | inverter017_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 775 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Number of DU Channels | Inverter | inverter017_MODBUS.HR0653_duChannels | Number of DU Channels | 776 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Number of Running Modules | Inverter | inverter017_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 777 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Operating State | Inverter | inverter017_MODBUS.HR1123_currentStatus | Operating State | 778 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Power Factor | Inverter | inverter017_MODBUS.HR1011_pf3 | Power Factor | 779 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV017 | Dagget 3_SUB1_INV017_Ramp Down | Inverter | inverter017_MODBUS.HR0286_dropGradient_p | Ramp Down | 780 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Ramp Up | Inverter | inverter017_MODBUS.HR0282_riseGradient_p | Ramp Up | 781 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power Delivered | Inverter | inverter017_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 782 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Reactive Power Delivered | Inverter | inverter017_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 783 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power | 784 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Reactive Power | Inverter | inverter017_MODBUS.HR1009_q3_kvar | Reactive Power | 785 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Reactive Power Mode | Inverter | inverter017_MODBUS.HR0552_qControlMode | Reactive Power Mode | 786 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Reactive Power Set Point Percent | Inverter | inverter017_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 787 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power AC Percent | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power AC Percent | 788 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power-AC | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power-AC | 789 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power-DC | Inverter | inverter017_MODBUS.HR1061_pdcInput_W | Real Power-DC | 790 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Air Intake | Inverter | inverter017_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 791 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Cabinet | Inverter | inverter017_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 792 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-IGBT | Inverter | inverter017_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 793 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Temperature-Module | Inverter | inverter017_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 794 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage A-B | Inverter | inverter017_MODBUS.HR1007_vRS_V | Voltage A-B | 795 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage B-C | Inverter | inverter017_MODBUS.HR1002_vST_V | Voltage B-C | 796 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage C-A | Inverter | inverter017_MODBUS.HR1003_vTR_V | Voltage C-A | 797 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Voltage DC | Inverter | inverter017_MODBUS.HR1051_vdcBus_V | Voltage DC | 798 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV018 | Dagget 3_SUB1_INV018_A Phase Current | Inverter | inverter018_MODBUS.HR1004_i1_A | A Phase Current | 799 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_B Phase Current | Inverter | inverter018_MODBUS.HR1005_i2_A | B Phase Current | 800 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_C Phase Current | Inverter | inverter018_MODBUS.HR1006_i3_A | C Phase Current | 801 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Bus Voltage | Inverter | inverter018_MODBUS.HR1051_vdcBus_V | Bus Voltage | 802 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV018 | Dagget 3_SUB1_INV018_Apparent Power | Inverter | inverter018_MODBUS.HR1010_s3_VA | Apparent Power | 803 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input1 | Inverter | inverter018_MODBUS.HR5005_m1_idc_A | Current DC Input# | 804 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC Input 1 | Inverter | inverter018_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 805 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input2 | Inverter | inverter018_MODBUS.HR5037_m2_idc_A | Current DC Input# | 806 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC input 2 | Inverter | inverter018_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 807 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input3 | Inverter | inverter018_MODBUS.HR5069_m3_idc_A | Current DC Input# | 808 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC input 3 | Inverter | inverter018_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 809 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input4 | Inverter | inverter018_MODBUS.HR5101_m4_idc_A | Current DC Input# | 810 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC input 4 | Inverter | inverter018_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 811 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input5 | Inverter | inverter018_MODBUS.HR5133_m5_idc_A | Current DC Input# | 812 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC input 5 | Inverter | inverter018_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 813 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current DC Input6 | Inverter | inverter018_MODBUS.HR5165_m6_idc_A | Current DC Input# | 814 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC input 6 | Inverter | inverter018_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 815 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current-AC | Inverter | inverter018_MODBUS.HR1007_i3Avg_A | Current-AC | 816 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Current-DC | Inverter | inverter018_MODBUS.HR1062_idcInput_A | Current-DC | 817 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Daily Energy Delivered | Inverter | inverter018_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 818 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power Set Point | Inverter | inverter018_MODBUS.HR0553_pRef | Real Power Set Point | 819 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Reactive Power Set Point | Inverter | inverter018_MODBUS.HR0558_qRef | Reactive Power Set Point | 820 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Frequency | Inverter | inverter018_MODBUS.HR1012_f3_Hz | Frequency | 821 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV018 | Dagget 3_SUB1_INV018_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Insulation Resistance | Inverter | inverter018_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 822 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Number of DU Channels | Inverter | inverter018_MODBUS.HR0653_duChannels | Number of DU Channels | 823 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Number of Running Modules | Inverter | inverter018_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 824 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Operating State | Inverter | inverter018_MODBUS.HR1123_currentStatus | Operating State | 825 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Power Factor | Inverter | inverter018_MODBUS.HR1011_pf3 | Power Factor | 826 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV018 | Dagget 3_SUB1_INV018_Ramp Down | Inverter | inverter018_MODBUS.HR0286_dropGradient_p | Ramp Down | 827 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Ramp Up | Inverter | inverter018_MODBUS.HR0282_riseGradient_p | Ramp Up | 828 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power Delivered | Inverter | inverter018_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 829 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Reactive Power Delivered | Inverter | inverter018_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 830 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power | 831 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Reactive Power | Inverter | inverter018_MODBUS.HR1009_q3_kvar | Reactive Power | 832 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Reactive Power Mode | Inverter | inverter018_MODBUS.HR0552_qControlMode | Reactive Power Mode | 833 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Reactive Power Set Point Percent | Inverter | inverter018_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 834 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power AC Percent | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power AC Percent | 835 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power-AC | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power-AC | 836 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power-DC | Inverter | inverter018_MODBUS.HR1061_pdcInput_W | Real Power-DC | 837 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Air Intake | Inverter | inverter018_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 838 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Cabinet | Inverter | inverter018_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 839 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-IGBT | Inverter | inverter018_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 840 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Temperature-Module | Inverter | inverter018_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 841 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage A-B | Inverter | inverter018_MODBUS.HR1008_vRS_V | Voltage A-B | 842 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage B-C | Inverter | inverter018_MODBUS.HR1002_vST_V | Voltage B-C | 843 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage C-A | Inverter | inverter018_MODBUS.HR1003_vTR_V | Voltage C-A | 844 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Voltage DC | Inverter | inverter018_MODBUS.HR1051_vdcBus_V | Voltage DC | 845 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV019 | Dagget 3_SUB1_INV019_A Phase Current | Inverter | inverter019_MODBUS.HR1004_i1_A | A Phase Current | 846 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_B Phase Current | Inverter | inverter019_MODBUS.HR1005_i2_A | B Phase Current | 847 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_C Phase Current | Inverter | inverter019_MODBUS.HR1006_i3_A | C Phase Current | 848 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Bus Voltage | Inverter | inverter019_MODBUS.HR1051_vdcBus_V | Bus Voltage | 849 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV019 | Dagget 3_SUB1_INV019_Apparent Power | Inverter | inverter019_MODBUS.HR1010_s3_VA | Apparent Power | 850 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input1 | Inverter | inverter019_MODBUS.HR5005_m1_idc_A | Current DC Input# | 851 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC Input 1 | Inverter | inverter019_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 852 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input2 | Inverter | inverter019_MODBUS.HR5037_m2_idc_A | Current DC Input# | 853 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC input 2 | Inverter | inverter019_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 854 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input3 | Inverter | inverter019_MODBUS.HR5069_m3_idc_A | Current DC Input# | 855 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC input 3 | Inverter | inverter019_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 856 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input4 | Inverter | inverter019_MODBUS.HR5101_m4_idc_A | Current DC Input# | 857 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC input 4 | Inverter | inverter019_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 858 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input5 | Inverter | inverter019_MODBUS.HR5133_m5_idc_A | Current DC Input# | 859 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC input 5 | Inverter | inverter019_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 860 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current DC Input6 | Inverter | inverter019_MODBUS.HR5165_m6_idc_A | Current DC Input# | 861 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC input 6 | Inverter | inverter019_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 862 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current-AC | Inverter | inverter019_MODBUS.HR1007_i3Avg_A | Current-AC | 863 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Current-DC | Inverter | inverter019_MODBUS.HR1062_idcInput_A | Current-DC | 864 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Daily Energy Delivered | Inverter | inverter019_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 865 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power Set Point | Inverter | inverter019_MODBUS.HR0553_pRef | Real Power Set Point | 866 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Reactive Power Set Point | Inverter | inverter019_MODBUS.HR0558_qRef | Reactive Power Set Point | 867 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Frequency | Inverter | inverter019_MODBUS.HR1012_f3_Hz | Frequency | 868 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV019 | Dagget 3_SUB1_INV019_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Insulation Resistance | Inverter | inverter019_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 869 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Number of DU Channels | Inverter | inverter019_MODBUS.HR0653_duChannels | Number of DU Channels | 870 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Number of Running Modules | Inverter | inverter019_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 871 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Operating State | Inverter | inverter019_MODBUS.HR1123_currentStatus | Operating State | 872 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Power Factor | Inverter | inverter019_MODBUS.HR1011_pf3 | Power Factor | 873 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV019 | Dagget 3_SUB1_INV019_Ramp Down | Inverter | inverter019_MODBUS.HR0286_dropGradient_p | Ramp Down | 874 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Ramp Up | Inverter | inverter019_MODBUS.HR0282_riseGradient_p | Ramp Up | 875 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power Delivered | Inverter | inverter019_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 876 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Reactive Power Delivered | Inverter | inverter019_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 877 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power | 878 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Reactive Power | Inverter | inverter019_MODBUS.HR1009_q3_kvar | Reactive Power | 879 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Reactive Power Mode | Inverter | inverter019_MODBUS.HR0552_qControlMode | Reactive Power Mode | 880 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Reactive Power Set Point Percent | Inverter | inverter019_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 881 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power AC Percent | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power AC Percent | 882 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power-AC | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power-AC | 883 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power-DC | Inverter | inverter019_MODBUS.HR1061_pdcInput_W | Real Power-DC | 884 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Air Intake | Inverter | inverter019_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 885 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Cabinet | Inverter | inverter019_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 886 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-IGBT | Inverter | inverter019_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 887 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Temperature-Module | Inverter | inverter019_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 888 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage A-B | Inverter | inverter019_MODBUS.HR1009_vRS_V | Voltage A-B | 889 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage B-C | Inverter | inverter019_MODBUS.HR1002_vST_V | Voltage B-C | 890 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage C-A | Inverter | inverter019_MODBUS.HR1003_vTR_V | Voltage C-A | 891 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Voltage DC | Inverter | inverter019_MODBUS.HR1051_vdcBus_V | Voltage DC | 892 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV020 | Dagget 3_SUB1_INV020_A Phase Current | Inverter | inverter020_MODBUS.HR1004_i1_A | A Phase Current | 893 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_B Phase Current | Inverter | inverter020_MODBUS.HR1005_i2_A | B Phase Current | 894 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_C Phase Current | Inverter | inverter020_MODBUS.HR1006_i3_A | C Phase Current | 895 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Bus Voltage | Inverter | inverter020_MODBUS.HR1051_vdcBus_V | Bus Voltage | 896 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV020 | Dagget 3_SUB1_INV020_Apparent Power | Inverter | inverter020_MODBUS.HR1010_s3_VA | Apparent Power | 897 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input1 | Inverter | inverter020_MODBUS.HR5005_m1_idc_A | Current DC Input# | 898 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC Input 1 | Inverter | inverter020_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 899 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input2 | Inverter | inverter020_MODBUS.HR5037_m2_idc_A | Current DC Input# | 900 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC input 2 | Inverter | inverter020_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 901 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input3 | Inverter | inverter020_MODBUS.HR5069_m3_idc_A | Current DC Input# | 902 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC input 3 | Inverter | inverter020_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 903 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input4 | Inverter | inverter020_MODBUS.HR5101_m4_idc_A | Current DC Input# | 904 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC input 4 | Inverter | inverter020_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 905 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input5 | Inverter | inverter020_MODBUS.HR5133_m5_idc_A | Current DC Input# | 906 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC input 5 | Inverter | inverter020_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 907 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current DC Input6 | Inverter | inverter020_MODBUS.HR5165_m6_idc_A | Current DC Input# | 908 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC input 6 | Inverter | inverter020_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 909 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current-AC | Inverter | inverter020_MODBUS.HR1007_i3Avg_A | Current-AC | 910 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Current-DC | Inverter | inverter020_MODBUS.HR1062_idcInput_A | Current-DC | 911 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Daily Energy Delivered | Inverter | inverter020_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 912 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power Set Point | Inverter | inverter020_MODBUS.HR0553_pRef | Real Power Set Point | 913 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Reactive Power Set Point | Inverter | inverter020_MODBUS.HR0558_qRef | Reactive Power Set Point | 914 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Frequency | Inverter | inverter020_MODBUS.HR1012_f3_Hz | Frequency | 915 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV020 | Dagget 3_SUB1_INV020_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Insulation Resistance | Inverter | inverter020_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 916 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Number of DU Channels | Inverter | inverter020_MODBUS.HR0653_duChannels | Number of DU Channels | 917 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Number of Running Modules | Inverter | inverter020_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 918 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Operating State | Inverter | inverter020_MODBUS.HR1123_currentStatus | Operating State | 919 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Power Factor | Inverter | inverter020_MODBUS.HR1011_pf3 | Power Factor | 920 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV020 | Dagget 3_SUB1_INV020_Ramp Down | Inverter | inverter020_MODBUS.HR0286_dropGradient_p | Ramp Down | 921 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Ramp Up | Inverter | inverter020_MODBUS.HR0282_riseGradient_p | Ramp Up | 922 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power Delivered | Inverter | inverter020_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 923 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Reactive Power Delivered | Inverter | inverter020_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 924 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power | 925 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Reactive Power | Inverter | inverter020_MODBUS.HR1009_q3_kvar | Reactive Power | 926 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Reactive Power Mode | Inverter | inverter020_MODBUS.HR0552_qControlMode | Reactive Power Mode | 927 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Reactive Power Set Point Percent | Inverter | inverter020_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 928 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power AC Percent | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power AC Percent | 929 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power-AC | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power-AC | 930 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power-DC | Inverter | inverter020_MODBUS.HR1061_pdcInput_W | Real Power-DC | 931 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Air Intake | Inverter | inverter020_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 932 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Cabinet | Inverter | inverter020_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 933 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-IGBT | Inverter | inverter020_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 934 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Temperature-Module | Inverter | inverter020_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 935 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage A-B | Inverter | inverter020_MODBUS.HR1010_vRS_V | Voltage A-B | 936 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage B-C | Inverter | inverter020_MODBUS.HR1002_vST_V | Voltage B-C | 937 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage C-A | Inverter | inverter020_MODBUS.HR1003_vTR_V | Voltage C-A | 938 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Voltage DC | Inverter | inverter020_MODBUS.HR1051_vdcBus_V | Voltage DC | 939 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV021 | Dagget 3_SUB1_INV021_A Phase Current | Inverter | inverter021_MODBUS.HR1004_i1_A | A Phase Current | 940 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_B Phase Current | Inverter | inverter021_MODBUS.HR1005_i2_A | B Phase Current | 941 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_C Phase Current | Inverter | inverter021_MODBUS.HR1006_i3_A | C Phase Current | 942 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Bus Voltage | Inverter | inverter021_MODBUS.HR1051_vdcBus_V | Bus Voltage | 943 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV021 | Dagget 3_SUB1_INV021_Apparent Power | Inverter | inverter021_MODBUS.HR1010_s3_VA | Apparent Power | 944 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input1 | Inverter | inverter021_MODBUS.HR5005_m1_idc_A | Current DC Input# | 945 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC Input 1 | Inverter | inverter021_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 946 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input2 | Inverter | inverter021_MODBUS.HR5037_m2_idc_A | Current DC Input# | 947 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC input 2 | Inverter | inverter021_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 948 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input3 | Inverter | inverter021_MODBUS.HR5069_m3_idc_A | Current DC Input# | 949 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC input 3 | Inverter | inverter021_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 950 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input4 | Inverter | inverter021_MODBUS.HR5101_m4_idc_A | Current DC Input# | 951 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC input 4 | Inverter | inverter021_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 952 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input5 | Inverter | inverter021_MODBUS.HR5133_m5_idc_A | Current DC Input# | 953 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC input 5 | Inverter | inverter021_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 954 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current DC Input6 | Inverter | inverter021_MODBUS.HR5165_m6_idc_A | Current DC Input# | 955 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC input 6 | Inverter | inverter021_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 956 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current-AC | Inverter | inverter021_MODBUS.HR1007_i3Avg_A | Current-AC | 957 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Current-DC | Inverter | inverter021_MODBUS.HR1062_idcInput_A | Current-DC | 958 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Daily Energy Delivered | Inverter | inverter021_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 959 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power Set Point | Inverter | inverter021_MODBUS.HR0553_pRef | Real Power Set Point | 960 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Reactive Power Set Point | Inverter | inverter021_MODBUS.HR0558_qRef | Reactive Power Set Point | 961 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Frequency | Inverter | inverter021_MODBUS.HR1012_f3_Hz | Frequency | 962 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV021 | Dagget 3_SUB1_INV021_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Insulation Resistance | Inverter | inverter021_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 963 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Number of DU Channels | Inverter | inverter021_MODBUS.HR0653_duChannels | Number of DU Channels | 964 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Number of Running Modules | Inverter | inverter021_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 965 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Operating State | Inverter | inverter021_MODBUS.HR1123_currentStatus | Operating State | 966 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Power Factor | Inverter | inverter021_MODBUS.HR1011_pf3 | Power Factor | 967 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV021 | Dagget 3_SUB1_INV021_Ramp Down | Inverter | inverter021_MODBUS.HR0286_dropGradient_p | Ramp Down | 968 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Ramp Up | Inverter | inverter021_MODBUS.HR0282_riseGradient_p | Ramp Up | 969 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power Delivered | Inverter | inverter021_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 970 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Reactive Power Delivered | Inverter | inverter021_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 971 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power | 972 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Reactive Power | Inverter | inverter021_MODBUS.HR1009_q3_kvar | Reactive Power | 973 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Reactive Power Mode | Inverter | inverter021_MODBUS.HR0552_qControlMode | Reactive Power Mode | 974 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Reactive Power Set Point Percent | Inverter | inverter021_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 975 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power AC Percent | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power AC Percent | 976 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power-AC | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power-AC | 977 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power-DC | Inverter | inverter021_MODBUS.HR1061_pdcInput_W | Real Power-DC | 978 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Air Intake | Inverter | inverter021_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 979 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Cabinet | Inverter | inverter021_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 980 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-IGBT | Inverter | inverter021_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 981 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Temperature-Module | Inverter | inverter021_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 982 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage A-B | Inverter | inverter021_MODBUS.HR1001_vRS_V | Voltage A-B | 983 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage B-C | Inverter | inverter021_MODBUS.HR1002_vST_V | Voltage B-C | 984 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage C-A | Inverter | inverter021_MODBUS.HR1003_vTR_V | Voltage C-A | 985 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Voltage DC | Inverter | inverter021_MODBUS.HR1051_vdcBus_V | Voltage DC | 986 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV022 | Dagget 3_SUB1_INV022_A Phase Current | Inverter | inverter022_MODBUS.HR1004_i1_A | A Phase Current | 987 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_B Phase Current | Inverter | inverter022_MODBUS.HR1005_i2_A | B Phase Current | 988 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_C Phase Current | Inverter | inverter022_MODBUS.HR1006_i3_A | C Phase Current | 989 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Bus Voltage | Inverter | inverter022_MODBUS.HR1051_vdcBus_V | Bus Voltage | 990 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV022 | Dagget 3_SUB1_INV022_Apparent Power | Inverter | inverter022_MODBUS.HR1010_s3_VA | Apparent Power | 991 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input1 | Inverter | inverter022_MODBUS.HR5005_m1_idc_A | Current DC Input# | 992 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC Input 1 | Inverter | inverter022_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 993 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input2 | Inverter | inverter022_MODBUS.HR5037_m2_idc_A | Current DC Input# | 994 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC input 2 | Inverter | inverter022_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 995 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input3 | Inverter | inverter022_MODBUS.HR5069_m3_idc_A | Current DC Input# | 996 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC input 3 | Inverter | inverter022_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 997 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input4 | Inverter | inverter022_MODBUS.HR5101_m4_idc_A | Current DC Input# | 998 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC input 4 | Inverter | inverter022_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 999 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input5 | Inverter | inverter022_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1000 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC input 5 | Inverter | inverter022_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1001 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current DC Input6 | Inverter | inverter022_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1002 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC input 6 | Inverter | inverter022_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1003 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current-AC | Inverter | inverter022_MODBUS.HR1007_i3Avg_A | Current-AC | 1004 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Current-DC | Inverter | inverter022_MODBUS.HR1062_idcInput_A | Current-DC | 1005 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Daily Energy Delivered | Inverter | inverter022_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1006 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power Set Point | Inverter | inverter022_MODBUS.HR0553_pRef | Real Power Set Point | 1007 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Reactive Power Set Point | Inverter | inverter022_MODBUS.HR0558_qRef | Reactive Power Set Point | 1008 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Frequency | Inverter | inverter022_MODBUS.HR1012_f3_Hz | Frequency | 1009 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV022 | Dagget 3_SUB1_INV022_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Insulation Resistance | Inverter | inverter022_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1010 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Number of DU Channels | Inverter | inverter022_MODBUS.HR0653_duChannels | Number of DU Channels | 1011 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Number of Running Modules | Inverter | inverter022_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1012 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Operating State | Inverter | inverter022_MODBUS.HR1123_currentStatus | Operating State | 1013 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Power Factor | Inverter | inverter022_MODBUS.HR1011_pf3 | Power Factor | 1014 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV022 | Dagget 3_SUB1_INV022_Ramp Down | Inverter | inverter022_MODBUS.HR0286_dropGradient_p | Ramp Down | 1015 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Ramp Up | Inverter | inverter022_MODBUS.HR0282_riseGradient_p | Ramp Up | 1016 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power Delivered | Inverter | inverter022_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1017 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Reactive Power Delivered | Inverter | inverter022_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1018 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power | 1019 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Reactive Power | Inverter | inverter022_MODBUS.HR1009_q3_kvar | Reactive Power | 1020 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Reactive Power Mode | Inverter | inverter022_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1021 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Reactive Power Set Point Percent | Inverter | inverter022_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1022 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power AC Percent | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1023 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power-AC | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power-AC | 1024 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power-DC | Inverter | inverter022_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1025 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Air Intake | Inverter | inverter022_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1026 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Cabinet | Inverter | inverter022_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1027 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-IGBT | Inverter | inverter022_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1028 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Temperature-Module | Inverter | inverter022_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1029 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage A-B | Inverter | inverter022_MODBUS.HR1002_vRS_V | Voltage A-B | 1030 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage B-C | Inverter | inverter022_MODBUS.HR1002_vST_V | Voltage B-C | 1031 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage C-A | Inverter | inverter022_MODBUS.HR1003_vTR_V | Voltage C-A | 1032 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Voltage DC | Inverter | inverter022_MODBUS.HR1051_vdcBus_V | Voltage DC | 1033 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV023 | Dagget 3_SUB1_INV023_A Phase Current | Inverter | inverter023_MODBUS.HR1004_i1_A | A Phase Current | 1034 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_B Phase Current | Inverter | inverter023_MODBUS.HR1005_i2_A | B Phase Current | 1035 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_C Phase Current | Inverter | inverter023_MODBUS.HR1006_i3_A | C Phase Current | 1036 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Bus Voltage | Inverter | inverter023_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1037 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV023 | Dagget 3_SUB1_INV023_Apparent Power | Inverter | inverter023_MODBUS.HR1010_s3_VA | Apparent Power | 1038 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input1 | Inverter | inverter023_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1039 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC Input 1 | Inverter | inverter023_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1040 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input2 | Inverter | inverter023_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1041 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC input 2 | Inverter | inverter023_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1042 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input3 | Inverter | inverter023_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1043 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC input 3 | Inverter | inverter023_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1044 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input4 | Inverter | inverter023_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1045 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC input 4 | Inverter | inverter023_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1046 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input5 | Inverter | inverter023_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1047 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC input 5 | Inverter | inverter023_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1048 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current DC Input6 | Inverter | inverter023_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1049 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC input 6 | Inverter | inverter023_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1050 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current-AC | Inverter | inverter023_MODBUS.HR1007_i3Avg_A | Current-AC | 1051 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Current-DC | Inverter | inverter023_MODBUS.HR1062_idcInput_A | Current-DC | 1052 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Daily Energy Delivered | Inverter | inverter023_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1053 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power Set Point | Inverter | inverter023_MODBUS.HR0553_pRef | Real Power Set Point | 1054 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Reactive Power Set Point | Inverter | inverter023_MODBUS.HR0558_qRef | Reactive Power Set Point | 1055 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Frequency | Inverter | inverter023_MODBUS.HR1012_f3_Hz | Frequency | 1056 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV023 | Dagget 3_SUB1_INV023_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Insulation Resistance | Inverter | inverter023_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1057 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Number of DU Channels | Inverter | inverter023_MODBUS.HR0653_duChannels | Number of DU Channels | 1058 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Number of Running Modules | Inverter | inverter023_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1059 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Operating State | Inverter | inverter023_MODBUS.HR1123_currentStatus | Operating State | 1060 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Power Factor | Inverter | inverter023_MODBUS.HR1011_pf3 | Power Factor | 1061 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV023 | Dagget 3_SUB1_INV023_Ramp Down | Inverter | inverter023_MODBUS.HR0286_dropGradient_p | Ramp Down | 1062 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Ramp Up | Inverter | inverter023_MODBUS.HR0282_riseGradient_p | Ramp Up | 1063 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power Delivered | Inverter | inverter023_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1064 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Reactive Power Delivered | Inverter | inverter023_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1065 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power | 1066 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Reactive Power | Inverter | inverter023_MODBUS.HR1009_q3_kvar | Reactive Power | 1067 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Reactive Power Mode | Inverter | inverter023_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1068 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Reactive Power Set Point Percent | Inverter | inverter023_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1069 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power AC Percent | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1070 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power-AC | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power-AC | 1071 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power-DC | Inverter | inverter023_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1072 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Air Intake | Inverter | inverter023_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1073 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Cabinet | Inverter | inverter023_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1074 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-IGBT | Inverter | inverter023_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1075 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Temperature-Module | Inverter | inverter023_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1076 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage A-B | Inverter | inverter023_MODBUS.HR1003_vRS_V | Voltage A-B | 1077 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage B-C | Inverter | inverter023_MODBUS.HR1002_vST_V | Voltage B-C | 1078 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage C-A | Inverter | inverter023_MODBUS.HR1003_vTR_V | Voltage C-A | 1079 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Voltage DC | Inverter | inverter023_MODBUS.HR1051_vdcBus_V | Voltage DC | 1080 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV024 | Dagget 3_SUB1_INV024_A Phase Current | Inverter | inverter024_MODBUS.HR1004_i1_A | A Phase Current | 1081 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_B Phase Current | Inverter | inverter024_MODBUS.HR1005_i2_A | B Phase Current | 1082 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_C Phase Current | Inverter | inverter024_MODBUS.HR1006_i3_A | C Phase Current | 1083 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Bus Voltage | Inverter | inverter024_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1084 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV024 | Dagget 3_SUB1_INV024_Apparent Power | Inverter | inverter024_MODBUS.HR1010_s3_VA | Apparent Power | 1085 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input1 | Inverter | inverter024_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1086 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC Input 1 | Inverter | inverter024_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1087 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input2 | Inverter | inverter024_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1088 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC input 2 | Inverter | inverter024_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1089 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input3 | Inverter | inverter024_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1090 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC input 3 | Inverter | inverter024_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1091 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input4 | Inverter | inverter024_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1092 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC input 4 | Inverter | inverter024_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1093 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input5 | Inverter | inverter024_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1094 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC input 5 | Inverter | inverter024_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1095 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current DC Input6 | Inverter | inverter024_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1096 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC input 6 | Inverter | inverter024_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1097 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current-AC | Inverter | inverter024_MODBUS.HR1007_i3Avg_A | Current-AC | 1098 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Current-DC | Inverter | inverter024_MODBUS.HR1062_idcInput_A | Current-DC | 1099 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Daily Energy Delivered | Inverter | inverter024_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1100 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power Set Point | Inverter | inverter024_MODBUS.HR0553_pRef | Real Power Set Point | 1101 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Reactive Power Set Point | Inverter | inverter024_MODBUS.HR0558_qRef | Reactive Power Set Point | 1102 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Frequency | Inverter | inverter024_MODBUS.HR1012_f3_Hz | Frequency | 1103 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV024 | Dagget 3_SUB1_INV024_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Insulation Resistance | Inverter | inverter024_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1104 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Number of DU Channels | Inverter | inverter024_MODBUS.HR0653_duChannels | Number of DU Channels | 1105 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Number of Running Modules | Inverter | inverter024_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1106 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Operating State | Inverter | inverter024_MODBUS.HR1123_currentStatus | Operating State | 1107 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Power Factor | Inverter | inverter024_MODBUS.HR1011_pf3 | Power Factor | 1108 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV024 | Dagget 3_SUB1_INV024_Ramp Down | Inverter | inverter024_MODBUS.HR0286_dropGradient_p | Ramp Down | 1109 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Ramp Up | Inverter | inverter024_MODBUS.HR0282_riseGradient_p | Ramp Up | 1110 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power Delivered | Inverter | inverter024_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1111 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Reactive Power Delivered | Inverter | inverter024_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1112 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power | 1113 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Reactive Power | Inverter | inverter024_MODBUS.HR1009_q3_kvar | Reactive Power | 1114 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Reactive Power Mode | Inverter | inverter024_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1115 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Reactive Power Set Point Percent | Inverter | inverter024_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1116 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power AC Percent | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1117 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power-AC | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power-AC | 1118 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power-DC | Inverter | inverter024_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1119 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Air Intake | Inverter | inverter024_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1120 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Cabinet | Inverter | inverter024_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1121 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-IGBT | Inverter | inverter024_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1122 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Temperature-Module | Inverter | inverter024_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1123 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage A-B | Inverter | inverter024_MODBUS.HR1004_vRS_V | Voltage A-B | 1124 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage B-C | Inverter | inverter024_MODBUS.HR1002_vST_V | Voltage B-C | 1125 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage C-A | Inverter | inverter024_MODBUS.HR1003_vTR_V | Voltage C-A | 1126 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Voltage DC | Inverter | inverter024_MODBUS.HR1051_vdcBus_V | Voltage DC | 1127 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV025 | Dagget 3_SUB1_INV025_A Phase Current | Inverter | inverter025_MODBUS.HR1004_i1_A | A Phase Current | 1128 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_B Phase Current | Inverter | inverter025_MODBUS.HR1005_i2_A | B Phase Current | 1129 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_C Phase Current | Inverter | inverter025_MODBUS.HR1006_i3_A | C Phase Current | 1130 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Bus Voltage | Inverter | inverter025_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1131 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV025 | Dagget 3_SUB1_INV025_Apparent Power | Inverter | inverter025_MODBUS.HR1010_s3_VA | Apparent Power | 1132 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input1 | Inverter | inverter025_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1133 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC Input 1 | Inverter | inverter025_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1134 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input2 | Inverter | inverter025_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1135 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC input 2 | Inverter | inverter025_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1136 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input3 | Inverter | inverter025_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1137 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC input 3 | Inverter | inverter025_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1138 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input4 | Inverter | inverter025_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1139 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC input 4 | Inverter | inverter025_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1140 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input5 | Inverter | inverter025_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1141 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC input 5 | Inverter | inverter025_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1142 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current DC Input6 | Inverter | inverter025_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1143 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC input 6 | Inverter | inverter025_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1144 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current-AC | Inverter | inverter025_MODBUS.HR1007_i3Avg_A | Current-AC | 1145 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Current-DC | Inverter | inverter025_MODBUS.HR1062_idcInput_A | Current-DC | 1146 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Daily Energy Delivered | Inverter | inverter025_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1147 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power Set Point | Inverter | inverter025_MODBUS.HR0553_pRef | Real Power Set Point | 1148 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Reactive Power Set Point | Inverter | inverter025_MODBUS.HR0558_qRef | Reactive Power Set Point | 1149 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Frequency | Inverter | inverter025_MODBUS.HR1012_f3_Hz | Frequency | 1150 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV025 | Dagget 3_SUB1_INV025_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Insulation Resistance | Inverter | inverter025_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1151 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Number of DU Channels | Inverter | inverter025_MODBUS.HR0653_duChannels | Number of DU Channels | 1152 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Number of Running Modules | Inverter | inverter025_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1153 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Operating State | Inverter | inverter025_MODBUS.HR1123_currentStatus | Operating State | 1154 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Power Factor | Inverter | inverter025_MODBUS.HR1011_pf3 | Power Factor | 1155 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV025 | Dagget 3_SUB1_INV025_Ramp Down | Inverter | inverter025_MODBUS.HR0286_dropGradient_p | Ramp Down | 1156 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Ramp Up | Inverter | inverter025_MODBUS.HR0282_riseGradient_p | Ramp Up | 1157 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power Delivered | Inverter | inverter025_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1158 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Reactive Power Delivered | Inverter | inverter025_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1159 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power | 1160 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Reactive Power | Inverter | inverter025_MODBUS.HR1009_q3_kvar | Reactive Power | 1161 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Reactive Power Mode | Inverter | inverter025_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1162 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Reactive Power Set Point Percent | Inverter | inverter025_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1163 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power AC Percent | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1164 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power-AC | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power-AC | 1165 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power-DC | Inverter | inverter025_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1166 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Air Intake | Inverter | inverter025_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1167 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Cabinet | Inverter | inverter025_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1168 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-IGBT | Inverter | inverter025_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1169 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Temperature-Module | Inverter | inverter025_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1170 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage A-B | Inverter | inverter025_MODBUS.HR1005_vRS_V | Voltage A-B | 1171 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage B-C | Inverter | inverter025_MODBUS.HR1002_vST_V | Voltage B-C | 1172 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage C-A | Inverter | inverter025_MODBUS.HR1003_vTR_V | Voltage C-A | 1173 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Voltage DC | Inverter | inverter025_MODBUS.HR1051_vdcBus_V | Voltage DC | 1174 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV026 | Dagget 3_SUB1_INV026_A Phase Current | Inverter | inverter026_MODBUS.HR1004_i1_A | A Phase Current | 1175 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_B Phase Current | Inverter | inverter026_MODBUS.HR1005_i2_A | B Phase Current | 1176 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_C Phase Current | Inverter | inverter026_MODBUS.HR1006_i3_A | C Phase Current | 1177 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Bus Voltage | Inverter | inverter026_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1178 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV026 | Dagget 3_SUB1_INV026_Apparent Power | Inverter | inverter026_MODBUS.HR1010_s3_VA | Apparent Power | 1179 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input1 | Inverter | inverter026_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1180 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC Input 1 | Inverter | inverter026_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1181 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input2 | Inverter | inverter026_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1182 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC input 2 | Inverter | inverter026_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1183 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input3 | Inverter | inverter026_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1184 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC input 3 | Inverter | inverter026_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1185 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input4 | Inverter | inverter026_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1186 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC input 4 | Inverter | inverter026_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1187 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input5 | Inverter | inverter026_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1188 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC input 5 | Inverter | inverter026_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1189 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current DC Input6 | Inverter | inverter026_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1190 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC input 6 | Inverter | inverter026_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1191 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current-AC | Inverter | inverter026_MODBUS.HR1007_i3Avg_A | Current-AC | 1192 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Current-DC | Inverter | inverter026_MODBUS.HR1062_idcInput_A | Current-DC | 1193 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Daily Energy Delivered | Inverter | inverter026_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1194 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power Set Point | Inverter | inverter026_MODBUS.HR0553_pRef | Real Power Set Point | 1195 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Reactive Power Set Point | Inverter | inverter026_MODBUS.HR0558_qRef | Reactive Power Set Point | 1196 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Frequency | Inverter | inverter026_MODBUS.HR1012_f3_Hz | Frequency | 1197 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV026 | Dagget 3_SUB1_INV026_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Insulation Resistance | Inverter | inverter026_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1198 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Number of DU Channels | Inverter | inverter026_MODBUS.HR0653_duChannels | Number of DU Channels | 1199 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Number of Running Modules | Inverter | inverter026_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1200 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Operating State | Inverter | inverter026_MODBUS.HR1123_currentStatus | Operating State | 1201 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Power Factor | Inverter | inverter026_MODBUS.HR1011_pf3 | Power Factor | 1202 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV026 | Dagget 3_SUB1_INV026_Ramp Down | Inverter | inverter026_MODBUS.HR0286_dropGradient_p | Ramp Down | 1203 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Ramp Up | Inverter | inverter026_MODBUS.HR0282_riseGradient_p | Ramp Up | 1204 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power Delivered | Inverter | inverter026_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1205 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Reactive Power Delivered | Inverter | inverter026_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1206 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power | 1207 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Reactive Power | Inverter | inverter026_MODBUS.HR1009_q3_kvar | Reactive Power | 1208 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Reactive Power Mode | Inverter | inverter026_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1209 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Reactive Power Set Point Percent | Inverter | inverter026_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1210 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power AC Percent | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1211 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power-AC | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power-AC | 1212 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power-DC | Inverter | inverter026_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1213 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Air Intake | Inverter | inverter026_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1214 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Cabinet | Inverter | inverter026_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1215 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-IGBT | Inverter | inverter026_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1216 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Temperature-Module | Inverter | inverter026_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1217 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage A-B | Inverter | inverter026_MODBUS.HR1006_vRS_V | Voltage A-B | 1218 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage B-C | Inverter | inverter026_MODBUS.HR1002_vST_V | Voltage B-C | 1219 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage C-A | Inverter | inverter026_MODBUS.HR1003_vTR_V | Voltage C-A | 1220 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Voltage DC | Inverter | inverter026_MODBUS.HR1051_vdcBus_V | Voltage DC | 1221 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV027 | Dagget 3_SUB1_INV027_A Phase Current | Inverter | inverter027_MODBUS.HR1004_i1_A | A Phase Current | 1222 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_B Phase Current | Inverter | inverter027_MODBUS.HR1005_i2_A | B Phase Current | 1223 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_C Phase Current | Inverter | inverter027_MODBUS.HR1006_i3_A | C Phase Current | 1224 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Bus Voltage | Inverter | inverter027_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1225 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV027 | Dagget 3_SUB1_INV027_Apparent Power | Inverter | inverter027_MODBUS.HR1010_s3_VA | Apparent Power | 1226 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input1 | Inverter | inverter027_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1227 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC Input 1 | Inverter | inverter027_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1228 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input2 | Inverter | inverter027_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1229 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC input 2 | Inverter | inverter027_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1230 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input3 | Inverter | inverter027_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1231 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC input 3 | Inverter | inverter027_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1232 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input4 | Inverter | inverter027_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1233 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC input 4 | Inverter | inverter027_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1234 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input5 | Inverter | inverter027_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1235 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC input 5 | Inverter | inverter027_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1236 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current DC Input6 | Inverter | inverter027_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1237 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC input 6 | Inverter | inverter027_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1238 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current-AC | Inverter | inverter027_MODBUS.HR1007_i3Avg_A | Current-AC | 1239 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Current-DC | Inverter | inverter027_MODBUS.HR1062_idcInput_A | Current-DC | 1240 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Daily Energy Delivered | Inverter | inverter027_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1241 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power Set Point | Inverter | inverter027_MODBUS.HR0553_pRef | Real Power Set Point | 1242 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Reactive Power Set Point | Inverter | inverter027_MODBUS.HR0558_qRef | Reactive Power Set Point | 1243 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Frequency | Inverter | inverter027_MODBUS.HR1012_f3_Hz | Frequency | 1244 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV027 | Dagget 3_SUB1_INV027_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Insulation Resistance | Inverter | inverter027_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1245 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Number of DU Channels | Inverter | inverter027_MODBUS.HR0653_duChannels | Number of DU Channels | 1246 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Number of Running Modules | Inverter | inverter027_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1247 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Operating State | Inverter | inverter027_MODBUS.HR1123_currentStatus | Operating State | 1248 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Power Factor | Inverter | inverter027_MODBUS.HR1011_pf3 | Power Factor | 1249 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV027 | Dagget 3_SUB1_INV027_Ramp Down | Inverter | inverter027_MODBUS.HR0286_dropGradient_p | Ramp Down | 1250 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Ramp Up | Inverter | inverter027_MODBUS.HR0282_riseGradient_p | Ramp Up | 1251 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power Delivered | Inverter | inverter027_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1252 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Reactive Power Delivered | Inverter | inverter027_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1253 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power | 1254 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Reactive Power | Inverter | inverter027_MODBUS.HR1009_q3_kvar | Reactive Power | 1255 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Reactive Power Mode | Inverter | inverter027_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1256 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Reactive Power Set Point Percent | Inverter | inverter027_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1257 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power AC Percent | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1258 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power-AC | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power-AC | 1259 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power-DC | Inverter | inverter027_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1260 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Air Intake | Inverter | inverter027_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1261 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Cabinet | Inverter | inverter027_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1262 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-IGBT | Inverter | inverter027_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1263 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Temperature-Module | Inverter | inverter027_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1264 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage A-B | Inverter | inverter027_MODBUS.HR1007_vRS_V | Voltage A-B | 1265 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage B-C | Inverter | inverter027_MODBUS.HR1002_vST_V | Voltage B-C | 1266 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage C-A | Inverter | inverter027_MODBUS.HR1003_vTR_V | Voltage C-A | 1267 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Voltage DC | Inverter | inverter027_MODBUS.HR1051_vdcBus_V | Voltage DC | 1268 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV028 | Dagget 3_SUB1_INV028_A Phase Current | Inverter | inverter028_MODBUS.HR1004_i1_A | A Phase Current | 1269 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_B Phase Current | Inverter | inverter028_MODBUS.HR1005_i2_A | B Phase Current | 1270 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_C Phase Current | Inverter | inverter028_MODBUS.HR1006_i3_A | C Phase Current | 1271 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Bus Voltage | Inverter | inverter028_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1272 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV028 | Dagget 3_SUB1_INV028_Apparent Power | Inverter | inverter028_MODBUS.HR1010_s3_VA | Apparent Power | 1273 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input1 | Inverter | inverter028_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1274 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC Input 1 | Inverter | inverter028_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1275 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input2 | Inverter | inverter028_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1276 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC input 2 | Inverter | inverter028_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1277 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input3 | Inverter | inverter028_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1278 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC input 3 | Inverter | inverter028_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1279 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input4 | Inverter | inverter028_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1280 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC input 4 | Inverter | inverter028_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1281 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input5 | Inverter | inverter028_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1282 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC input 5 | Inverter | inverter028_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1283 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current DC Input6 | Inverter | inverter028_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1284 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC input 6 | Inverter | inverter028_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1285 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current-AC | Inverter | inverter028_MODBUS.HR1007_i3Avg_A | Current-AC | 1286 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Current-DC | Inverter | inverter028_MODBUS.HR1062_idcInput_A | Current-DC | 1287 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Daily Energy Delivered | Inverter | inverter028_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1288 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power Set Point | Inverter | inverter028_MODBUS.HR0553_pRef | Real Power Set Point | 1289 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Reactive Power Set Point | Inverter | inverter028_MODBUS.HR0558_qRef | Reactive Power Set Point | 1290 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Frequency | Inverter | inverter028_MODBUS.HR1012_f3_Hz | Frequency | 1291 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV028 | Dagget 3_SUB1_INV028_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Insulation Resistance | Inverter | inverter028_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1292 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Number of DU Channels | Inverter | inverter028_MODBUS.HR0653_duChannels | Number of DU Channels | 1293 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Number of Running Modules | Inverter | inverter028_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1294 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Operating State | Inverter | inverter028_MODBUS.HR1123_currentStatus | Operating State | 1295 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Power Factor | Inverter | inverter028_MODBUS.HR1011_pf3 | Power Factor | 1296 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV028 | Dagget 3_SUB1_INV028_Ramp Down | Inverter | inverter028_MODBUS.HR0286_dropGradient_p | Ramp Down | 1297 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Ramp Up | Inverter | inverter028_MODBUS.HR0282_riseGradient_p | Ramp Up | 1298 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power Delivered | Inverter | inverter028_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1299 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Reactive Power Delivered | Inverter | inverter028_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1300 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power | 1301 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Reactive Power | Inverter | inverter028_MODBUS.HR1009_q3_kvar | Reactive Power | 1302 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Reactive Power Mode | Inverter | inverter028_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1303 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Reactive Power Set Point Percent | Inverter | inverter028_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1304 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power AC Percent | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1305 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power-AC | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power-AC | 1306 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power-DC | Inverter | inverter028_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1307 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Air Intake | Inverter | inverter028_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1308 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Cabinet | Inverter | inverter028_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1309 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-IGBT | Inverter | inverter028_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1310 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Temperature-Module | Inverter | inverter028_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1311 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage A-B | Inverter | inverter028_MODBUS.HR1008_vRS_V | Voltage A-B | 1312 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage B-C | Inverter | inverter028_MODBUS.HR1002_vST_V | Voltage B-C | 1313 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage C-A | Inverter | inverter028_MODBUS.HR1003_vTR_V | Voltage C-A | 1314 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Voltage DC | Inverter | inverter028_MODBUS.HR1051_vdcBus_V | Voltage DC | 1315 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV029 | Dagget 3_SUB1_INV029_A Phase Current | Inverter | inverter029_MODBUS.HR1004_i1_A | A Phase Current | 1316 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_B Phase Current | Inverter | inverter029_MODBUS.HR1005_i2_A | B Phase Current | 1317 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_C Phase Current | Inverter | inverter029_MODBUS.HR1006_i3_A | C Phase Current | 1318 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Bus Voltage | Inverter | inverter029_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1319 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV029 | Dagget 3_SUB1_INV029_Apparent Power | Inverter | inverter029_MODBUS.HR1010_s3_VA | Apparent Power | 1320 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input1 | Inverter | inverter029_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1321 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC Input 1 | Inverter | inverter029_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1322 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input2 | Inverter | inverter029_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1323 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC input 2 | Inverter | inverter029_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1324 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input3 | Inverter | inverter029_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1325 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC input 3 | Inverter | inverter029_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1326 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input4 | Inverter | inverter029_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1327 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC input 4 | Inverter | inverter029_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1328 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input5 | Inverter | inverter029_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1329 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC input 5 | Inverter | inverter029_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1330 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current DC Input6 | Inverter | inverter029_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1331 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC input 6 | Inverter | inverter029_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1332 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current-AC | Inverter | inverter029_MODBUS.HR1007_i3Avg_A | Current-AC | 1333 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Current-DC | Inverter | inverter029_MODBUS.HR1062_idcInput_A | Current-DC | 1334 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Daily Energy Delivered | Inverter | inverter029_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1335 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power Set Point | Inverter | inverter029_MODBUS.HR0553_pRef | Real Power Set Point | 1336 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Reactive Power Set Point | Inverter | inverter029_MODBUS.HR0558_qRef | Reactive Power Set Point | 1337 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Frequency | Inverter | inverter029_MODBUS.HR1012_f3_Hz | Frequency | 1338 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV029 | Dagget 3_SUB1_INV029_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Insulation Resistance | Inverter | inverter029_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1339 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Number of DU Channels | Inverter | inverter029_MODBUS.HR0653_duChannels | Number of DU Channels | 1340 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Number of Running Modules | Inverter | inverter029_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1341 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Operating State | Inverter | inverter029_MODBUS.HR1123_currentStatus | Operating State | 1342 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Power Factor | Inverter | inverter029_MODBUS.HR1011_pf3 | Power Factor | 1343 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV029 | Dagget 3_SUB1_INV029_Ramp Down | Inverter | inverter029_MODBUS.HR0286_dropGradient_p | Ramp Down | 1344 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Ramp Up | Inverter | inverter029_MODBUS.HR0282_riseGradient_p | Ramp Up | 1345 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power Delivered | Inverter | inverter029_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1346 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Reactive Power Delivered | Inverter | inverter029_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1347 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power | 1348 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Reactive Power | Inverter | inverter029_MODBUS.HR1009_q3_kvar | Reactive Power | 1349 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Reactive Power Mode | Inverter | inverter029_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1350 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Reactive Power Set Point Percent | Inverter | inverter029_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1351 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power AC Percent | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1352 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power-AC | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power-AC | 1353 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power-DC | Inverter | inverter029_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1354 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Air Intake | Inverter | inverter029_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1355 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Cabinet | Inverter | inverter029_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1356 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-IGBT | Inverter | inverter029_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1357 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Temperature-Module | Inverter | inverter029_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1358 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage A-B | Inverter | inverter029_MODBUS.HR1009_vRS_V | Voltage A-B | 1359 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage B-C | Inverter | inverter029_MODBUS.HR1002_vST_V | Voltage B-C | 1360 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage C-A | Inverter | inverter029_MODBUS.HR1003_vTR_V | Voltage C-A | 1361 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Voltage DC | Inverter | inverter029_MODBUS.HR1051_vdcBus_V | Voltage DC | 1362 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV030 | Dagget 3_SUB1_INV030_A Phase Current | Inverter | inverter030_MODBUS.HR1004_i1_A | A Phase Current | 1363 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_B Phase Current | Inverter | inverter030_MODBUS.HR1005_i2_A | B Phase Current | 1364 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_C Phase Current | Inverter | inverter030_MODBUS.HR1006_i3_A | C Phase Current | 1365 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Bus Voltage | Inverter | inverter030_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1366 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV030 | Dagget 3_SUB1_INV030_Apparent Power | Inverter | inverter030_MODBUS.HR1010_s3_VA | Apparent Power | 1367 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input1 | Inverter | inverter030_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1368 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC Input 1 | Inverter | inverter030_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1369 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input2 | Inverter | inverter030_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1370 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC input 2 | Inverter | inverter030_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1371 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input3 | Inverter | inverter030_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1372 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC input 3 | Inverter | inverter030_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1373 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input4 | Inverter | inverter030_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1374 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC input 4 | Inverter | inverter030_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1375 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input5 | Inverter | inverter030_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1376 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC input 5 | Inverter | inverter030_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1377 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current DC Input6 | Inverter | inverter030_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1378 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC input 6 | Inverter | inverter030_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1379 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current-AC | Inverter | inverter030_MODBUS.HR1007_i3Avg_A | Current-AC | 1380 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Current-DC | Inverter | inverter030_MODBUS.HR1062_idcInput_A | Current-DC | 1381 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Daily Energy Delivered | Inverter | inverter030_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1382 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power Set Point | Inverter | inverter030_MODBUS.HR0553_pRef | Real Power Set Point | 1383 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Reactive Power Set Point | Inverter | inverter030_MODBUS.HR0558_qRef | Reactive Power Set Point | 1384 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Frequency | Inverter | inverter030_MODBUS.HR1012_f3_Hz | Frequency | 1385 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV030 | Dagget 3_SUB1_INV030_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Insulation Resistance | Inverter | inverter030_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1386 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Number of DU Channels | Inverter | inverter030_MODBUS.HR0653_duChannels | Number of DU Channels | 1387 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Number of Running Modules | Inverter | inverter030_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1388 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Operating State | Inverter | inverter030_MODBUS.HR1123_currentStatus | Operating State | 1389 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Power Factor | Inverter | inverter030_MODBUS.HR1011_pf3 | Power Factor | 1390 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV030 | Dagget 3_SUB1_INV030_Ramp Down | Inverter | inverter030_MODBUS.HR0286_dropGradient_p | Ramp Down | 1391 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Ramp Up | Inverter | inverter030_MODBUS.HR0282_riseGradient_p | Ramp Up | 1392 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power Delivered | Inverter | inverter030_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1393 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Reactive Power Delivered | Inverter | inverter030_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1394 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power | 1395 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Reactive Power | Inverter | inverter030_MODBUS.HR1009_q3_kvar | Reactive Power | 1396 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Reactive Power Mode | Inverter | inverter030_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1397 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Reactive Power Set Point Percent | Inverter | inverter030_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1398 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power AC Percent | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1399 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power-AC | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power-AC | 1400 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power-DC | Inverter | inverter030_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1401 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Air Intake | Inverter | inverter030_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1402 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Cabinet | Inverter | inverter030_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1403 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-IGBT | Inverter | inverter030_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1404 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Temperature-Module | Inverter | inverter030_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1405 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage A-B | Inverter | inverter030_MODBUS.HR1010_vRS_V | Voltage A-B | 1406 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage B-C | Inverter | inverter030_MODBUS.HR1002_vST_V | Voltage B-C | 1407 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage C-A | Inverter | inverter030_MODBUS.HR1003_vTR_V | Voltage C-A | 1408 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Voltage DC | Inverter | inverter030_MODBUS.HR1051_vdcBus_V | Voltage DC | 1409 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV031 | Dagget 3_SUB1_INV031_A Phase Current | Inverter | inverter031_MODBUS.HR1004_i1_A | A Phase Current | 1410 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_B Phase Current | Inverter | inverter031_MODBUS.HR1005_i2_A | B Phase Current | 1411 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_C Phase Current | Inverter | inverter031_MODBUS.HR1006_i3_A | C Phase Current | 1412 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Bus Voltage | Inverter | inverter031_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1413 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV031 | Dagget 3_SUB1_INV031_Apparent Power | Inverter | inverter031_MODBUS.HR1010_s3_VA | Apparent Power | 1414 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input1 | Inverter | inverter031_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1415 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC Input 1 | Inverter | inverter031_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1416 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input2 | Inverter | inverter031_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1417 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC input 2 | Inverter | inverter031_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1418 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input3 | Inverter | inverter031_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1419 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC input 3 | Inverter | inverter031_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1420 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input4 | Inverter | inverter031_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1421 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC input 4 | Inverter | inverter031_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1422 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input5 | Inverter | inverter031_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1423 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC input 5 | Inverter | inverter031_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1424 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current DC Input6 | Inverter | inverter031_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1425 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC input 6 | Inverter | inverter031_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1426 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current-AC | Inverter | inverter031_MODBUS.HR1007_i3Avg_A | Current-AC | 1427 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Current-DC | Inverter | inverter031_MODBUS.HR1062_idcInput_A | Current-DC | 1428 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Daily Energy Delivered | Inverter | inverter031_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1429 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power Set Point | Inverter | inverter031_MODBUS.HR0553_pRef | Real Power Set Point | 1430 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Reactive Power Set Point | Inverter | inverter031_MODBUS.HR0558_qRef | Reactive Power Set Point | 1431 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Frequency | Inverter | inverter031_MODBUS.HR1012_f3_Hz | Frequency | 1432 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV031 | Dagget 3_SUB1_INV031_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Insulation Resistance | Inverter | inverter031_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1433 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Number of DU Channels | Inverter | inverter031_MODBUS.HR0653_duChannels | Number of DU Channels | 1434 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Number of Running Modules | Inverter | inverter031_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1435 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Operating State | Inverter | inverter031_MODBUS.HR1123_currentStatus | Operating State | 1436 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Power Factor | Inverter | inverter031_MODBUS.HR1011_pf3 | Power Factor | 1437 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV031 | Dagget 3_SUB1_INV031_Ramp Down | Inverter | inverter031_MODBUS.HR0286_dropGradient_p | Ramp Down | 1438 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Ramp Up | Inverter | inverter031_MODBUS.HR0282_riseGradient_p | Ramp Up | 1439 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power Delivered | Inverter | inverter031_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1440 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Reactive Power Delivered | Inverter | inverter031_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1441 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power | 1442 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Reactive Power | Inverter | inverter031_MODBUS.HR1009_q3_kvar | Reactive Power | 1443 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Reactive Power Mode | Inverter | inverter031_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1444 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Reactive Power Set Point Percent | Inverter | inverter031_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1445 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power AC Percent | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1446 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power-AC | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power-AC | 1447 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power-DC | Inverter | inverter031_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1448 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Air Intake | Inverter | inverter031_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1449 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Cabinet | Inverter | inverter031_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1450 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-IGBT | Inverter | inverter031_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1451 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Temperature-Module | Inverter | inverter031_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1452 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage A-B | Inverter | inverter031_MODBUS.HR1001_vRS_V | Voltage A-B | 1453 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage B-C | Inverter | inverter031_MODBUS.HR1002_vST_V | Voltage B-C | 1454 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage C-A | Inverter | inverter031_MODBUS.HR1003_vTR_V | Voltage C-A | 1455 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Voltage DC | Inverter | inverter031_MODBUS.HR1051_vdcBus_V | Voltage DC | 1456 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV032 | Dagget 3_SUB1_INV032_A Phase Current | Inverter | inverter032_MODBUS.HR1004_i1_A | A Phase Current | 1457 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_B Phase Current | Inverter | inverter032_MODBUS.HR1005_i2_A | B Phase Current | 1458 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_C Phase Current | Inverter | inverter032_MODBUS.HR1006_i3_A | C Phase Current | 1459 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Bus Voltage | Inverter | inverter032_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1460 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV032 | Dagget 3_SUB1_INV032_Apparent Power | Inverter | inverter032_MODBUS.HR1010_s3_VA | Apparent Power | 1461 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input1 | Inverter | inverter032_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1462 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC Input 1 | Inverter | inverter032_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1463 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input2 | Inverter | inverter032_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1464 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC input 2 | Inverter | inverter032_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1465 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input3 | Inverter | inverter032_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1466 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC input 3 | Inverter | inverter032_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1467 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input4 | Inverter | inverter032_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1468 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC input 4 | Inverter | inverter032_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1469 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input5 | Inverter | inverter032_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1470 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC input 5 | Inverter | inverter032_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1471 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current DC Input6 | Inverter | inverter032_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1472 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC input 6 | Inverter | inverter032_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1473 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current-AC | Inverter | inverter032_MODBUS.HR1007_i3Avg_A | Current-AC | 1474 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Current-DC | Inverter | inverter032_MODBUS.HR1062_idcInput_A | Current-DC | 1475 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Daily Energy Delivered | Inverter | inverter032_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1476 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power Set Point | Inverter | inverter032_MODBUS.HR0553_pRef | Real Power Set Point | 1477 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Reactive Power Set Point | Inverter | inverter032_MODBUS.HR0558_qRef | Reactive Power Set Point | 1478 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Frequency | Inverter | inverter032_MODBUS.HR1012_f3_Hz | Frequency | 1479 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV032 | Dagget 3_SUB1_INV032_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Insulation Resistance | Inverter | inverter032_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1480 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Number of DU Channels | Inverter | inverter032_MODBUS.HR0653_duChannels | Number of DU Channels | 1481 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Number of Running Modules | Inverter | inverter032_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1482 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Operating State | Inverter | inverter032_MODBUS.HR1123_currentStatus | Operating State | 1483 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Power Factor | Inverter | inverter032_MODBUS.HR1011_pf3 | Power Factor | 1484 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV032 | Dagget 3_SUB1_INV032_Ramp Down | Inverter | inverter032_MODBUS.HR0286_dropGradient_p | Ramp Down | 1485 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Ramp Up | Inverter | inverter032_MODBUS.HR0282_riseGradient_p | Ramp Up | 1486 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power Delivered | Inverter | inverter032_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1487 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Reactive Power Delivered | Inverter | inverter032_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1488 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power | 1489 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Reactive Power | Inverter | inverter032_MODBUS.HR1009_q3_kvar | Reactive Power | 1490 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Reactive Power Mode | Inverter | inverter032_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1491 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Reactive Power Set Point Percent | Inverter | inverter032_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1492 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power AC Percent | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1493 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power-AC | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power-AC | 1494 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power-DC | Inverter | inverter032_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1495 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Air Intake | Inverter | inverter032_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1496 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Cabinet | Inverter | inverter032_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1497 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-IGBT | Inverter | inverter032_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1498 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Temperature-Module | Inverter | inverter032_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1499 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage A-B | Inverter | inverter032_MODBUS.HR1002_vRS_V | Voltage A-B | 1500 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage B-C | Inverter | inverter032_MODBUS.HR1002_vST_V | Voltage B-C | 1501 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage C-A | Inverter | inverter032_MODBUS.HR1003_vTR_V | Voltage C-A | 1502 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Voltage DC | Inverter | inverter032_MODBUS.HR1051_vdcBus_V | Voltage DC | 1503 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV033 | Dagget 3_SUB1_INV033_A Phase Current | Inverter | inverter033_MODBUS.HR1004_i1_A | A Phase Current | 1504 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_B Phase Current | Inverter | inverter033_MODBUS.HR1005_i2_A | B Phase Current | 1505 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_C Phase Current | Inverter | inverter033_MODBUS.HR1006_i3_A | C Phase Current | 1506 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Bus Voltage | Inverter | inverter033_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1507 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV033 | Dagget 3_SUB1_INV033_Apparent Power | Inverter | inverter033_MODBUS.HR1010_s3_VA | Apparent Power | 1508 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input1 | Inverter | inverter033_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1509 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC Input 1 | Inverter | inverter033_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1510 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input2 | Inverter | inverter033_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1511 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC input 2 | Inverter | inverter033_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1512 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input3 | Inverter | inverter033_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1513 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC input 3 | Inverter | inverter033_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1514 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input4 | Inverter | inverter033_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1515 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC input 4 | Inverter | inverter033_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1516 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input5 | Inverter | inverter033_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1517 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC input 5 | Inverter | inverter033_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1518 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current DC Input6 | Inverter | inverter033_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1519 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC input 6 | Inverter | inverter033_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1520 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current-AC | Inverter | inverter033_MODBUS.HR1007_i3Avg_A | Current-AC | 1521 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Current-DC | Inverter | inverter033_MODBUS.HR1062_idcInput_A | Current-DC | 1522 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Daily Energy Delivered | Inverter | inverter033_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1523 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power Set Point | Inverter | inverter033_MODBUS.HR0553_pRef | Real Power Set Point | 1524 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Reactive Power Set Point | Inverter | inverter033_MODBUS.HR0558_qRef | Reactive Power Set Point | 1525 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Frequency | Inverter | inverter033_MODBUS.HR1012_f3_Hz | Frequency | 1526 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV033 | Dagget 3_SUB1_INV033_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Insulation Resistance | Inverter | inverter033_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1527 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Number of DU Channels | Inverter | inverter033_MODBUS.HR0653_duChannels | Number of DU Channels | 1528 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Number of Running Modules | Inverter | inverter033_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1529 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Operating State | Inverter | inverter033_MODBUS.HR1123_currentStatus | Operating State | 1530 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Power Factor | Inverter | inverter033_MODBUS.HR1011_pf3 | Power Factor | 1531 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV033 | Dagget 3_SUB1_INV033_Ramp Down | Inverter | inverter033_MODBUS.HR0286_dropGradient_p | Ramp Down | 1532 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Ramp Up | Inverter | inverter033_MODBUS.HR0282_riseGradient_p | Ramp Up | 1533 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power Delivered | Inverter | inverter033_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1534 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Reactive Power Delivered | Inverter | inverter033_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1535 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power | 1536 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Reactive Power | Inverter | inverter033_MODBUS.HR1009_q3_kvar | Reactive Power | 1537 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Reactive Power Mode | Inverter | inverter033_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1538 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Reactive Power Set Point Percent | Inverter | inverter033_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1539 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power AC Percent | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1540 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power-AC | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power-AC | 1541 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power-DC | Inverter | inverter033_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1542 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Air Intake | Inverter | inverter033_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1543 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Cabinet | Inverter | inverter033_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1544 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-IGBT | Inverter | inverter033_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1545 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Temperature-Module | Inverter | inverter033_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1546 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage A-B | Inverter | inverter033_MODBUS.HR1003_vRS_V | Voltage A-B | 1547 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage B-C | Inverter | inverter033_MODBUS.HR1002_vST_V | Voltage B-C | 1548 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage C-A | Inverter | inverter033_MODBUS.HR1003_vTR_V | Voltage C-A | 1549 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Voltage DC | Inverter | inverter033_MODBUS.HR1051_vdcBus_V | Voltage DC | 1550 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV034 | Dagget 3_SUB1_INV034_A Phase Current | Inverter | inverter034_MODBUS.HR1004_i1_A | A Phase Current | 1551 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_B Phase Current | Inverter | inverter034_MODBUS.HR1005_i2_A | B Phase Current | 1552 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_C Phase Current | Inverter | inverter034_MODBUS.HR1006_i3_A | C Phase Current | 1553 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Bus Voltage | Inverter | inverter034_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1554 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV034 | Dagget 3_SUB1_INV034_Apparent Power | Inverter | inverter034_MODBUS.HR1010_s3_VA | Apparent Power | 1555 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input1 | Inverter | inverter034_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1556 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC Input 1 | Inverter | inverter034_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1557 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input2 | Inverter | inverter034_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1558 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC input 2 | Inverter | inverter034_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1559 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input3 | Inverter | inverter034_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1560 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC input 3 | Inverter | inverter034_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1561 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input4 | Inverter | inverter034_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1562 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC input 4 | Inverter | inverter034_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1563 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input5 | Inverter | inverter034_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1564 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC input 5 | Inverter | inverter034_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1565 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current DC Input6 | Inverter | inverter034_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1566 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC input 6 | Inverter | inverter034_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1567 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current-AC | Inverter | inverter034_MODBUS.HR1007_i3Avg_A | Current-AC | 1568 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Current-DC | Inverter | inverter034_MODBUS.HR1062_idcInput_A | Current-DC | 1569 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Daily Energy Delivered | Inverter | inverter034_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1570 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power Set Point | Inverter | inverter034_MODBUS.HR0553_pRef | Real Power Set Point | 1571 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Reactive Power Set Point | Inverter | inverter034_MODBUS.HR0558_qRef | Reactive Power Set Point | 1572 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Frequency | Inverter | inverter034_MODBUS.HR1012_f3_Hz | Frequency | 1573 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV034 | Dagget 3_SUB1_INV034_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Insulation Resistance | Inverter | inverter034_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1574 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Number of DU Channels | Inverter | inverter034_MODBUS.HR0653_duChannels | Number of DU Channels | 1575 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Number of Running Modules | Inverter | inverter034_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1576 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Operating State | Inverter | inverter034_MODBUS.HR1123_currentStatus | Operating State | 1577 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Power Factor | Inverter | inverter034_MODBUS.HR1011_pf3 | Power Factor | 1578 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV034 | Dagget 3_SUB1_INV034_Ramp Down | Inverter | inverter034_MODBUS.HR0286_dropGradient_p | Ramp Down | 1579 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Ramp Up | Inverter | inverter034_MODBUS.HR0282_riseGradient_p | Ramp Up | 1580 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power Delivered | Inverter | inverter034_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1581 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Reactive Power Delivered | Inverter | inverter034_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1582 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power | 1583 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Reactive Power | Inverter | inverter034_MODBUS.HR1009_q3_kvar | Reactive Power | 1584 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Reactive Power Mode | Inverter | inverter034_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1585 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Reactive Power Set Point Percent | Inverter | inverter034_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1586 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power AC Percent | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1587 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power-AC | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power-AC | 1588 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power-DC | Inverter | inverter034_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1589 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Air Intake | Inverter | inverter034_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1590 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Cabinet | Inverter | inverter034_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1591 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-IGBT | Inverter | inverter034_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1592 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Temperature-Module | Inverter | inverter034_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1593 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage A-B | Inverter | inverter034_MODBUS.HR1004_vRS_V | Voltage A-B | 1594 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage B-C | Inverter | inverter034_MODBUS.HR1002_vST_V | Voltage B-C | 1595 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage C-A | Inverter | inverter034_MODBUS.HR1003_vTR_V | Voltage C-A | 1596 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Voltage DC | Inverter | inverter034_MODBUS.HR1051_vdcBus_V | Voltage DC | 1597 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV035 | Dagget 3_SUB1_INV035_A Phase Current | Inverter | inverter035_MODBUS.HR1004_i1_A | A Phase Current | 1598 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_B Phase Current | Inverter | inverter035_MODBUS.HR1005_i2_A | B Phase Current | 1599 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_C Phase Current | Inverter | inverter035_MODBUS.HR1006_i3_A | C Phase Current | 1600 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Bus Voltage | Inverter | inverter035_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1601 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV035 | Dagget 3_SUB1_INV035_Apparent Power | Inverter | inverter035_MODBUS.HR1010_s3_VA | Apparent Power | 1602 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input1 | Inverter | inverter035_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1603 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC Input 1 | Inverter | inverter035_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1604 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input2 | Inverter | inverter035_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1605 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC input 2 | Inverter | inverter035_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1606 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input3 | Inverter | inverter035_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1607 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC input 3 | Inverter | inverter035_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1608 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input4 | Inverter | inverter035_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1609 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC input 4 | Inverter | inverter035_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1610 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input5 | Inverter | inverter035_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1611 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC input 5 | Inverter | inverter035_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1612 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current DC Input6 | Inverter | inverter035_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1613 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC input 6 | Inverter | inverter035_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1614 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current-AC | Inverter | inverter035_MODBUS.HR1007_i3Avg_A | Current-AC | 1615 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Current-DC | Inverter | inverter035_MODBUS.HR1062_idcInput_A | Current-DC | 1616 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Daily Energy Delivered | Inverter | inverter035_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1617 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power Set Point | Inverter | inverter035_MODBUS.HR0553_pRef | Real Power Set Point | 1618 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Reactive Power Set Point | Inverter | inverter035_MODBUS.HR0558_qRef | Reactive Power Set Point | 1619 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Frequency | Inverter | inverter035_MODBUS.HR1012_f3_Hz | Frequency | 1620 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV035 | Dagget 3_SUB1_INV035_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Insulation Resistance | Inverter | inverter035_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1621 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Number of DU Channels | Inverter | inverter035_MODBUS.HR0653_duChannels | Number of DU Channels | 1622 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Number of Running Modules | Inverter | inverter035_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1623 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Operating State | Inverter | inverter035_MODBUS.HR1123_currentStatus | Operating State | 1624 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Power Factor | Inverter | inverter035_MODBUS.HR1011_pf3 | Power Factor | 1625 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV035 | Dagget 3_SUB1_INV035_Ramp Down | Inverter | inverter035_MODBUS.HR0286_dropGradient_p | Ramp Down | 1626 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Ramp Up | Inverter | inverter035_MODBUS.HR0282_riseGradient_p | Ramp Up | 1627 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power Delivered | Inverter | inverter035_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1628 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Reactive Power Delivered | Inverter | inverter035_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1629 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power | 1630 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Reactive Power | Inverter | inverter035_MODBUS.HR1009_q3_kvar | Reactive Power | 1631 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Reactive Power Mode | Inverter | inverter035_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1632 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Reactive Power Set Point Percent | Inverter | inverter035_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1633 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power AC Percent | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1634 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power-AC | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power-AC | 1635 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power-DC | Inverter | inverter035_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1636 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Air Intake | Inverter | inverter035_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1637 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Cabinet | Inverter | inverter035_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1638 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-IGBT | Inverter | inverter035_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1639 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Temperature-Module | Inverter | inverter035_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1640 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage A-B | Inverter | inverter035_MODBUS.HR1005_vRS_V | Voltage A-B | 1641 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage B-C | Inverter | inverter035_MODBUS.HR1002_vST_V | Voltage B-C | 1642 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage C-A | Inverter | inverter035_MODBUS.HR1003_vTR_V | Voltage C-A | 1643 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Voltage DC | Inverter | inverter035_MODBUS.HR1051_vdcBus_V | Voltage DC | 1644 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV036 | Dagget 3_SUB1_INV036_A Phase Current | Inverter | inverter036_MODBUS.HR1004_i1_A | A Phase Current | 1645 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_B Phase Current | Inverter | inverter036_MODBUS.HR1005_i2_A | B Phase Current | 1646 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_C Phase Current | Inverter | inverter036_MODBUS.HR1006_i3_A | C Phase Current | 1647 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Bus Voltage | Inverter | inverter036_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1648 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV036 | Dagget 3_SUB1_INV036_Apparent Power | Inverter | inverter036_MODBUS.HR1010_s3_VA | Apparent Power | 1649 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input1 | Inverter | inverter036_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1650 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC Input 1 | Inverter | inverter036_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1651 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input2 | Inverter | inverter036_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1652 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC input 2 | Inverter | inverter036_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1653 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input3 | Inverter | inverter036_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1654 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC input 3 | Inverter | inverter036_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1655 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input4 | Inverter | inverter036_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1656 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC input 4 | Inverter | inverter036_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1657 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input5 | Inverter | inverter036_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1658 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC input 5 | Inverter | inverter036_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1659 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current DC Input6 | Inverter | inverter036_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1660 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC input 6 | Inverter | inverter036_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1661 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current-AC | Inverter | inverter036_MODBUS.HR1007_i3Avg_A | Current-AC | 1662 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Current-DC | Inverter | inverter036_MODBUS.HR1062_idcInput_A | Current-DC | 1663 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Daily Energy Delivered | Inverter | inverter036_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1664 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power Set Point | Inverter | inverter036_MODBUS.HR0553_pRef | Real Power Set Point | 1665 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Reactive Power Set Point | Inverter | inverter036_MODBUS.HR0558_qRef | Reactive Power Set Point | 1666 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Frequency | Inverter | inverter036_MODBUS.HR1012_f3_Hz | Frequency | 1667 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV036 | Dagget 3_SUB1_INV036_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Insulation Resistance | Inverter | inverter036_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1668 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Number of DU Channels | Inverter | inverter036_MODBUS.HR0653_duChannels | Number of DU Channels | 1669 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Number of Running Modules | Inverter | inverter036_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1670 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Operating State | Inverter | inverter036_MODBUS.HR1123_currentStatus | Operating State | 1671 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Power Factor | Inverter | inverter036_MODBUS.HR1011_pf3 | Power Factor | 1672 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV036 | Dagget 3_SUB1_INV036_Ramp Down | Inverter | inverter036_MODBUS.HR0286_dropGradient_p | Ramp Down | 1673 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Ramp Up | Inverter | inverter036_MODBUS.HR0282_riseGradient_p | Ramp Up | 1674 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power Delivered | Inverter | inverter036_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1675 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Reactive Power Delivered | Inverter | inverter036_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1676 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power | 1677 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Reactive Power | Inverter | inverter036_MODBUS.HR1009_q3_kvar | Reactive Power | 1678 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Reactive Power Mode | Inverter | inverter036_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1679 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Reactive Power Set Point Percent | Inverter | inverter036_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1680 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power AC Percent | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1681 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power-AC | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power-AC | 1682 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power-DC | Inverter | inverter036_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1683 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Air Intake | Inverter | inverter036_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1684 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Cabinet | Inverter | inverter036_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1685 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-IGBT | Inverter | inverter036_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1686 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Temperature-Module | Inverter | inverter036_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1687 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage A-B | Inverter | inverter036_MODBUS.HR1006_vRS_V | Voltage A-B | 1688 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage B-C | Inverter | inverter036_MODBUS.HR1002_vST_V | Voltage B-C | 1689 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage C-A | Inverter | inverter036_MODBUS.HR1003_vTR_V | Voltage C-A | 1690 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Voltage DC | Inverter | inverter036_MODBUS.HR1051_vdcBus_V | Voltage DC | 1691 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV037 | Dagget 3_SUB1_INV037_A Phase Current | Inverter | inverter037_MODBUS.HR1004_i1_A | A Phase Current | 1692 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_B Phase Current | Inverter | inverter037_MODBUS.HR1005_i2_A | B Phase Current | 1693 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_C Phase Current | Inverter | inverter037_MODBUS.HR1006_i3_A | C Phase Current | 1694 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Bus Voltage | Inverter | inverter037_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1695 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV037 | Dagget 3_SUB1_INV037_Apparent Power | Inverter | inverter037_MODBUS.HR1010_s3_VA | Apparent Power | 1696 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input1 | Inverter | inverter037_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1697 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC Input 1 | Inverter | inverter037_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1698 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input2 | Inverter | inverter037_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1699 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC input 2 | Inverter | inverter037_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1700 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input3 | Inverter | inverter037_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1701 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC input 3 | Inverter | inverter037_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1702 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input4 | Inverter | inverter037_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1703 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC input 4 | Inverter | inverter037_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1704 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input5 | Inverter | inverter037_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1705 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC input 5 | Inverter | inverter037_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1706 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current DC Input6 | Inverter | inverter037_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1707 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC input 6 | Inverter | inverter037_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1708 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current-AC | Inverter | inverter037_MODBUS.HR1007_i3Avg_A | Current-AC | 1709 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Current-DC | Inverter | inverter037_MODBUS.HR1062_idcInput_A | Current-DC | 1710 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Daily Energy Delivered | Inverter | inverter037_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1711 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power Set Point | Inverter | inverter037_MODBUS.HR0553_pRef | Real Power Set Point | 1712 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Reactive Power Set Point | Inverter | inverter037_MODBUS.HR0558_qRef | Reactive Power Set Point | 1713 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Frequency | Inverter | inverter037_MODBUS.HR1012_f3_Hz | Frequency | 1714 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV037 | Dagget 3_SUB1_INV037_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Insulation Resistance | Inverter | inverter037_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1715 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Number of DU Channels | Inverter | inverter037_MODBUS.HR0653_duChannels | Number of DU Channels | 1716 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Number of Running Modules | Inverter | inverter037_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1717 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Operating State | Inverter | inverter037_MODBUS.HR1123_currentStatus | Operating State | 1718 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Power Factor | Inverter | inverter037_MODBUS.HR1011_pf3 | Power Factor | 1719 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV037 | Dagget 3_SUB1_INV037_Ramp Down | Inverter | inverter037_MODBUS.HR0286_dropGradient_p | Ramp Down | 1720 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Ramp Up | Inverter | inverter037_MODBUS.HR0282_riseGradient_p | Ramp Up | 1721 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power Delivered | Inverter | inverter037_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1722 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Reactive Power Delivered | Inverter | inverter037_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1723 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power | 1724 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Reactive Power | Inverter | inverter037_MODBUS.HR1009_q3_kvar | Reactive Power | 1725 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Reactive Power Mode | Inverter | inverter037_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1726 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Reactive Power Set Point Percent | Inverter | inverter037_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1727 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power AC Percent | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1728 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power-AC | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power-AC | 1729 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power-DC | Inverter | inverter037_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1730 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Air Intake | Inverter | inverter037_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1731 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Cabinet | Inverter | inverter037_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1732 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-IGBT | Inverter | inverter037_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1733 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Temperature-Module | Inverter | inverter037_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1734 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage A-B | Inverter | inverter037_MODBUS.HR1007_vRS_V | Voltage A-B | 1735 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage B-C | Inverter | inverter037_MODBUS.HR1002_vST_V | Voltage B-C | 1736 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage C-A | Inverter | inverter037_MODBUS.HR1003_vTR_V | Voltage C-A | 1737 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Voltage DC | Inverter | inverter037_MODBUS.HR1051_vdcBus_V | Voltage DC | 1738 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV038 | Dagget 3_SUB1_INV038_A Phase Current | Inverter | inverter038_MODBUS.HR1004_i1_A | A Phase Current | 1739 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_B Phase Current | Inverter | inverter038_MODBUS.HR1005_i2_A | B Phase Current | 1740 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_C Phase Current | Inverter | inverter038_MODBUS.HR1006_i3_A | C Phase Current | 1741 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Bus Voltage | Inverter | inverter038_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1742 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV038 | Dagget 3_SUB1_INV038_Apparent Power | Inverter | inverter038_MODBUS.HR1010_s3_VA | Apparent Power | 1743 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input1 | Inverter | inverter038_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1744 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC Input 1 | Inverter | inverter038_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1745 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input2 | Inverter | inverter038_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1746 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC input 2 | Inverter | inverter038_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1747 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input3 | Inverter | inverter038_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1748 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC input 3 | Inverter | inverter038_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1749 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input4 | Inverter | inverter038_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1750 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC input 4 | Inverter | inverter038_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1751 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input5 | Inverter | inverter038_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1752 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC input 5 | Inverter | inverter038_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1753 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current DC Input6 | Inverter | inverter038_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1754 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC input 6 | Inverter | inverter038_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1755 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current-AC | Inverter | inverter038_MODBUS.HR1007_i3Avg_A | Current-AC | 1756 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Current-DC | Inverter | inverter038_MODBUS.HR1062_idcInput_A | Current-DC | 1757 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Daily Energy Delivered | Inverter | inverter038_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1758 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power Set Point | Inverter | inverter038_MODBUS.HR0553_pRef | Real Power Set Point | 1759 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Reactive Power Set Point | Inverter | inverter038_MODBUS.HR0558_qRef | Reactive Power Set Point | 1760 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Frequency | Inverter | inverter038_MODBUS.HR1012_f3_Hz | Frequency | 1761 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV038 | Dagget 3_SUB1_INV038_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Insulation Resistance | Inverter | inverter038_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1762 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Number of DU Channels | Inverter | inverter038_MODBUS.HR0653_duChannels | Number of DU Channels | 1763 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Number of Running Modules | Inverter | inverter038_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1764 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Operating State | Inverter | inverter038_MODBUS.HR1123_currentStatus | Operating State | 1765 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Power Factor | Inverter | inverter038_MODBUS.HR1011_pf3 | Power Factor | 1766 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV038 | Dagget 3_SUB1_INV038_Ramp Down | Inverter | inverter038_MODBUS.HR0286_dropGradient_p | Ramp Down | 1767 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Ramp Up | Inverter | inverter038_MODBUS.HR0282_riseGradient_p | Ramp Up | 1768 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power Delivered | Inverter | inverter038_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1769 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Reactive Power Delivered | Inverter | inverter038_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1770 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power | 1771 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Reactive Power | Inverter | inverter038_MODBUS.HR1009_q3_kvar | Reactive Power | 1772 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Reactive Power Mode | Inverter | inverter038_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1773 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Reactive Power Set Point Percent | Inverter | inverter038_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1774 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power AC Percent | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1775 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power-AC | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power-AC | 1776 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power-DC | Inverter | inverter038_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1777 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Air Intake | Inverter | inverter038_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1778 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Cabinet | Inverter | inverter038_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1779 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-IGBT | Inverter | inverter038_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1780 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Temperature-Module | Inverter | inverter038_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1781 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage A-B | Inverter | inverter038_MODBUS.HR1008_vRS_V | Voltage A-B | 1782 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage B-C | Inverter | inverter038_MODBUS.HR1002_vST_V | Voltage B-C | 1783 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage C-A | Inverter | inverter038_MODBUS.HR1003_vTR_V | Voltage C-A | 1784 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Voltage DC | Inverter | inverter038_MODBUS.HR1051_vdcBus_V | Voltage DC | 1785 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV039 | Dagget 3_SUB1_INV039_A Phase Current | Inverter | inverter039_MODBUS.HR1004_i1_A | A Phase Current | 1786 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_B Phase Current | Inverter | inverter039_MODBUS.HR1005_i2_A | B Phase Current | 1787 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_C Phase Current | Inverter | inverter039_MODBUS.HR1006_i3_A | C Phase Current | 1788 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Bus Voltage | Inverter | inverter039_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1789 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV039 | Dagget 3_SUB1_INV039_Apparent Power | Inverter | inverter039_MODBUS.HR1010_s3_VA | Apparent Power | 1790 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input1 | Inverter | inverter039_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1791 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC Input 1 | Inverter | inverter039_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1792 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input2 | Inverter | inverter039_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1793 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC input 2 | Inverter | inverter039_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1794 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input3 | Inverter | inverter039_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1795 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC input 3 | Inverter | inverter039_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1796 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input4 | Inverter | inverter039_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1797 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC input 4 | Inverter | inverter039_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1798 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input5 | Inverter | inverter039_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1799 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC input 5 | Inverter | inverter039_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1800 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current DC Input6 | Inverter | inverter039_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1801 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC input 6 | Inverter | inverter039_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1802 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current-AC | Inverter | inverter039_MODBUS.HR1007_i3Avg_A | Current-AC | 1803 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Current-DC | Inverter | inverter039_MODBUS.HR1062_idcInput_A | Current-DC | 1804 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Daily Energy Delivered | Inverter | inverter039_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1805 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power Set Point | Inverter | inverter039_MODBUS.HR0553_pRef | Real Power Set Point | 1806 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Reactive Power Set Point | Inverter | inverter039_MODBUS.HR0558_qRef | Reactive Power Set Point | 1807 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Frequency | Inverter | inverter039_MODBUS.HR1012_f3_Hz | Frequency | 1808 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV039 | Dagget 3_SUB1_INV039_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Insulation Resistance | Inverter | inverter039_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1809 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Number of DU Channels | Inverter | inverter039_MODBUS.HR0653_duChannels | Number of DU Channels | 1810 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Number of Running Modules | Inverter | inverter039_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1811 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Operating State | Inverter | inverter039_MODBUS.HR1123_currentStatus | Operating State | 1812 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Power Factor | Inverter | inverter039_MODBUS.HR1011_pf3 | Power Factor | 1813 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV039 | Dagget 3_SUB1_INV039_Ramp Down | Inverter | inverter039_MODBUS.HR0286_dropGradient_p | Ramp Down | 1814 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Ramp Up | Inverter | inverter039_MODBUS.HR0282_riseGradient_p | Ramp Up | 1815 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power Delivered | Inverter | inverter039_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1816 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Reactive Power Delivered | Inverter | inverter039_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1817 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power | 1818 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Reactive Power | Inverter | inverter039_MODBUS.HR1009_q3_kvar | Reactive Power | 1819 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Reactive Power Mode | Inverter | inverter039_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1820 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Reactive Power Set Point Percent | Inverter | inverter039_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1821 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power AC Percent | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1822 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power-AC | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power-AC | 1823 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power-DC | Inverter | inverter039_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1824 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Air Intake | Inverter | inverter039_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1825 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Cabinet | Inverter | inverter039_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1826 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-IGBT | Inverter | inverter039_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1827 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Temperature-Module | Inverter | inverter039_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1828 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage A-B | Inverter | inverter039_MODBUS.HR1009_vRS_V | Voltage A-B | 1829 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage B-C | Inverter | inverter039_MODBUS.HR1002_vST_V | Voltage B-C | 1830 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage C-A | Inverter | inverter039_MODBUS.HR1003_vTR_V | Voltage C-A | 1831 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Voltage DC | Inverter | inverter039_MODBUS.HR1051_vdcBus_V | Voltage DC | 1832 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV040 | Dagget 3_SUB1_INV040_A Phase Current | Inverter | inverter040_MODBUS.HR1004_i1_A | A Phase Current | 1833 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_B Phase Current | Inverter | inverter040_MODBUS.HR1005_i2_A | B Phase Current | 1834 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_C Phase Current | Inverter | inverter040_MODBUS.HR1006_i3_A | C Phase Current | 1835 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Bus Voltage | Inverter | inverter040_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1836 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV040 | Dagget 3_SUB1_INV040_Apparent Power | Inverter | inverter040_MODBUS.HR1010_s3_VA | Apparent Power | 1837 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input1 | Inverter | inverter040_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1838 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC Input 1 | Inverter | inverter040_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1839 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input2 | Inverter | inverter040_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1840 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC input 2 | Inverter | inverter040_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1841 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input3 | Inverter | inverter040_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1842 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC input 3 | Inverter | inverter040_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1843 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input4 | Inverter | inverter040_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1844 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC input 4 | Inverter | inverter040_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1845 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input5 | Inverter | inverter040_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1846 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC input 5 | Inverter | inverter040_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1847 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current DC Input6 | Inverter | inverter040_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1848 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC input 6 | Inverter | inverter040_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1849 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current-AC | Inverter | inverter040_MODBUS.HR1007_i3Avg_A | Current-AC | 1850 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Current-DC | Inverter | inverter040_MODBUS.HR1062_idcInput_A | Current-DC | 1851 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Daily Energy Delivered | Inverter | inverter040_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1852 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power Set Point | Inverter | inverter040_MODBUS.HR0553_pRef | Real Power Set Point | 1853 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Reactive Power Set Point | Inverter | inverter040_MODBUS.HR0558_qRef | Reactive Power Set Point | 1854 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Frequency | Inverter | inverter040_MODBUS.HR1012_f3_Hz | Frequency | 1855 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV040 | Dagget 3_SUB1_INV040_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Insulation Resistance | Inverter | inverter040_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1856 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Number of DU Channels | Inverter | inverter040_MODBUS.HR0653_duChannels | Number of DU Channels | 1857 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Number of Running Modules | Inverter | inverter040_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1858 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Operating State | Inverter | inverter040_MODBUS.HR1123_currentStatus | Operating State | 1859 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Power Factor | Inverter | inverter040_MODBUS.HR1011_pf3 | Power Factor | 1860 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV040 | Dagget 3_SUB1_INV040_Ramp Down | Inverter | inverter040_MODBUS.HR0286_dropGradient_p | Ramp Down | 1861 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Ramp Up | Inverter | inverter040_MODBUS.HR0282_riseGradient_p | Ramp Up | 1862 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power Delivered | Inverter | inverter040_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1863 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Reactive Power Delivered | Inverter | inverter040_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1864 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power | 1865 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Reactive Power | Inverter | inverter040_MODBUS.HR1009_q3_kvar | Reactive Power | 1866 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Reactive Power Mode | Inverter | inverter040_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1867 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Reactive Power Set Point Percent | Inverter | inverter040_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1868 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power AC Percent | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1869 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power-AC | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power-AC | 1870 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power-DC | Inverter | inverter040_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1871 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Air Intake | Inverter | inverter040_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1872 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Cabinet | Inverter | inverter040_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1873 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-IGBT | Inverter | inverter040_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1874 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Temperature-Module | Inverter | inverter040_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1875 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage A-B | Inverter | inverter040_MODBUS.HR1010_vRS_V | Voltage A-B | 1876 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage B-C | Inverter | inverter040_MODBUS.HR1002_vST_V | Voltage B-C | 1877 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage C-A | Inverter | inverter040_MODBUS.HR1003_vTR_V | Voltage C-A | 1878 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Voltage DC | Inverter | inverter040_MODBUS.HR1051_vdcBus_V | Voltage DC | 1879 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV041 | Dagget 3_SUB1_INV041_A Phase Current | Inverter | inverter041_MODBUS.HR1004_i1_A | A Phase Current | 1880 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_B Phase Current | Inverter | inverter041_MODBUS.HR1005_i2_A | B Phase Current | 1881 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_C Phase Current | Inverter | inverter041_MODBUS.HR1006_i3_A | C Phase Current | 1882 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Bus Voltage | Inverter | inverter041_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1883 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV041 | Dagget 3_SUB1_INV041_Apparent Power | Inverter | inverter041_MODBUS.HR1010_s3_VA | Apparent Power | 1884 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input1 | Inverter | inverter041_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1885 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC Input 1 | Inverter | inverter041_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1886 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input2 | Inverter | inverter041_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1887 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC input 2 | Inverter | inverter041_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1888 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input3 | Inverter | inverter041_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1889 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC input 3 | Inverter | inverter041_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1890 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input4 | Inverter | inverter041_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1891 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC input 4 | Inverter | inverter041_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1892 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input5 | Inverter | inverter041_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1893 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC input 5 | Inverter | inverter041_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1894 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current DC Input6 | Inverter | inverter041_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1895 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC input 6 | Inverter | inverter041_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1896 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current-AC | Inverter | inverter041_MODBUS.HR1007_i3Avg_A | Current-AC | 1897 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Current-DC | Inverter | inverter041_MODBUS.HR1062_idcInput_A | Current-DC | 1898 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Daily Energy Delivered | Inverter | inverter041_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1899 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power Set Point | Inverter | inverter041_MODBUS.HR0553_pRef | Real Power Set Point | 1900 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Reactive Power Set Point | Inverter | inverter041_MODBUS.HR0558_qRef | Reactive Power Set Point | 1901 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Frequency | Inverter | inverter041_MODBUS.HR1012_f3_Hz | Frequency | 1902 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV041 | Dagget 3_SUB1_INV041_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Insulation Resistance | Inverter | inverter041_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1903 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Number of DU Channels | Inverter | inverter041_MODBUS.HR0653_duChannels | Number of DU Channels | 1904 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Number of Running Modules | Inverter | inverter041_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1905 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Operating State | Inverter | inverter041_MODBUS.HR1123_currentStatus | Operating State | 1906 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Power Factor | Inverter | inverter041_MODBUS.HR1011_pf3 | Power Factor | 1907 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV041 | Dagget 3_SUB1_INV041_Ramp Down | Inverter | inverter041_MODBUS.HR0286_dropGradient_p | Ramp Down | 1908 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Ramp Up | Inverter | inverter041_MODBUS.HR0282_riseGradient_p | Ramp Up | 1909 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power Delivered | Inverter | inverter041_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1910 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Reactive Power Delivered | Inverter | inverter041_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1911 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power | 1912 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Reactive Power | Inverter | inverter041_MODBUS.HR1009_q3_kvar | Reactive Power | 1913 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Reactive Power Mode | Inverter | inverter041_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1914 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Reactive Power Set Point Percent | Inverter | inverter041_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1915 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power AC Percent | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1916 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power-AC | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power-AC | 1917 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power-DC | Inverter | inverter041_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1918 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Air Intake | Inverter | inverter041_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1919 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Cabinet | Inverter | inverter041_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1920 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-IGBT | Inverter | inverter041_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1921 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Temperature-Module | Inverter | inverter041_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1922 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage A-B | Inverter | inverter041_MODBUS.HR1001_vRS_V | Voltage A-B | 1923 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage B-C | Inverter | inverter041_MODBUS.HR1002_vST_V | Voltage B-C | 1924 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage C-A | Inverter | inverter041_MODBUS.HR1003_vTR_V | Voltage C-A | 1925 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Voltage DC | Inverter | inverter041_MODBUS.HR1051_vdcBus_V | Voltage DC | 1926 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV042 | Dagget 3_SUB1_INV042_A Phase Current | Inverter | inverter042_MODBUS.HR1004_i1_A | A Phase Current | 1927 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_B Phase Current | Inverter | inverter042_MODBUS.HR1005_i2_A | B Phase Current | 1928 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_C Phase Current | Inverter | inverter042_MODBUS.HR1006_i3_A | C Phase Current | 1929 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Bus Voltage | Inverter | inverter042_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1930 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV042 | Dagget 3_SUB1_INV042_Apparent Power | Inverter | inverter042_MODBUS.HR1010_s3_VA | Apparent Power | 1931 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input1 | Inverter | inverter042_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1932 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC Input 1 | Inverter | inverter042_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1933 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input2 | Inverter | inverter042_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1934 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC input 2 | Inverter | inverter042_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1935 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input3 | Inverter | inverter042_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1936 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC input 3 | Inverter | inverter042_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1937 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input4 | Inverter | inverter042_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1938 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC input 4 | Inverter | inverter042_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1939 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input5 | Inverter | inverter042_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1940 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC input 5 | Inverter | inverter042_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1941 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current DC Input6 | Inverter | inverter042_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1942 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC input 6 | Inverter | inverter042_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1943 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current-AC | Inverter | inverter042_MODBUS.HR1007_i3Avg_A | Current-AC | 1944 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Current-DC | Inverter | inverter042_MODBUS.HR1062_idcInput_A | Current-DC | 1945 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Daily Energy Delivered | Inverter | inverter042_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1946 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power Set Point | Inverter | inverter042_MODBUS.HR0553_pRef | Real Power Set Point | 1947 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Reactive Power Set Point | Inverter | inverter042_MODBUS.HR0558_qRef | Reactive Power Set Point | 1948 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Frequency | Inverter | inverter042_MODBUS.HR1012_f3_Hz | Frequency | 1949 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV042 | Dagget 3_SUB1_INV042_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Insulation Resistance | Inverter | inverter042_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1950 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Number of DU Channels | Inverter | inverter042_MODBUS.HR0653_duChannels | Number of DU Channels | 1951 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Number of Running Modules | Inverter | inverter042_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1952 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Operating State | Inverter | inverter042_MODBUS.HR1123_currentStatus | Operating State | 1953 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Power Factor | Inverter | inverter042_MODBUS.HR1011_pf3 | Power Factor | 1954 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV042 | Dagget 3_SUB1_INV042_Ramp Down | Inverter | inverter042_MODBUS.HR0286_dropGradient_p | Ramp Down | 1955 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Ramp Up | Inverter | inverter042_MODBUS.HR0282_riseGradient_p | Ramp Up | 1956 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power Delivered | Inverter | inverter042_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1957 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Reactive Power Delivered | Inverter | inverter042_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1958 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power | 1959 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Reactive Power | Inverter | inverter042_MODBUS.HR1009_q3_kvar | Reactive Power | 1960 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Reactive Power Mode | Inverter | inverter042_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1961 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Reactive Power Set Point Percent | Inverter | inverter042_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1962 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power AC Percent | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1963 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power-AC | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power-AC | 1964 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power-DC | Inverter | inverter042_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1965 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Air Intake | Inverter | inverter042_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1966 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Cabinet | Inverter | inverter042_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1967 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-IGBT | Inverter | inverter042_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1968 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Temperature-Module | Inverter | inverter042_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1969 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage A-B | Inverter | inverter042_MODBUS.HR1002_vRS_V | Voltage A-B | 1970 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage B-C | Inverter | inverter042_MODBUS.HR1002_vST_V | Voltage B-C | 1971 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage C-A | Inverter | inverter042_MODBUS.HR1003_vTR_V | Voltage C-A | 1972 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Voltage DC | Inverter | inverter042_MODBUS.HR1051_vdcBus_V | Voltage DC | 1973 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV043 | Dagget 3_SUB1_INV043_A Phase Current | Inverter | inverter043_MODBUS.HR1004_i1_A | A Phase Current | 1974 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_B Phase Current | Inverter | inverter043_MODBUS.HR1005_i2_A | B Phase Current | 1975 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_C Phase Current | Inverter | inverter043_MODBUS.HR1006_i3_A | C Phase Current | 1976 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Bus Voltage | Inverter | inverter043_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1977 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV043 | Dagget 3_SUB1_INV043_Apparent Power | Inverter | inverter043_MODBUS.HR1010_s3_VA | Apparent Power | 1978 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input1 | Inverter | inverter043_MODBUS.HR5005_m1_idc_A | Current DC Input# | 1979 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC Input 1 | Inverter | inverter043_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 1980 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input2 | Inverter | inverter043_MODBUS.HR5037_m2_idc_A | Current DC Input# | 1981 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC input 2 | Inverter | inverter043_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 1982 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input3 | Inverter | inverter043_MODBUS.HR5069_m3_idc_A | Current DC Input# | 1983 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC input 3 | Inverter | inverter043_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 1984 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input4 | Inverter | inverter043_MODBUS.HR5101_m4_idc_A | Current DC Input# | 1985 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC input 4 | Inverter | inverter043_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 1986 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input5 | Inverter | inverter043_MODBUS.HR5133_m5_idc_A | Current DC Input# | 1987 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC input 5 | Inverter | inverter043_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 1988 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current DC Input6 | Inverter | inverter043_MODBUS.HR5165_m6_idc_A | Current DC Input# | 1989 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC input 6 | Inverter | inverter043_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 1990 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current-AC | Inverter | inverter043_MODBUS.HR1007_i3Avg_A | Current-AC | 1991 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Current-DC | Inverter | inverter043_MODBUS.HR1062_idcInput_A | Current-DC | 1992 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Daily Energy Delivered | Inverter | inverter043_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1993 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power Set Point | Inverter | inverter043_MODBUS.HR0553_pRef | Real Power Set Point | 1994 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Reactive Power Set Point | Inverter | inverter043_MODBUS.HR0558_qRef | Reactive Power Set Point | 1995 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Frequency | Inverter | inverter043_MODBUS.HR1012_f3_Hz | Frequency | 1996 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV043 | Dagget 3_SUB1_INV043_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Insulation Resistance | Inverter | inverter043_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1997 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Number of DU Channels | Inverter | inverter043_MODBUS.HR0653_duChannels | Number of DU Channels | 1998 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Number of Running Modules | Inverter | inverter043_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1999 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Operating State | Inverter | inverter043_MODBUS.HR1123_currentStatus | Operating State | 2000 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Power Factor | Inverter | inverter043_MODBUS.HR1011_pf3 | Power Factor | 2001 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV043 | Dagget 3_SUB1_INV043_Ramp Down | Inverter | inverter043_MODBUS.HR0286_dropGradient_p | Ramp Down | 2002 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Ramp Up | Inverter | inverter043_MODBUS.HR0282_riseGradient_p | Ramp Up | 2003 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power Delivered | Inverter | inverter043_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2004 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Reactive Power Delivered | Inverter | inverter043_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2005 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power | 2006 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Reactive Power | Inverter | inverter043_MODBUS.HR1009_q3_kvar | Reactive Power | 2007 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Reactive Power Mode | Inverter | inverter043_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2008 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Reactive Power Set Point Percent | Inverter | inverter043_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2009 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power AC Percent | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2010 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power-AC | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power-AC | 2011 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power-DC | Inverter | inverter043_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2012 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Air Intake | Inverter | inverter043_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2013 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Cabinet | Inverter | inverter043_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2014 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-IGBT | Inverter | inverter043_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2015 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Temperature-Module | Inverter | inverter043_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2016 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage A-B | Inverter | inverter043_MODBUS.HR1003_vRS_V | Voltage A-B | 2017 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage B-C | Inverter | inverter043_MODBUS.HR1002_vST_V | Voltage B-C | 2018 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage C-A | Inverter | inverter043_MODBUS.HR1003_vTR_V | Voltage C-A | 2019 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Voltage DC | Inverter | inverter043_MODBUS.HR1051_vdcBus_V | Voltage DC | 2020 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV044 | Dagget 3_SUB1_INV044_A Phase Current | Inverter | inverter044_MODBUS.HR1004_i1_A | A Phase Current | 2021 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_B Phase Current | Inverter | inverter044_MODBUS.HR1005_i2_A | B Phase Current | 2022 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_C Phase Current | Inverter | inverter044_MODBUS.HR1006_i3_A | C Phase Current | 2023 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Bus Voltage | Inverter | inverter044_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2024 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV044 | Dagget 3_SUB1_INV044_Apparent Power | Inverter | inverter044_MODBUS.HR1010_s3_VA | Apparent Power | 2025 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input1 | Inverter | inverter044_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2026 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC Input 1 | Inverter | inverter044_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2027 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input2 | Inverter | inverter044_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2028 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC input 2 | Inverter | inverter044_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2029 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input3 | Inverter | inverter044_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2030 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC input 3 | Inverter | inverter044_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2031 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input4 | Inverter | inverter044_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2032 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC input 4 | Inverter | inverter044_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2033 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input5 | Inverter | inverter044_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2034 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC input 5 | Inverter | inverter044_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2035 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current DC Input6 | Inverter | inverter044_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2036 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC input 6 | Inverter | inverter044_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2037 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current-AC | Inverter | inverter044_MODBUS.HR1007_i3Avg_A | Current-AC | 2038 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Current-DC | Inverter | inverter044_MODBUS.HR1062_idcInput_A | Current-DC | 2039 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Daily Energy Delivered | Inverter | inverter044_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2040 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power Set Point | Inverter | inverter044_MODBUS.HR0553_pRef | Real Power Set Point | 2041 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Reactive Power Set Point | Inverter | inverter044_MODBUS.HR0558_qRef | Reactive Power Set Point | 2042 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Frequency | Inverter | inverter044_MODBUS.HR1012_f3_Hz | Frequency | 2043 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV044 | Dagget 3_SUB1_INV044_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Insulation Resistance | Inverter | inverter044_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2044 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Number of DU Channels | Inverter | inverter044_MODBUS.HR0653_duChannels | Number of DU Channels | 2045 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Number of Running Modules | Inverter | inverter044_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2046 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Operating State | Inverter | inverter044_MODBUS.HR1123_currentStatus | Operating State | 2047 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Power Factor | Inverter | inverter044_MODBUS.HR1011_pf3 | Power Factor | 2048 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV044 | Dagget 3_SUB1_INV044_Ramp Down | Inverter | inverter044_MODBUS.HR0286_dropGradient_p | Ramp Down | 2049 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Ramp Up | Inverter | inverter044_MODBUS.HR0282_riseGradient_p | Ramp Up | 2050 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power Delivered | Inverter | inverter044_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2051 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Reactive Power Delivered | Inverter | inverter044_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2052 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power | 2053 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Reactive Power | Inverter | inverter044_MODBUS.HR1009_q3_kvar | Reactive Power | 2054 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Reactive Power Mode | Inverter | inverter044_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2055 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Reactive Power Set Point Percent | Inverter | inverter044_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2056 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power AC Percent | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2057 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power-AC | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power-AC | 2058 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power-DC | Inverter | inverter044_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2059 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Air Intake | Inverter | inverter044_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2060 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Cabinet | Inverter | inverter044_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2061 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-IGBT | Inverter | inverter044_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2062 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Temperature-Module | Inverter | inverter044_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2063 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage A-B | Inverter | inverter044_MODBUS.HR1004_vRS_V | Voltage A-B | 2064 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage B-C | Inverter | inverter044_MODBUS.HR1002_vST_V | Voltage B-C | 2065 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage C-A | Inverter | inverter044_MODBUS.HR1003_vTR_V | Voltage C-A | 2066 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Voltage DC | Inverter | inverter044_MODBUS.HR1051_vdcBus_V | Voltage DC | 2067 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV045 | Dagget 3_SUB1_INV045_A Phase Current | Inverter | inverter045_MODBUS.HR1004_i1_A | A Phase Current | 2068 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_B Phase Current | Inverter | inverter045_MODBUS.HR1005_i2_A | B Phase Current | 2069 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_C Phase Current | Inverter | inverter045_MODBUS.HR1006_i3_A | C Phase Current | 2070 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Bus Voltage | Inverter | inverter045_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2071 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV045 | Dagget 3_SUB1_INV045_Apparent Power | Inverter | inverter045_MODBUS.HR1010_s3_VA | Apparent Power | 2072 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input1 | Inverter | inverter045_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2073 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC Input 1 | Inverter | inverter045_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2074 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input2 | Inverter | inverter045_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2075 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC input 2 | Inverter | inverter045_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2076 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input3 | Inverter | inverter045_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2077 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC input 3 | Inverter | inverter045_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2078 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input4 | Inverter | inverter045_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2079 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC input 4 | Inverter | inverter045_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2080 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input5 | Inverter | inverter045_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2081 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC input 5 | Inverter | inverter045_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2082 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current DC Input6 | Inverter | inverter045_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2083 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC input 6 | Inverter | inverter045_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2084 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current-AC | Inverter | inverter045_MODBUS.HR1007_i3Avg_A | Current-AC | 2085 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Current-DC | Inverter | inverter045_MODBUS.HR1062_idcInput_A | Current-DC | 2086 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Daily Energy Delivered | Inverter | inverter045_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2087 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power Set Point | Inverter | inverter045_MODBUS.HR0553_pRef | Real Power Set Point | 2088 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Reactive Power Set Point | Inverter | inverter045_MODBUS.HR0558_qRef | Reactive Power Set Point | 2089 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Frequency | Inverter | inverter045_MODBUS.HR1012_f3_Hz | Frequency | 2090 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV045 | Dagget 3_SUB1_INV045_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Insulation Resistance | Inverter | inverter045_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2091 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Number of DU Channels | Inverter | inverter045_MODBUS.HR0653_duChannels | Number of DU Channels | 2092 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Number of Running Modules | Inverter | inverter045_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2093 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Operating State | Inverter | inverter045_MODBUS.HR1123_currentStatus | Operating State | 2094 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Power Factor | Inverter | inverter045_MODBUS.HR1011_pf3 | Power Factor | 2095 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV045 | Dagget 3_SUB1_INV045_Ramp Down | Inverter | inverter045_MODBUS.HR0286_dropGradient_p | Ramp Down | 2096 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Ramp Up | Inverter | inverter045_MODBUS.HR0282_riseGradient_p | Ramp Up | 2097 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power Delivered | Inverter | inverter045_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2098 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Reactive Power Delivered | Inverter | inverter045_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2099 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power | 2100 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Reactive Power | Inverter | inverter045_MODBUS.HR1009_q3_kvar | Reactive Power | 2101 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Reactive Power Mode | Inverter | inverter045_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2102 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Reactive Power Set Point Percent | Inverter | inverter045_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2103 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power AC Percent | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2104 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power-AC | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power-AC | 2105 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power-DC | Inverter | inverter045_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2106 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Air Intake | Inverter | inverter045_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2107 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Cabinet | Inverter | inverter045_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2108 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-IGBT | Inverter | inverter045_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2109 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Temperature-Module | Inverter | inverter045_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2110 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage A-B | Inverter | inverter045_MODBUS.HR1005_vRS_V | Voltage A-B | 2111 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage B-C | Inverter | inverter045_MODBUS.HR1002_vST_V | Voltage B-C | 2112 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage C-A | Inverter | inverter045_MODBUS.HR1003_vTR_V | Voltage C-A | 2113 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Voltage DC | Inverter | inverter045_MODBUS.HR1051_vdcBus_V | Voltage DC | 2114 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV046 | Dagget 3_SUB1_INV046_A Phase Current | Inverter | inverter046_MODBUS.HR1004_i1_A | A Phase Current | 2115 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_B Phase Current | Inverter | inverter046_MODBUS.HR1005_i2_A | B Phase Current | 2116 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_C Phase Current | Inverter | inverter046_MODBUS.HR1006_i3_A | C Phase Current | 2117 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Bus Voltage | Inverter | inverter046_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2118 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV046 | Dagget 3_SUB1_INV046_Apparent Power | Inverter | inverter046_MODBUS.HR1010_s3_VA | Apparent Power | 2119 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input1 | Inverter | inverter046_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2120 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC Input 1 | Inverter | inverter046_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2121 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input2 | Inverter | inverter046_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2122 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC input 2 | Inverter | inverter046_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2123 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input3 | Inverter | inverter046_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2124 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC input 3 | Inverter | inverter046_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2125 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input4 | Inverter | inverter046_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2126 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC input 4 | Inverter | inverter046_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2127 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input5 | Inverter | inverter046_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2128 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC input 5 | Inverter | inverter046_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2129 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current DC Input6 | Inverter | inverter046_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2130 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC input 6 | Inverter | inverter046_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2131 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current-AC | Inverter | inverter046_MODBUS.HR1007_i3Avg_A | Current-AC | 2132 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Current-DC | Inverter | inverter046_MODBUS.HR1062_idcInput_A | Current-DC | 2133 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Daily Energy Delivered | Inverter | inverter046_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2134 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power Set Point | Inverter | inverter046_MODBUS.HR0553_pRef | Real Power Set Point | 2135 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Reactive Power Set Point | Inverter | inverter046_MODBUS.HR0558_qRef | Reactive Power Set Point | 2136 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Frequency | Inverter | inverter046_MODBUS.HR1012_f3_Hz | Frequency | 2137 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV046 | Dagget 3_SUB1_INV046_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Insulation Resistance | Inverter | inverter046_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2138 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Number of DU Channels | Inverter | inverter046_MODBUS.HR0653_duChannels | Number of DU Channels | 2139 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Number of Running Modules | Inverter | inverter046_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2140 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Operating State | Inverter | inverter046_MODBUS.HR1123_currentStatus | Operating State | 2141 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Power Factor | Inverter | inverter046_MODBUS.HR1011_pf3 | Power Factor | 2142 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV046 | Dagget 3_SUB1_INV046_Ramp Down | Inverter | inverter046_MODBUS.HR0286_dropGradient_p | Ramp Down | 2143 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Ramp Up | Inverter | inverter046_MODBUS.HR0282_riseGradient_p | Ramp Up | 2144 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power Delivered | Inverter | inverter046_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2145 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Reactive Power Delivered | Inverter | inverter046_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2146 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power | 2147 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Reactive Power | Inverter | inverter046_MODBUS.HR1009_q3_kvar | Reactive Power | 2148 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Reactive Power Mode | Inverter | inverter046_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2149 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Reactive Power Set Point Percent | Inverter | inverter046_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2150 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power AC Percent | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2151 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power-AC | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power-AC | 2152 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power-DC | Inverter | inverter046_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2153 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Air Intake | Inverter | inverter046_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2154 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Cabinet | Inverter | inverter046_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2155 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-IGBT | Inverter | inverter046_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2156 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Temperature-Module | Inverter | inverter046_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2157 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage A-B | Inverter | inverter046_MODBUS.HR1006_vRS_V | Voltage A-B | 2158 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage B-C | Inverter | inverter046_MODBUS.HR1002_vST_V | Voltage B-C | 2159 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage C-A | Inverter | inverter046_MODBUS.HR1003_vTR_V | Voltage C-A | 2160 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Voltage DC | Inverter | inverter046_MODBUS.HR1051_vdcBus_V | Voltage DC | 2161 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV047 | Dagget 3_SUB1_INV047_A Phase Current | Inverter | inverter047_MODBUS.HR1004_i1_A | A Phase Current | 2162 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_B Phase Current | Inverter | inverter047_MODBUS.HR1005_i2_A | B Phase Current | 2163 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_C Phase Current | Inverter | inverter047_MODBUS.HR1006_i3_A | C Phase Current | 2164 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Bus Voltage | Inverter | inverter047_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2165 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV047 | Dagget 3_SUB1_INV047_Apparent Power | Inverter | inverter047_MODBUS.HR1010_s3_VA | Apparent Power | 2166 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input1 | Inverter | inverter047_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2167 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC Input 1 | Inverter | inverter047_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2168 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input2 | Inverter | inverter047_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2169 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC input 2 | Inverter | inverter047_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2170 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input3 | Inverter | inverter047_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2171 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC input 3 | Inverter | inverter047_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2172 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input4 | Inverter | inverter047_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2173 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC input 4 | Inverter | inverter047_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2174 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input5 | Inverter | inverter047_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2175 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC input 5 | Inverter | inverter047_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2176 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current DC Input6 | Inverter | inverter047_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2177 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC input 6 | Inverter | inverter047_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2178 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current-AC | Inverter | inverter047_MODBUS.HR1007_i3Avg_A | Current-AC | 2179 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Current-DC | Inverter | inverter047_MODBUS.HR1062_idcInput_A | Current-DC | 2180 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Daily Energy Delivered | Inverter | inverter047_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2181 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power Set Point | Inverter | inverter047_MODBUS.HR0553_pRef | Real Power Set Point | 2182 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Reactive Power Set Point | Inverter | inverter047_MODBUS.HR0558_qRef | Reactive Power Set Point | 2183 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Frequency | Inverter | inverter047_MODBUS.HR1012_f3_Hz | Frequency | 2184 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV047 | Dagget 3_SUB1_INV047_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Insulation Resistance | Inverter | inverter047_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2185 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Number of DU Channels | Inverter | inverter047_MODBUS.HR0653_duChannels | Number of DU Channels | 2186 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Number of Running Modules | Inverter | inverter047_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2187 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Operating State | Inverter | inverter047_MODBUS.HR1123_currentStatus | Operating State | 2188 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Power Factor | Inverter | inverter047_MODBUS.HR1011_pf3 | Power Factor | 2189 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV047 | Dagget 3_SUB1_INV047_Ramp Down | Inverter | inverter047_MODBUS.HR0286_dropGradient_p | Ramp Down | 2190 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Ramp Up | Inverter | inverter047_MODBUS.HR0282_riseGradient_p | Ramp Up | 2191 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power Delivered | Inverter | inverter047_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2192 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Reactive Power Delivered | Inverter | inverter047_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2193 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power | 2194 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Reactive Power | Inverter | inverter047_MODBUS.HR1009_q3_kvar | Reactive Power | 2195 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Reactive Power Mode | Inverter | inverter047_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2196 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Reactive Power Set Point Percent | Inverter | inverter047_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2197 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power AC Percent | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2198 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power-AC | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power-AC | 2199 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power-DC | Inverter | inverter047_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2200 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Air Intake | Inverter | inverter047_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2201 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Cabinet | Inverter | inverter047_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2202 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-IGBT | Inverter | inverter047_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2203 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Temperature-Module | Inverter | inverter047_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2204 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage A-B | Inverter | inverter047_MODBUS.HR1007_vRS_V | Voltage A-B | 2205 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage B-C | Inverter | inverter047_MODBUS.HR1002_vST_V | Voltage B-C | 2206 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage C-A | Inverter | inverter047_MODBUS.HR1003_vTR_V | Voltage C-A | 2207 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Voltage DC | Inverter | inverter047_MODBUS.HR1051_vdcBus_V | Voltage DC | 2208 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV048 | Dagget 3_SUB1_INV048_A Phase Current | Inverter | inverter048_MODBUS.HR1004_i1_A | A Phase Current | 2209 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_B Phase Current | Inverter | inverter048_MODBUS.HR1005_i2_A | B Phase Current | 2210 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_C Phase Current | Inverter | inverter048_MODBUS.HR1006_i3_A | C Phase Current | 2211 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Bus Voltage | Inverter | inverter048_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2212 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV048 | Dagget 3_SUB1_INV048_Apparent Power | Inverter | inverter048_MODBUS.HR1010_s3_VA | Apparent Power | 2213 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input1 | Inverter | inverter048_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2214 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC Input 1 | Inverter | inverter048_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2215 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input2 | Inverter | inverter048_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2216 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC input 2 | Inverter | inverter048_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2217 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input3 | Inverter | inverter048_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2218 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC input 3 | Inverter | inverter048_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2219 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input4 | Inverter | inverter048_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2220 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC input 4 | Inverter | inverter048_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2221 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input5 | Inverter | inverter048_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2222 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC input 5 | Inverter | inverter048_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2223 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current DC Input6 | Inverter | inverter048_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2224 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC input 6 | Inverter | inverter048_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2225 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current-AC | Inverter | inverter048_MODBUS.HR1007_i3Avg_A | Current-AC | 2226 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Current-DC | Inverter | inverter048_MODBUS.HR1062_idcInput_A | Current-DC | 2227 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Daily Energy Delivered | Inverter | inverter048_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2228 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power Set Point | Inverter | inverter048_MODBUS.HR0553_pRef | Real Power Set Point | 2229 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Reactive Power Set Point | Inverter | inverter048_MODBUS.HR0558_qRef | Reactive Power Set Point | 2230 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Frequency | Inverter | inverter048_MODBUS.HR1012_f3_Hz | Frequency | 2231 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV048 | Dagget 3_SUB1_INV048_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Insulation Resistance | Inverter | inverter048_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2232 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Number of DU Channels | Inverter | inverter048_MODBUS.HR0653_duChannels | Number of DU Channels | 2233 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Number of Running Modules | Inverter | inverter048_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2234 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Operating State | Inverter | inverter048_MODBUS.HR1123_currentStatus | Operating State | 2235 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Power Factor | Inverter | inverter048_MODBUS.HR1011_pf3 | Power Factor | 2236 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV048 | Dagget 3_SUB1_INV048_Ramp Down | Inverter | inverter048_MODBUS.HR0286_dropGradient_p | Ramp Down | 2237 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Ramp Up | Inverter | inverter048_MODBUS.HR0282_riseGradient_p | Ramp Up | 2238 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power Delivered | Inverter | inverter048_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2239 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Reactive Power Delivered | Inverter | inverter048_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2240 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power | 2241 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Reactive Power | Inverter | inverter048_MODBUS.HR1009_q3_kvar | Reactive Power | 2242 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Reactive Power Mode | Inverter | inverter048_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2243 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Reactive Power Set Point Percent | Inverter | inverter048_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2244 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power AC Percent | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2245 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power-AC | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power-AC | 2246 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power-DC | Inverter | inverter048_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2247 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Air Intake | Inverter | inverter048_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2248 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Cabinet | Inverter | inverter048_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2249 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-IGBT | Inverter | inverter048_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2250 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Temperature-Module | Inverter | inverter048_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2251 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage A-B | Inverter | inverter048_MODBUS.HR1008_vRS_V | Voltage A-B | 2252 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage B-C | Inverter | inverter048_MODBUS.HR1002_vST_V | Voltage B-C | 2253 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage C-A | Inverter | inverter048_MODBUS.HR1003_vTR_V | Voltage C-A | 2254 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Voltage DC | Inverter | inverter048_MODBUS.HR1051_vdcBus_V | Voltage DC | 2255 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV049 | Dagget 3_SUB1_INV049_A Phase Current | Inverter | inverter049_MODBUS.HR1004_i1_A | A Phase Current | 2256 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_B Phase Current | Inverter | inverter049_MODBUS.HR1005_i2_A | B Phase Current | 2257 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_C Phase Current | Inverter | inverter049_MODBUS.HR1006_i3_A | C Phase Current | 2258 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Bus Voltage | Inverter | inverter049_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2259 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV049 | Dagget 3_SUB1_INV049_Apparent Power | Inverter | inverter049_MODBUS.HR1010_s3_VA | Apparent Power | 2260 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input1 | Inverter | inverter049_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2261 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC Input 1 | Inverter | inverter049_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2262 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input2 | Inverter | inverter049_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2263 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC input 2 | Inverter | inverter049_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2264 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input3 | Inverter | inverter049_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2265 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC input 3 | Inverter | inverter049_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2266 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input4 | Inverter | inverter049_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2267 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC input 4 | Inverter | inverter049_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2268 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input5 | Inverter | inverter049_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2269 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC input 5 | Inverter | inverter049_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2270 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current DC Input6 | Inverter | inverter049_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2271 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC input 6 | Inverter | inverter049_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2272 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current-AC | Inverter | inverter049_MODBUS.HR1007_i3Avg_A | Current-AC | 2273 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Current-DC | Inverter | inverter049_MODBUS.HR1062_idcInput_A | Current-DC | 2274 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Daily Energy Delivered | Inverter | inverter049_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2275 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power Set Point | Inverter | inverter049_MODBUS.HR0553_pRef | Real Power Set Point | 2276 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Reactive Power Set Point | Inverter | inverter049_MODBUS.HR0558_qRef | Reactive Power Set Point | 2277 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Frequency | Inverter | inverter049_MODBUS.HR1012_f3_Hz | Frequency | 2278 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV049 | Dagget 3_SUB1_INV049_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Insulation Resistance | Inverter | inverter049_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2279 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Number of DU Channels | Inverter | inverter049_MODBUS.HR0653_duChannels | Number of DU Channels | 2280 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Number of Running Modules | Inverter | inverter049_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2281 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Operating State | Inverter | inverter049_MODBUS.HR1123_currentStatus | Operating State | 2282 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Power Factor | Inverter | inverter049_MODBUS.HR1011_pf3 | Power Factor | 2283 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV049 | Dagget 3_SUB1_INV049_Ramp Down | Inverter | inverter049_MODBUS.HR0286_dropGradient_p | Ramp Down | 2284 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Ramp Up | Inverter | inverter049_MODBUS.HR0282_riseGradient_p | Ramp Up | 2285 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power Delivered | Inverter | inverter049_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2286 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Reactive Power Delivered | Inverter | inverter049_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2287 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power | 2288 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Reactive Power | Inverter | inverter049_MODBUS.HR1009_q3_kvar | Reactive Power | 2289 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Reactive Power Mode | Inverter | inverter049_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2290 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Reactive Power Set Point Percent | Inverter | inverter049_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2291 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power AC Percent | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2292 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power-AC | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power-AC | 2293 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power-DC | Inverter | inverter049_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2294 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Air Intake | Inverter | inverter049_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2295 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Cabinet | Inverter | inverter049_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2296 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-IGBT | Inverter | inverter049_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2297 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Temperature-Module | Inverter | inverter049_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2298 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage A-B | Inverter | inverter049_MODBUS.HR1009_vRS_V | Voltage A-B | 2299 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage B-C | Inverter | inverter049_MODBUS.HR1002_vST_V | Voltage B-C | 2300 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage C-A | Inverter | inverter049_MODBUS.HR1003_vTR_V | Voltage C-A | 2301 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Voltage DC | Inverter | inverter049_MODBUS.HR1051_vdcBus_V | Voltage DC | 2302 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV050 | Dagget 3_SUB1_INV050_A Phase Current | Inverter | Inverter050_MODBUS.HR1004_i1_A | A Phase Current | 2303 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_B Phase Current | Inverter | Inverter050_MODBUS.HR1005_i2_A | B Phase Current | 2304 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_C Phase Current | Inverter | Inverter050_MODBUS.HR1006_i3_A | C Phase Current | 2305 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Bus Voltage | Inverter | Inverter050_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2306 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV050 | Dagget 3_SUB1_INV050_Apparent Power | Inverter | Inverter050_MODBUS.HR1010_s3_VA | Apparent Power | 2307 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input1 | Inverter | Inverter050_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2308 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC Input 1 | Inverter | Inverter050_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2309 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input2 | Inverter | Inverter050_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2310 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC input 2 | Inverter | Inverter050_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2311 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input3 | Inverter | Inverter050_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2312 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC input 3 | Inverter | Inverter050_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2313 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input4 | Inverter | Inverter050_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2314 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC input 4 | Inverter | Inverter050_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2315 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input5 | Inverter | Inverter050_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2316 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC input 5 | Inverter | Inverter050_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2317 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current DC Input6 | Inverter | Inverter050_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2318 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC input 6 | Inverter | Inverter050_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2319 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current-AC | Inverter | Inverter050_MODBUS.HR1007_i3Avg_A | Current-AC | 2320 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Current-DC | Inverter | Inverter050_MODBUS.HR1062_idcInput_A | Current-DC | 2321 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Daily Energy Delivered | Inverter | Inverter050_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2322 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power Set Point | Inverter | Inverter050_MODBUS.HR0553_pRef | Real Power Set Point | 2323 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Reactive Power Set Point | Inverter | Inverter050_MODBUS.HR0558_qRef | Reactive Power Set Point | 2324 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Frequency | Inverter | Inverter050_MODBUS.HR1012_f3_Hz | Frequency | 2325 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV050 | Dagget 3_SUB1_INV050_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Insulation Resistance | Inverter | Inverter050_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2326 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Number of DU Channels | Inverter | Inverter050_MODBUS.HR0653_duChannels | Number of DU Channels | 2327 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Number of Running Modules | Inverter | Inverter050_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2328 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Operating State | Inverter | Inverter050_MODBUS.HR1123_currentStatus | Operating State | 2329 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Power Factor | Inverter | Inverter050_MODBUS.HR1011_pf3 | Power Factor | 2330 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV050 | Dagget 3_SUB1_INV050_Ramp Down | Inverter | Inverter050_MODBUS.HR0286_dropGradient_p | Ramp Down | 2331 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Ramp Up | Inverter | Inverter050_MODBUS.HR0282_riseGradient_p | Ramp Up | 2332 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power Delivered | Inverter | Inverter050_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2333 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Reactive Power Delivered | Inverter | Inverter050_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2334 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power | 2335 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Reactive Power | Inverter | Inverter050_MODBUS.HR1009_q3_kvar | Reactive Power | 2336 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Reactive Power Mode | Inverter | Inverter050_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2337 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Reactive Power Set Point Percent | Inverter | Inverter050_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2338 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power AC Percent | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2339 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power-AC | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power-AC | 2340 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power-DC | Inverter | Inverter050_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2341 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Air Intake | Inverter | Inverter050_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2342 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Cabinet | Inverter | Inverter050_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2343 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-IGBT | Inverter | Inverter050_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2344 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Temperature-Module | Inverter | Inverter050_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2345 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage A-B | Inverter | Inverter050_MODBUS.HR1010_vRS_V | Voltage A-B | 2346 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage B-C | Inverter | Inverter050_MODBUS.HR1002_vST_V | Voltage B-C | 2347 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage C-A | Inverter | Inverter050_MODBUS.HR1003_vTR_V | Voltage C-A | 2348 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Voltage DC | Inverter | Inverter050_MODBUS.HR1051_vdcBus_V | Voltage DC | 2349 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV051 | Dagget 3_SUB1_INV051_A Phase Current | Inverter | Inverter051_MODBUS.HR1004_i1_A | A Phase Current | 2350 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_B Phase Current | Inverter | Inverter051_MODBUS.HR1005_i2_A | B Phase Current | 2351 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_C Phase Current | Inverter | Inverter051_MODBUS.HR1006_i3_A | C Phase Current | 2352 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Bus Voltage | Inverter | Inverter051_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2353 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV051 | Dagget 3_SUB1_INV051_Apparent Power | Inverter | Inverter051_MODBUS.HR1010_s3_VA | Apparent Power | 2354 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input1 | Inverter | Inverter051_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2355 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC Input 1 | Inverter | Inverter051_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2356 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input2 | Inverter | Inverter051_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2357 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC input 2 | Inverter | Inverter051_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2358 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input3 | Inverter | Inverter051_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2359 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC input 3 | Inverter | Inverter051_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2360 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input4 | Inverter | Inverter051_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2361 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC input 4 | Inverter | Inverter051_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2362 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input5 | Inverter | Inverter051_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2363 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC input 5 | Inverter | Inverter051_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2364 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current DC Input6 | Inverter | Inverter051_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2365 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC input 6 | Inverter | Inverter051_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2366 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current-AC | Inverter | Inverter051_MODBUS.HR1007_i3Avg_A | Current-AC | 2367 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Current-DC | Inverter | Inverter051_MODBUS.HR1062_idcInput_A | Current-DC | 2368 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Daily Energy Delivered | Inverter | Inverter051_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2369 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power Set Point | Inverter | Inverter051_MODBUS.HR0553_pRef | Real Power Set Point | 2370 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Reactive Power Set Point | Inverter | Inverter051_MODBUS.HR0558_qRef | Reactive Power Set Point | 2371 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Frequency | Inverter | Inverter051_MODBUS.HR1012_f3_Hz | Frequency | 2372 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV051 | Dagget 3_SUB1_INV051_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Insulation Resistance | Inverter | Inverter051_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2373 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Number of DU Channels | Inverter | Inverter051_MODBUS.HR0653_duChannels | Number of DU Channels | 2374 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Number of Running Modules | Inverter | Inverter051_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2375 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Operating State | Inverter | Inverter051_MODBUS.HR1123_currentStatus | Operating State | 2376 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Power Factor | Inverter | Inverter051_MODBUS.HR1011_pf3 | Power Factor | 2377 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV051 | Dagget 3_SUB1_INV051_Ramp Down | Inverter | Inverter051_MODBUS.HR0286_dropGradient_p | Ramp Down | 2378 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Ramp Up | Inverter | Inverter051_MODBUS.HR0282_riseGradient_p | Ramp Up | 2379 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power Delivered | Inverter | Inverter051_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2380 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Reactive Power Delivered | Inverter | Inverter051_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2381 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power | 2382 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Reactive Power | Inverter | Inverter051_MODBUS.HR1009_q3_kvar | Reactive Power | 2383 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Reactive Power Mode | Inverter | Inverter051_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2384 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Reactive Power Set Point Percent | Inverter | Inverter051_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2385 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power AC Percent | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2386 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power-AC | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power-AC | 2387 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power-DC | Inverter | Inverter051_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2388 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Air Intake | Inverter | Inverter051_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2389 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Cabinet | Inverter | Inverter051_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2390 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-IGBT | Inverter | Inverter051_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2391 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Temperature-Module | Inverter | Inverter051_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2392 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage A-B | Inverter | Inverter051_MODBUS.HR1001_vRS_V | Voltage A-B | 2393 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage B-C | Inverter | Inverter051_MODBUS.HR1002_vST_V | Voltage B-C | 2394 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage C-A | Inverter | Inverter051_MODBUS.HR1003_vTR_V | Voltage C-A | 2395 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Voltage DC | Inverter | Inverter051_MODBUS.HR1051_vdcBus_V | Voltage DC | 2396 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV052 | Dagget 3_SUB1_INV052_A Phase Current | Inverter | Inverter052_MODBUS.HR1004_i1_A | A Phase Current | 2397 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_B Phase Current | Inverter | Inverter052_MODBUS.HR1005_i2_A | B Phase Current | 2398 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_C Phase Current | Inverter | Inverter052_MODBUS.HR1006_i3_A | C Phase Current | 2399 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Bus Voltage | Inverter | Inverter052_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2400 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV052 | Dagget 3_SUB1_INV052_Apparent Power | Inverter | Inverter052_MODBUS.HR1010_s3_VA | Apparent Power | 2401 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input1 | Inverter | Inverter052_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2402 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC Input 1 | Inverter | Inverter052_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2403 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input2 | Inverter | Inverter052_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2404 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC input 2 | Inverter | Inverter052_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2405 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input3 | Inverter | Inverter052_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2406 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC input 3 | Inverter | Inverter052_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2407 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input4 | Inverter | Inverter052_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2408 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC input 4 | Inverter | Inverter052_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2409 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input5 | Inverter | Inverter052_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2410 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC input 5 | Inverter | Inverter052_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2411 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current DC Input6 | Inverter | Inverter052_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2412 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC input 6 | Inverter | Inverter052_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2413 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current-AC | Inverter | Inverter052_MODBUS.HR1007_i3Avg_A | Current-AC | 2414 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Current-DC | Inverter | Inverter052_MODBUS.HR1062_idcInput_A | Current-DC | 2415 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Daily Energy Delivered | Inverter | Inverter052_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2416 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power Set Point | Inverter | Inverter052_MODBUS.HR0553_pRef | Real Power Set Point | 2417 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Reactive Power Set Point | Inverter | Inverter052_MODBUS.HR0558_qRef | Reactive Power Set Point | 2418 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Frequency | Inverter | Inverter052_MODBUS.HR1012_f3_Hz | Frequency | 2419 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV052 | Dagget 3_SUB1_INV052_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Insulation Resistance | Inverter | Inverter052_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2420 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Number of DU Channels | Inverter | Inverter052_MODBUS.HR0653_duChannels | Number of DU Channels | 2421 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Number of Running Modules | Inverter | Inverter052_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2422 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Operating State | Inverter | Inverter052_MODBUS.HR1123_currentStatus | Operating State | 2423 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Power Factor | Inverter | Inverter052_MODBUS.HR1011_pf3 | Power Factor | 2424 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV052 | Dagget 3_SUB1_INV052_Ramp Down | Inverter | Inverter052_MODBUS.HR0286_dropGradient_p | Ramp Down | 2425 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Ramp Up | Inverter | Inverter052_MODBUS.HR0282_riseGradient_p | Ramp Up | 2426 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power Delivered | Inverter | Inverter052_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2427 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Reactive Power Delivered | Inverter | Inverter052_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2428 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power | 2429 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Reactive Power | Inverter | Inverter052_MODBUS.HR1009_q3_kvar | Reactive Power | 2430 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Reactive Power Mode | Inverter | Inverter052_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2431 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Reactive Power Set Point Percent | Inverter | Inverter052_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2432 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power AC Percent | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2433 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power-AC | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power-AC | 2434 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power-DC | Inverter | Inverter052_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2435 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Air Intake | Inverter | Inverter052_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2436 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Cabinet | Inverter | Inverter052_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2437 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-IGBT | Inverter | Inverter052_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2438 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Temperature-Module | Inverter | Inverter052_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2439 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage A-B | Inverter | Inverter052_MODBUS.HR1002_vRS_V | Voltage A-B | 2440 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage B-C | Inverter | Inverter052_MODBUS.HR1002_vST_V | Voltage B-C | 2441 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage C-A | Inverter | Inverter052_MODBUS.HR1003_vTR_V | Voltage C-A | 2442 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Voltage DC | Inverter | Inverter052_MODBUS.HR1051_vdcBus_V | Voltage DC | 2443 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV053 | Dagget 3_SUB1_INV053_A Phase Current | Inverter | Inverter053_MODBUS.HR1004_i1_A | A Phase Current | 2444 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_B Phase Current | Inverter | Inverter053_MODBUS.HR1005_i2_A | B Phase Current | 2445 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_C Phase Current | Inverter | Inverter053_MODBUS.HR1006_i3_A | C Phase Current | 2446 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Bus Voltage | Inverter | Inverter053_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2447 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV053 | Dagget 3_SUB1_INV053_Apparent Power | Inverter | Inverter053_MODBUS.HR1010_s3_VA | Apparent Power | 2448 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input1 | Inverter | Inverter053_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2449 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC Input 1 | Inverter | Inverter053_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2450 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input2 | Inverter | Inverter053_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2451 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC input 2 | Inverter | Inverter053_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2452 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input3 | Inverter | Inverter053_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2453 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC input 3 | Inverter | Inverter053_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2454 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input4 | Inverter | Inverter053_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2455 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC input 4 | Inverter | Inverter053_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2456 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input5 | Inverter | Inverter053_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2457 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC input 5 | Inverter | Inverter053_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2458 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current DC Input6 | Inverter | Inverter053_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2459 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC input 6 | Inverter | Inverter053_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2460 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current-AC | Inverter | Inverter053_MODBUS.HR1007_i3Avg_A | Current-AC | 2461 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Current-DC | Inverter | Inverter053_MODBUS.HR1062_idcInput_A | Current-DC | 2462 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Daily Energy Delivered | Inverter | Inverter053_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2463 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power Set Point | Inverter | Inverter053_MODBUS.HR0553_pRef | Real Power Set Point | 2464 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Reactive Power Set Point | Inverter | Inverter053_MODBUS.HR0558_qRef | Reactive Power Set Point | 2465 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Frequency | Inverter | Inverter053_MODBUS.HR1012_f3_Hz | Frequency | 2466 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV053 | Dagget 3_SUB1_INV053_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Insulation Resistance | Inverter | Inverter053_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2467 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Number of DU Channels | Inverter | Inverter053_MODBUS.HR0653_duChannels | Number of DU Channels | 2468 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Number of Running Modules | Inverter | Inverter053_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2469 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Operating State | Inverter | Inverter053_MODBUS.HR1123_currentStatus | Operating State | 2470 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Power Factor | Inverter | Inverter053_MODBUS.HR1011_pf3 | Power Factor | 2471 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV053 | Dagget 3_SUB1_INV053_Ramp Down | Inverter | Inverter053_MODBUS.HR0286_dropGradient_p | Ramp Down | 2472 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Ramp Up | Inverter | Inverter053_MODBUS.HR0282_riseGradient_p | Ramp Up | 2473 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power Delivered | Inverter | Inverter053_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2474 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Reactive Power Delivered | Inverter | Inverter053_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2475 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power | 2476 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Reactive Power | Inverter | Inverter053_MODBUS.HR1009_q3_kvar | Reactive Power | 2477 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Reactive Power Mode | Inverter | Inverter053_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2478 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Reactive Power Set Point Percent | Inverter | Inverter053_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2479 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power AC Percent | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2480 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power-AC | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power-AC | 2481 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power-DC | Inverter | Inverter053_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2482 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Air Intake | Inverter | Inverter053_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2483 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Cabinet | Inverter | Inverter053_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2484 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-IGBT | Inverter | Inverter053_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2485 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Temperature-Module | Inverter | Inverter053_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2486 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage A-B | Inverter | Inverter053_MODBUS.HR1003_vRS_V | Voltage A-B | 2487 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage B-C | Inverter | Inverter053_MODBUS.HR1002_vST_V | Voltage B-C | 2488 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage C-A | Inverter | Inverter053_MODBUS.HR1003_vTR_V | Voltage C-A | 2489 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Voltage DC | Inverter | Inverter053_MODBUS.HR1051_vdcBus_V | Voltage DC | 2490 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV054 | Dagget 3_SUB1_INV054_A Phase Current | Inverter | Inverter054_MODBUS.HR1004_i1_A | A Phase Current | 2491 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_B Phase Current | Inverter | Inverter054_MODBUS.HR1005_i2_A | B Phase Current | 2492 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_C Phase Current | Inverter | Inverter054_MODBUS.HR1006_i3_A | C Phase Current | 2493 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Bus Voltage | Inverter | Inverter054_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2494 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV054 | Dagget 3_SUB1_INV054_Apparent Power | Inverter | Inverter054_MODBUS.HR1010_s3_VA | Apparent Power | 2495 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input1 | Inverter | Inverter054_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2496 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC Input 1 | Inverter | Inverter054_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2497 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input2 | Inverter | Inverter054_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2498 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC input 2 | Inverter | Inverter054_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2499 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input3 | Inverter | Inverter054_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2500 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC input 3 | Inverter | Inverter054_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2501 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input4 | Inverter | Inverter054_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2502 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC input 4 | Inverter | Inverter054_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2503 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input5 | Inverter | Inverter054_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2504 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC input 5 | Inverter | Inverter054_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2505 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current DC Input6 | Inverter | Inverter054_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2506 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC input 6 | Inverter | Inverter054_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2507 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current-AC | Inverter | Inverter054_MODBUS.HR1007_i3Avg_A | Current-AC | 2508 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Current-DC | Inverter | Inverter054_MODBUS.HR1062_idcInput_A | Current-DC | 2509 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Daily Energy Delivered | Inverter | Inverter054_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2510 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power Set Point | Inverter | Inverter054_MODBUS.HR0553_pRef | Real Power Set Point | 2511 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Reactive Power Set Point | Inverter | Inverter054_MODBUS.HR0558_qRef | Reactive Power Set Point | 2512 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Frequency | Inverter | Inverter054_MODBUS.HR1012_f3_Hz | Frequency | 2513 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV054 | Dagget 3_SUB1_INV054_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Insulation Resistance | Inverter | Inverter054_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2514 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Number of DU Channels | Inverter | Inverter054_MODBUS.HR0653_duChannels | Number of DU Channels | 2515 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Number of Running Modules | Inverter | Inverter054_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2516 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Operating State | Inverter | Inverter054_MODBUS.HR1123_currentStatus | Operating State | 2517 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Power Factor | Inverter | Inverter054_MODBUS.HR1011_pf3 | Power Factor | 2518 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV054 | Dagget 3_SUB1_INV054_Ramp Down | Inverter | Inverter054_MODBUS.HR0286_dropGradient_p | Ramp Down | 2519 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Ramp Up | Inverter | Inverter054_MODBUS.HR0282_riseGradient_p | Ramp Up | 2520 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power Delivered | Inverter | Inverter054_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2521 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Reactive Power Delivered | Inverter | Inverter054_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2522 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power | 2523 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Reactive Power | Inverter | Inverter054_MODBUS.HR1009_q3_kvar | Reactive Power | 2524 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Reactive Power Mode | Inverter | Inverter054_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2525 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Reactive Power Set Point Percent | Inverter | Inverter054_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2526 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power AC Percent | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2527 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power-AC | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power-AC | 2528 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power-DC | Inverter | Inverter054_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2529 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Air Intake | Inverter | Inverter054_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2530 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Cabinet | Inverter | Inverter054_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2531 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-IGBT | Inverter | Inverter054_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2532 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Temperature-Module | Inverter | Inverter054_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2533 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage A-B | Inverter | Inverter054_MODBUS.HR1004_vRS_V | Voltage A-B | 2534 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage B-C | Inverter | Inverter054_MODBUS.HR1002_vST_V | Voltage B-C | 2535 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage C-A | Inverter | Inverter054_MODBUS.HR1003_vTR_V | Voltage C-A | 2536 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Voltage DC | Inverter | Inverter054_MODBUS.HR1051_vdcBus_V | Voltage DC | 2537 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV055 | Dagget 3_SUB1_INV055_A Phase Current | Inverter | Inverter055_MODBUS.HR1004_i1_A | A Phase Current | 2538 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_B Phase Current | Inverter | Inverter055_MODBUS.HR1005_i2_A | B Phase Current | 2539 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_C Phase Current | Inverter | Inverter055_MODBUS.HR1006_i3_A | C Phase Current | 2540 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Bus Voltage | Inverter | Inverter055_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2541 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV055 | Dagget 3_SUB1_INV055_Apparent Power | Inverter | Inverter055_MODBUS.HR1010_s3_VA | Apparent Power | 2542 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input1 | Inverter | Inverter055_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2543 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC Input 1 | Inverter | Inverter055_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2544 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input2 | Inverter | Inverter055_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2545 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC input 2 | Inverter | Inverter055_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2546 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input3 | Inverter | Inverter055_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2547 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC input 3 | Inverter | Inverter055_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2548 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input4 | Inverter | Inverter055_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2549 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC input 4 | Inverter | Inverter055_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2550 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input5 | Inverter | Inverter055_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2551 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC input 5 | Inverter | Inverter055_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2552 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current DC Input6 | Inverter | Inverter055_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2553 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC input 6 | Inverter | Inverter055_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2554 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current-AC | Inverter | Inverter055_MODBUS.HR1007_i3Avg_A | Current-AC | 2555 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Current-DC | Inverter | Inverter055_MODBUS.HR1062_idcInput_A | Current-DC | 2556 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Daily Energy Delivered | Inverter | Inverter055_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2557 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power Set Point | Inverter | Inverter055_MODBUS.HR0553_pRef | Real Power Set Point | 2558 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Reactive Power Set Point | Inverter | Inverter055_MODBUS.HR0558_qRef | Reactive Power Set Point | 2559 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Frequency | Inverter | Inverter055_MODBUS.HR1012_f3_Hz | Frequency | 2560 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV055 | Dagget 3_SUB1_INV055_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Insulation Resistance | Inverter | Inverter055_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2561 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Number of DU Channels | Inverter | Inverter055_MODBUS.HR0653_duChannels | Number of DU Channels | 2562 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Number of Running Modules | Inverter | Inverter055_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2563 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Operating State | Inverter | Inverter055_MODBUS.HR1123_currentStatus | Operating State | 2564 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Power Factor | Inverter | Inverter055_MODBUS.HR1011_pf3 | Power Factor | 2565 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV055 | Dagget 3_SUB1_INV055_Ramp Down | Inverter | Inverter055_MODBUS.HR0286_dropGradient_p | Ramp Down | 2566 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Ramp Up | Inverter | Inverter055_MODBUS.HR0282_riseGradient_p | Ramp Up | 2567 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power Delivered | Inverter | Inverter055_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2568 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Reactive Power Delivered | Inverter | Inverter055_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2569 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power | 2570 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Reactive Power | Inverter | Inverter055_MODBUS.HR1009_q3_kvar | Reactive Power | 2571 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Reactive Power Mode | Inverter | Inverter055_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2572 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Reactive Power Set Point Percent | Inverter | Inverter055_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2573 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power AC Percent | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2574 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power-AC | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power-AC | 2575 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power-DC | Inverter | Inverter055_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2576 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Air Intake | Inverter | Inverter055_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2577 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Cabinet | Inverter | Inverter055_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2578 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-IGBT | Inverter | Inverter055_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2579 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Temperature-Module | Inverter | Inverter055_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2580 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage A-B | Inverter | Inverter055_MODBUS.HR1005_vRS_V | Voltage A-B | 2581 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage B-C | Inverter | Inverter055_MODBUS.HR1002_vST_V | Voltage B-C | 2582 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage C-A | Inverter | Inverter055_MODBUS.HR1003_vTR_V | Voltage C-A | 2583 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Voltage DC | Inverter | Inverter055_MODBUS.HR1051_vdcBus_V | Voltage DC | 2584 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV056 | Dagget 3_SUB1_INV056_A Phase Current | Inverter | Inverter056_MODBUS.HR1004_i1_A | A Phase Current | 2585 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_B Phase Current | Inverter | Inverter056_MODBUS.HR1005_i2_A | B Phase Current | 2586 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_C Phase Current | Inverter | Inverter056_MODBUS.HR1006_i3_A | C Phase Current | 2587 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Bus Voltage | Inverter | Inverter056_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2588 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV056 | Dagget 3_SUB1_INV056_Apparent Power | Inverter | Inverter056_MODBUS.HR1010_s3_VA | Apparent Power | 2589 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input1 | Inverter | Inverter056_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2590 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC Input 1 | Inverter | Inverter056_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2591 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input2 | Inverter | Inverter056_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2592 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC input 2 | Inverter | Inverter056_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2593 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input3 | Inverter | Inverter056_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2594 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC input 3 | Inverter | Inverter056_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2595 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input4 | Inverter | Inverter056_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2596 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC input 4 | Inverter | Inverter056_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2597 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input5 | Inverter | Inverter056_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2598 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC input 5 | Inverter | Inverter056_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2599 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current DC Input6 | Inverter | Inverter056_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2600 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC input 6 | Inverter | Inverter056_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2601 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current-AC | Inverter | Inverter056_MODBUS.HR1007_i3Avg_A | Current-AC | 2602 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Current-DC | Inverter | Inverter056_MODBUS.HR1062_idcInput_A | Current-DC | 2603 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Daily Energy Delivered | Inverter | Inverter056_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2604 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power Set Point | Inverter | Inverter056_MODBUS.HR0553_pRef | Real Power Set Point | 2605 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Reactive Power Set Point | Inverter | Inverter056_MODBUS.HR0558_qRef | Reactive Power Set Point | 2606 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Frequency | Inverter | Inverter056_MODBUS.HR1012_f3_Hz | Frequency | 2607 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV056 | Dagget 3_SUB1_INV056_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Insulation Resistance | Inverter | Inverter056_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2608 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Number of DU Channels | Inverter | Inverter056_MODBUS.HR0653_duChannels | Number of DU Channels | 2609 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Number of Running Modules | Inverter | Inverter056_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2610 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Operating State | Inverter | Inverter056_MODBUS.HR1123_currentStatus | Operating State | 2611 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Power Factor | Inverter | Inverter056_MODBUS.HR1011_pf3 | Power Factor | 2612 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV056 | Dagget 3_SUB1_INV056_Ramp Down | Inverter | Inverter056_MODBUS.HR0286_dropGradient_p | Ramp Down | 2613 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Ramp Up | Inverter | Inverter056_MODBUS.HR0282_riseGradient_p | Ramp Up | 2614 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power Delivered | Inverter | Inverter056_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2615 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Reactive Power Delivered | Inverter | Inverter056_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2616 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power | 2617 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Reactive Power | Inverter | Inverter056_MODBUS.HR1009_q3_kvar | Reactive Power | 2618 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Reactive Power Mode | Inverter | Inverter056_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2619 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Reactive Power Set Point Percent | Inverter | Inverter056_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2620 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power AC Percent | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2621 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power-AC | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power-AC | 2622 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power-DC | Inverter | Inverter056_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2623 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Air Intake | Inverter | Inverter056_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2624 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Cabinet | Inverter | Inverter056_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2625 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-IGBT | Inverter | Inverter056_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2626 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Temperature-Module | Inverter | Inverter056_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2627 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage A-B | Inverter | Inverter056_MODBUS.HR1006_vRS_V | Voltage A-B | 2628 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage B-C | Inverter | Inverter056_MODBUS.HR1002_vST_V | Voltage B-C | 2629 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage C-A | Inverter | Inverter056_MODBUS.HR1003_vTR_V | Voltage C-A | 2630 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Voltage DC | Inverter | Inverter056_MODBUS.HR1051_vdcBus_V | Voltage DC | 2631 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV057 | Dagget 3_SUB1_INV057_A Phase Current | Inverter | Inverter057_MODBUS.HR1004_i1_A | A Phase Current | 2632 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_B Phase Current | Inverter | Inverter057_MODBUS.HR1005_i2_A | B Phase Current | 2633 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_C Phase Current | Inverter | Inverter057_MODBUS.HR1006_i3_A | C Phase Current | 2634 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Bus Voltage | Inverter | Inverter057_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2635 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV057 | Dagget 3_SUB1_INV057_Apparent Power | Inverter | Inverter057_MODBUS.HR1010_s3_VA | Apparent Power | 2636 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input1 | Inverter | Inverter057_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2637 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC Input 1 | Inverter | Inverter057_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2638 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input2 | Inverter | Inverter057_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2639 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC input 2 | Inverter | Inverter057_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2640 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input3 | Inverter | Inverter057_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2641 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC input 3 | Inverter | Inverter057_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2642 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input4 | Inverter | Inverter057_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2643 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC input 4 | Inverter | Inverter057_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2644 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input5 | Inverter | Inverter057_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2645 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC input 5 | Inverter | Inverter057_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2646 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current DC Input6 | Inverter | Inverter057_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2647 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC input 6 | Inverter | Inverter057_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2648 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current-AC | Inverter | Inverter057_MODBUS.HR1007_i3Avg_A | Current-AC | 2649 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Current-DC | Inverter | Inverter057_MODBUS.HR1062_idcInput_A | Current-DC | 2650 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Daily Energy Delivered | Inverter | Inverter057_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2651 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power Set Point | Inverter | Inverter057_MODBUS.HR0553_pRef | Real Power Set Point | 2652 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Reactive Power Set Point | Inverter | Inverter057_MODBUS.HR0558_qRef | Reactive Power Set Point | 2653 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Frequency | Inverter | Inverter057_MODBUS.HR1012_f3_Hz | Frequency | 2654 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV057 | Dagget 3_SUB1_INV057_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Insulation Resistance | Inverter | Inverter057_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2655 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Number of DU Channels | Inverter | Inverter057_MODBUS.HR0653_duChannels | Number of DU Channels | 2656 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Number of Running Modules | Inverter | Inverter057_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2657 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Operating State | Inverter | Inverter057_MODBUS.HR1123_currentStatus | Operating State | 2658 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Power Factor | Inverter | Inverter057_MODBUS.HR1011_pf3 | Power Factor | 2659 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV057 | Dagget 3_SUB1_INV057_Ramp Down | Inverter | Inverter057_MODBUS.HR0286_dropGradient_p | Ramp Down | 2660 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Ramp Up | Inverter | Inverter057_MODBUS.HR0282_riseGradient_p | Ramp Up | 2661 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power Delivered | Inverter | Inverter057_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2662 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Reactive Power Delivered | Inverter | Inverter057_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2663 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power | 2664 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Reactive Power | Inverter | Inverter057_MODBUS.HR1009_q3_kvar | Reactive Power | 2665 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Reactive Power Mode | Inverter | Inverter057_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2666 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Reactive Power Set Point Percent | Inverter | Inverter057_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2667 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power AC Percent | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2668 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power-AC | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power-AC | 2669 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power-DC | Inverter | Inverter057_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2670 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Air Intake | Inverter | Inverter057_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2671 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Cabinet | Inverter | Inverter057_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2672 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-IGBT | Inverter | Inverter057_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2673 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Temperature-Module | Inverter | Inverter057_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2674 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage A-B | Inverter | Inverter057_MODBUS.HR1007_vRS_V | Voltage A-B | 2675 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage B-C | Inverter | Inverter057_MODBUS.HR1002_vST_V | Voltage B-C | 2676 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage C-A | Inverter | Inverter057_MODBUS.HR1003_vTR_V | Voltage C-A | 2677 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Voltage DC | Inverter | Inverter057_MODBUS.HR1051_vdcBus_V | Voltage DC | 2678 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV058 | Dagget 3_SUB1_INV058_A Phase Current | Inverter | Inverter058_MODBUS.HR1004_i1_A | A Phase Current | 2679 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_B Phase Current | Inverter | Inverter058_MODBUS.HR1005_i2_A | B Phase Current | 2680 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_C Phase Current | Inverter | Inverter058_MODBUS.HR1006_i3_A | C Phase Current | 2681 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Bus Voltage | Inverter | Inverter058_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2682 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV058 | Dagget 3_SUB1_INV058_Apparent Power | Inverter | Inverter058_MODBUS.HR1010_s3_VA | Apparent Power | 2683 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input1 | Inverter | Inverter058_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2684 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC Input 1 | Inverter | Inverter058_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2685 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input2 | Inverter | Inverter058_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2686 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC input 2 | Inverter | Inverter058_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2687 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input3 | Inverter | Inverter058_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2688 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC input 3 | Inverter | Inverter058_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2689 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input4 | Inverter | Inverter058_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2690 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC input 4 | Inverter | Inverter058_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2691 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input5 | Inverter | Inverter058_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2692 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC input 5 | Inverter | Inverter058_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2693 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current DC Input6 | Inverter | Inverter058_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2694 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC input 6 | Inverter | Inverter058_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2695 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current-AC | Inverter | Inverter058_MODBUS.HR1007_i3Avg_A | Current-AC | 2696 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Current-DC | Inverter | Inverter058_MODBUS.HR1062_idcInput_A | Current-DC | 2697 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Daily Energy Delivered | Inverter | Inverter058_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2698 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power Set Point | Inverter | Inverter058_MODBUS.HR0553_pRef | Real Power Set Point | 2699 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Reactive Power Set Point | Inverter | Inverter058_MODBUS.HR0558_qRef | Reactive Power Set Point | 2700 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Frequency | Inverter | Inverter058_MODBUS.HR1012_f3_Hz | Frequency | 2701 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV058 | Dagget 3_SUB1_INV058_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Insulation Resistance | Inverter | Inverter058_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2702 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Number of DU Channels | Inverter | Inverter058_MODBUS.HR0653_duChannels | Number of DU Channels | 2703 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Number of Running Modules | Inverter | Inverter058_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2704 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Operating State | Inverter | Inverter058_MODBUS.HR1123_currentStatus | Operating State | 2705 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Power Factor | Inverter | Inverter058_MODBUS.HR1011_pf3 | Power Factor | 2706 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV058 | Dagget 3_SUB1_INV058_Ramp Down | Inverter | Inverter058_MODBUS.HR0286_dropGradient_p | Ramp Down | 2707 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Ramp Up | Inverter | Inverter058_MODBUS.HR0282_riseGradient_p | Ramp Up | 2708 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power Delivered | Inverter | Inverter058_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2709 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Reactive Power Delivered | Inverter | Inverter058_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2710 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power | 2711 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Reactive Power | Inverter | Inverter058_MODBUS.HR1009_q3_kvar | Reactive Power | 2712 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Reactive Power Mode | Inverter | Inverter058_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2713 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Reactive Power Set Point Percent | Inverter | Inverter058_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2714 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power AC Percent | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2715 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power-AC | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power-AC | 2716 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power-DC | Inverter | Inverter058_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2717 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Air Intake | Inverter | Inverter058_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2718 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Cabinet | Inverter | Inverter058_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2719 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-IGBT | Inverter | Inverter058_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2720 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Temperature-Module | Inverter | Inverter058_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2721 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage A-B | Inverter | Inverter058_MODBUS.HR1008_vRS_V | Voltage A-B | 2722 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage B-C | Inverter | Inverter058_MODBUS.HR1002_vST_V | Voltage B-C | 2723 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage C-A | Inverter | Inverter058_MODBUS.HR1003_vTR_V | Voltage C-A | 2724 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Voltage DC | Inverter | Inverter058_MODBUS.HR1051_vdcBus_V | Voltage DC | 2725 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV059 | Dagget 3_SUB1_INV059_A Phase Current | Inverter | Inverter059_MODBUS.HR1004_i1_A | A Phase Current | 2726 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_B Phase Current | Inverter | Inverter059_MODBUS.HR1005_i2_A | B Phase Current | 2727 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_C Phase Current | Inverter | Inverter059_MODBUS.HR1006_i3_A | C Phase Current | 2728 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Bus Voltage | Inverter | Inverter059_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2729 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV059 | Dagget 3_SUB1_INV059_Apparent Power | Inverter | Inverter059_MODBUS.HR1010_s3_VA | Apparent Power | 2730 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input1 | Inverter | Inverter059_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2731 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC Input 1 | Inverter | Inverter059_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2732 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input2 | Inverter | Inverter059_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2733 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC input 2 | Inverter | Inverter059_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2734 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input3 | Inverter | Inverter059_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2735 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC input 3 | Inverter | Inverter059_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2736 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input4 | Inverter | Inverter059_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2737 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC input 4 | Inverter | Inverter059_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2738 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input5 | Inverter | Inverter059_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2739 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC input 5 | Inverter | Inverter059_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2740 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current DC Input6 | Inverter | Inverter059_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2741 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC input 6 | Inverter | Inverter059_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2742 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current-AC | Inverter | Inverter059_MODBUS.HR1007_i3Avg_A | Current-AC | 2743 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Current-DC | Inverter | Inverter059_MODBUS.HR1062_idcInput_A | Current-DC | 2744 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Daily Energy Delivered | Inverter | Inverter059_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2745 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power Set Point | Inverter | Inverter059_MODBUS.HR0553_pRef | Real Power Set Point | 2746 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Reactive Power Set Point | Inverter | Inverter059_MODBUS.HR0558_qRef | Reactive Power Set Point | 2747 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Frequency | Inverter | Inverter059_MODBUS.HR1012_f3_Hz | Frequency | 2748 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV059 | Dagget 3_SUB1_INV059_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Insulation Resistance | Inverter | Inverter059_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2749 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Number of DU Channels | Inverter | Inverter059_MODBUS.HR0653_duChannels | Number of DU Channels | 2750 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Number of Running Modules | Inverter | Inverter059_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2751 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Operating State | Inverter | Inverter059_MODBUS.HR1123_currentStatus | Operating State | 2752 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Power Factor | Inverter | Inverter059_MODBUS.HR1011_pf3 | Power Factor | 2753 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV059 | Dagget 3_SUB1_INV059_Ramp Down | Inverter | Inverter059_MODBUS.HR0286_dropGradient_p | Ramp Down | 2754 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Ramp Up | Inverter | Inverter059_MODBUS.HR0282_riseGradient_p | Ramp Up | 2755 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power Delivered | Inverter | Inverter059_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2756 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Reactive Power Delivered | Inverter | Inverter059_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2757 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power | 2758 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Reactive Power | Inverter | Inverter059_MODBUS.HR1009_q3_kvar | Reactive Power | 2759 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Reactive Power Mode | Inverter | Inverter059_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2760 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Reactive Power Set Point Percent | Inverter | Inverter059_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2761 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power AC Percent | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2762 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power-AC | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power-AC | 2763 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power-DC | Inverter | Inverter059_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2764 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Air Intake | Inverter | Inverter059_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2765 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Cabinet | Inverter | Inverter059_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2766 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-IGBT | Inverter | Inverter059_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2767 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Temperature-Module | Inverter | Inverter059_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2768 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage A-B | Inverter | Inverter059_MODBUS.HR1009_vRS_V | Voltage A-B | 2769 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage B-C | Inverter | Inverter059_MODBUS.HR1002_vST_V | Voltage B-C | 2770 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage C-A | Inverter | Inverter059_MODBUS.HR1003_vTR_V | Voltage C-A | 2771 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Voltage DC | Inverter | Inverter059_MODBUS.HR1051_vdcBus_V | Voltage DC | 2772 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV060 | Dagget 3_SUB1_INV060_A Phase Current | Inverter | Inverter060_MODBUS.HR1004_i1_A | A Phase Current | 2773 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_B Phase Current | Inverter | Inverter060_MODBUS.HR1005_i2_A | B Phase Current | 2774 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_C Phase Current | Inverter | Inverter060_MODBUS.HR1006_i3_A | C Phase Current | 2775 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Bus Voltage | Inverter | Inverter060_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2776 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV060 | Dagget 3_SUB1_INV060_Apparent Power | Inverter | Inverter060_MODBUS.HR1010_s3_VA | Apparent Power | 2777 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input1 | Inverter | Inverter060_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2778 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC Input 1 | Inverter | Inverter060_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2779 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input2 | Inverter | Inverter060_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2780 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC input 2 | Inverter | Inverter060_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2781 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input3 | Inverter | Inverter060_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2782 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC input 3 | Inverter | Inverter060_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2783 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input4 | Inverter | Inverter060_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2784 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC input 4 | Inverter | Inverter060_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2785 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input5 | Inverter | Inverter060_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2786 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC input 5 | Inverter | Inverter060_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2787 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current DC Input6 | Inverter | Inverter060_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2788 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC input 6 | Inverter | Inverter060_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2789 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current-AC | Inverter | Inverter060_MODBUS.HR1007_i3Avg_A | Current-AC | 2790 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Current-DC | Inverter | Inverter060_MODBUS.HR1062_idcInput_A | Current-DC | 2791 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Daily Energy Delivered | Inverter | Inverter060_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2792 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power Set Point | Inverter | Inverter060_MODBUS.HR0553_pRef | Real Power Set Point | 2793 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Reactive Power Set Point | Inverter | Inverter060_MODBUS.HR0558_qRef | Reactive Power Set Point | 2794 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Frequency | Inverter | Inverter060_MODBUS.HR1012_f3_Hz | Frequency | 2795 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV060 | Dagget 3_SUB1_INV060_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Insulation Resistance | Inverter | Inverter060_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2796 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Number of DU Channels | Inverter | Inverter060_MODBUS.HR0653_duChannels | Number of DU Channels | 2797 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Number of Running Modules | Inverter | Inverter060_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2798 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Operating State | Inverter | Inverter060_MODBUS.HR1123_currentStatus | Operating State | 2799 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Power Factor | Inverter | Inverter060_MODBUS.HR1011_pf3 | Power Factor | 2800 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV060 | Dagget 3_SUB1_INV060_Ramp Down | Inverter | Inverter060_MODBUS.HR0286_dropGradient_p | Ramp Down | 2801 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Ramp Up | Inverter | Inverter060_MODBUS.HR0282_riseGradient_p | Ramp Up | 2802 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power Delivered | Inverter | Inverter060_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2803 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Reactive Power Delivered | Inverter | Inverter060_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2804 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power | 2805 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Reactive Power | Inverter | Inverter060_MODBUS.HR1009_q3_kvar | Reactive Power | 2806 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Reactive Power Mode | Inverter | Inverter060_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2807 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Reactive Power Set Point Percent | Inverter | Inverter060_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2808 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power AC Percent | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2809 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power-AC | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power-AC | 2810 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power-DC | Inverter | Inverter060_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2811 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Air Intake | Inverter | Inverter060_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2812 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Cabinet | Inverter | Inverter060_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2813 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-IGBT | Inverter | Inverter060_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2814 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Temperature-Module | Inverter | Inverter060_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2815 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage A-B | Inverter | Inverter060_MODBUS.HR1010_vRS_V | Voltage A-B | 2816 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage B-C | Inverter | Inverter060_MODBUS.HR1002_vST_V | Voltage B-C | 2817 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage C-A | Inverter | Inverter060_MODBUS.HR1003_vTR_V | Voltage C-A | 2818 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Voltage DC | Inverter | Inverter060_MODBUS.HR1051_vdcBus_V | Voltage DC | 2819 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV061 | Dagget 3_SUB1_INV061_A Phase Current | Inverter | Inverter061_MODBUS.HR1004_i1_A | A Phase Current | 2820 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_B Phase Current | Inverter | Inverter061_MODBUS.HR1005_i2_A | B Phase Current | 2821 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_C Phase Current | Inverter | Inverter061_MODBUS.HR1006_i3_A | C Phase Current | 2822 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Bus Voltage | Inverter | Inverter061_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2823 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV061 | Dagget 3_SUB1_INV061_Apparent Power | Inverter | Inverter061_MODBUS.HR1010_s3_VA | Apparent Power | 2824 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input1 | Inverter | Inverter061_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2825 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC Input 1 | Inverter | Inverter061_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2826 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input2 | Inverter | Inverter061_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2827 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC input 2 | Inverter | Inverter061_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2828 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input3 | Inverter | Inverter061_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2829 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC input 3 | Inverter | Inverter061_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2830 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input4 | Inverter | Inverter061_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2831 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC input 4 | Inverter | Inverter061_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2832 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input5 | Inverter | Inverter061_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2833 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC input 5 | Inverter | Inverter061_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2834 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current DC Input6 | Inverter | Inverter061_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2835 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC input 6 | Inverter | Inverter061_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2836 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current-AC | Inverter | Inverter061_MODBUS.HR1007_i3Avg_A | Current-AC | 2837 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Current-DC | Inverter | Inverter061_MODBUS.HR1062_idcInput_A | Current-DC | 2838 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Daily Energy Delivered | Inverter | Inverter061_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2839 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power Set Point | Inverter | Inverter061_MODBUS.HR0553_pRef | Real Power Set Point | 2840 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Reactive Power Set Point | Inverter | Inverter061_MODBUS.HR0558_qRef | Reactive Power Set Point | 2841 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Frequency | Inverter | Inverter061_MODBUS.HR1012_f3_Hz | Frequency | 2842 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV061 | Dagget 3_SUB1_INV061_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Insulation Resistance | Inverter | Inverter061_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2843 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Number of DU Channels | Inverter | Inverter061_MODBUS.HR0653_duChannels | Number of DU Channels | 2844 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Number of Running Modules | Inverter | Inverter061_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2845 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Operating State | Inverter | Inverter061_MODBUS.HR1123_currentStatus | Operating State | 2846 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Power Factor | Inverter | Inverter061_MODBUS.HR1011_pf3 | Power Factor | 2847 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV061 | Dagget 3_SUB1_INV061_Ramp Down | Inverter | Inverter061_MODBUS.HR0286_dropGradient_p | Ramp Down | 2848 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Ramp Up | Inverter | Inverter061_MODBUS.HR0282_riseGradient_p | Ramp Up | 2849 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power Delivered | Inverter | Inverter061_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2850 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Reactive Power Delivered | Inverter | Inverter061_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2851 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power | 2852 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Reactive Power | Inverter | Inverter061_MODBUS.HR1009_q3_kvar | Reactive Power | 2853 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Reactive Power Mode | Inverter | Inverter061_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2854 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Reactive Power Set Point Percent | Inverter | Inverter061_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2855 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power AC Percent | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2856 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power-AC | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power-AC | 2857 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power-DC | Inverter | Inverter061_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2858 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Air Intake | Inverter | Inverter061_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2859 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Cabinet | Inverter | Inverter061_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2860 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-IGBT | Inverter | Inverter061_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2861 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Temperature-Module | Inverter | Inverter061_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2862 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage A-B | Inverter | Inverter061_MODBUS.HR1001_vRS_V | Voltage A-B | 2863 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage B-C | Inverter | Inverter061_MODBUS.HR1002_vST_V | Voltage B-C | 2864 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage C-A | Inverter | Inverter061_MODBUS.HR1003_vTR_V | Voltage C-A | 2865 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Voltage DC | Inverter | Inverter061_MODBUS.HR1051_vdcBus_V | Voltage DC | 2866 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV062 | Dagget 3_SUB1_INV062_A Phase Current | Inverter | Inverter062_MODBUS.HR1004_i1_A | A Phase Current | 2867 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_B Phase Current | Inverter | Inverter062_MODBUS.HR1005_i2_A | B Phase Current | 2868 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_C Phase Current | Inverter | Inverter062_MODBUS.HR1006_i3_A | C Phase Current | 2869 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Bus Voltage | Inverter | Inverter062_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2870 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV062 | Dagget 3_SUB1_INV062_Apparent Power | Inverter | Inverter062_MODBUS.HR1010_s3_VA | Apparent Power | 2871 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input1 | Inverter | Inverter062_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2872 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC Input 1 | Inverter | Inverter062_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2873 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input2 | Inverter | Inverter062_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2874 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC input 2 | Inverter | Inverter062_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2875 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input3 | Inverter | Inverter062_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2876 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC input 3 | Inverter | Inverter062_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2877 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input4 | Inverter | Inverter062_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2878 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC input 4 | Inverter | Inverter062_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2879 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input5 | Inverter | Inverter062_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2880 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC input 5 | Inverter | Inverter062_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2881 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current DC Input6 | Inverter | Inverter062_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2882 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC input 6 | Inverter | Inverter062_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2883 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current-AC | Inverter | Inverter062_MODBUS.HR1007_i3Avg_A | Current-AC | 2884 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Current-DC | Inverter | Inverter062_MODBUS.HR1062_idcInput_A | Current-DC | 2885 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Daily Energy Delivered | Inverter | Inverter062_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2886 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power Set Point | Inverter | Inverter062_MODBUS.HR0553_pRef | Real Power Set Point | 2887 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Reactive Power Set Point | Inverter | Inverter062_MODBUS.HR0558_qRef | Reactive Power Set Point | 2888 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Frequency | Inverter | Inverter062_MODBUS.HR1012_f3_Hz | Frequency | 2889 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV062 | Dagget 3_SUB1_INV062_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Insulation Resistance | Inverter | Inverter062_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2890 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Number of DU Channels | Inverter | Inverter062_MODBUS.HR0653_duChannels | Number of DU Channels | 2891 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Number of Running Modules | Inverter | Inverter062_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2892 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Operating State | Inverter | Inverter062_MODBUS.HR1123_currentStatus | Operating State | 2893 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Power Factor | Inverter | Inverter062_MODBUS.HR1011_pf3 | Power Factor | 2894 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV062 | Dagget 3_SUB1_INV062_Ramp Down | Inverter | Inverter062_MODBUS.HR0286_dropGradient_p | Ramp Down | 2895 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Ramp Up | Inverter | Inverter062_MODBUS.HR0282_riseGradient_p | Ramp Up | 2896 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power Delivered | Inverter | Inverter062_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2897 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Reactive Power Delivered | Inverter | Inverter062_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2898 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power | 2899 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Reactive Power | Inverter | Inverter062_MODBUS.HR1009_q3_kvar | Reactive Power | 2900 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Reactive Power Mode | Inverter | Inverter062_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2901 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Reactive Power Set Point Percent | Inverter | Inverter062_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2902 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power AC Percent | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2903 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power-AC | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power-AC | 2904 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power-DC | Inverter | Inverter062_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2905 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Air Intake | Inverter | Inverter062_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2906 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Cabinet | Inverter | Inverter062_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2907 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-IGBT | Inverter | Inverter062_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2908 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Temperature-Module | Inverter | Inverter062_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2909 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage A-B | Inverter | Inverter062_MODBUS.HR1002_vRS_V | Voltage A-B | 2910 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage B-C | Inverter | Inverter062_MODBUS.HR1002_vST_V | Voltage B-C | 2911 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage C-A | Inverter | Inverter062_MODBUS.HR1003_vTR_V | Voltage C-A | 2912 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Voltage DC | Inverter | Inverter062_MODBUS.HR1051_vdcBus_V | Voltage DC | 2913 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV063 | Dagget 3_SUB1_INV063_A Phase Current | Inverter | Inverter063_MODBUS.HR1004_i1_A | A Phase Current | 2914 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_B Phase Current | Inverter | Inverter063_MODBUS.HR1005_i2_A | B Phase Current | 2915 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_C Phase Current | Inverter | Inverter063_MODBUS.HR1006_i3_A | C Phase Current | 2916 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Bus Voltage | Inverter | Inverter063_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2917 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV063 | Dagget 3_SUB1_INV063_Apparent Power | Inverter | Inverter063_MODBUS.HR1010_s3_VA | Apparent Power | 2918 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input1 | Inverter | Inverter063_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2919 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC Input 1 | Inverter | Inverter063_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2920 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input2 | Inverter | Inverter063_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2921 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC input 2 | Inverter | Inverter063_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2922 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input3 | Inverter | Inverter063_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2923 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC input 3 | Inverter | Inverter063_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2924 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input4 | Inverter | Inverter063_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2925 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC input 4 | Inverter | Inverter063_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2926 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input5 | Inverter | Inverter063_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2927 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC input 5 | Inverter | Inverter063_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2928 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current DC Input6 | Inverter | Inverter063_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2929 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC input 6 | Inverter | Inverter063_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2930 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current-AC | Inverter | Inverter063_MODBUS.HR1007_i3Avg_A | Current-AC | 2931 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Current-DC | Inverter | Inverter063_MODBUS.HR1062_idcInput_A | Current-DC | 2932 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Daily Energy Delivered | Inverter | Inverter063_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2933 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power Set Point | Inverter | Inverter063_MODBUS.HR0553_pRef | Real Power Set Point | 2934 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Reactive Power Set Point | Inverter | Inverter063_MODBUS.HR0558_qRef | Reactive Power Set Point | 2935 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Frequency | Inverter | Inverter063_MODBUS.HR1012_f3_Hz | Frequency | 2936 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV063 | Dagget 3_SUB1_INV063_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Insulation Resistance | Inverter | Inverter063_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2937 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Number of DU Channels | Inverter | Inverter063_MODBUS.HR0653_duChannels | Number of DU Channels | 2938 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Number of Running Modules | Inverter | Inverter063_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2939 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Operating State | Inverter | Inverter063_MODBUS.HR1123_currentStatus | Operating State | 2940 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Power Factor | Inverter | Inverter063_MODBUS.HR1011_pf3 | Power Factor | 2941 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV063 | Dagget 3_SUB1_INV063_Ramp Down | Inverter | Inverter063_MODBUS.HR0286_dropGradient_p | Ramp Down | 2942 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Ramp Up | Inverter | Inverter063_MODBUS.HR0282_riseGradient_p | Ramp Up | 2943 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power Delivered | Inverter | Inverter063_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2944 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Reactive Power Delivered | Inverter | Inverter063_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2945 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power | 2946 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Reactive Power | Inverter | Inverter063_MODBUS.HR1009_q3_kvar | Reactive Power | 2947 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Reactive Power Mode | Inverter | Inverter063_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2948 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Reactive Power Set Point Percent | Inverter | Inverter063_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2949 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power AC Percent | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2950 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power-AC | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power-AC | 2951 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power-DC | Inverter | Inverter063_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2952 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Air Intake | Inverter | Inverter063_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2953 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Cabinet | Inverter | Inverter063_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2954 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-IGBT | Inverter | Inverter063_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2955 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Temperature-Module | Inverter | Inverter063_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2956 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage A-B | Inverter | Inverter063_MODBUS.HR1003_vRS_V | Voltage A-B | 2957 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage B-C | Inverter | Inverter063_MODBUS.HR1002_vST_V | Voltage B-C | 2958 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage C-A | Inverter | Inverter063_MODBUS.HR1003_vTR_V | Voltage C-A | 2959 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Voltage DC | Inverter | Inverter063_MODBUS.HR1051_vdcBus_V | Voltage DC | 2960 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV064 | Dagget 3_SUB1_INV064_A Phase Current | Inverter | Inverter064_MODBUS.HR1004_i1_A | A Phase Current | 2961 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_B Phase Current | Inverter | Inverter064_MODBUS.HR1005_i2_A | B Phase Current | 2962 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_C Phase Current | Inverter | Inverter064_MODBUS.HR1006_i3_A | C Phase Current | 2963 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Bus Voltage | Inverter | Inverter064_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2964 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV064 | Dagget 3_SUB1_INV064_Apparent Power | Inverter | Inverter064_MODBUS.HR1010_s3_VA | Apparent Power | 2965 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input1 | Inverter | Inverter064_MODBUS.HR5005_m1_idc_A | Current DC Input# | 2966 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC Input 1 | Inverter | Inverter064_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 2967 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input2 | Inverter | Inverter064_MODBUS.HR5037_m2_idc_A | Current DC Input# | 2968 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC input 2 | Inverter | Inverter064_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 2969 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input3 | Inverter | Inverter064_MODBUS.HR5069_m3_idc_A | Current DC Input# | 2970 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC input 3 | Inverter | Inverter064_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 2971 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input4 | Inverter | Inverter064_MODBUS.HR5101_m4_idc_A | Current DC Input# | 2972 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC input 4 | Inverter | Inverter064_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 2973 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input5 | Inverter | Inverter064_MODBUS.HR5133_m5_idc_A | Current DC Input# | 2974 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC input 5 | Inverter | Inverter064_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 2975 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current DC Input6 | Inverter | Inverter064_MODBUS.HR5165_m6_idc_A | Current DC Input# | 2976 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC input 6 | Inverter | Inverter064_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 2977 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current-AC | Inverter | Inverter064_MODBUS.HR1007_i3Avg_A | Current-AC | 2978 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Current-DC | Inverter | Inverter064_MODBUS.HR1062_idcInput_A | Current-DC | 2979 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Daily Energy Delivered | Inverter | Inverter064_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2980 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power Set Point | Inverter | Inverter064_MODBUS.HR0553_pRef | Real Power Set Point | 2981 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Reactive Power Set Point | Inverter | Inverter064_MODBUS.HR0558_qRef | Reactive Power Set Point | 2982 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Frequency | Inverter | Inverter064_MODBUS.HR1012_f3_Hz | Frequency | 2983 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV064 | Dagget 3_SUB1_INV064_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Insulation Resistance | Inverter | Inverter064_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2984 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Number of DU Channels | Inverter | Inverter064_MODBUS.HR0653_duChannels | Number of DU Channels | 2985 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Number of Running Modules | Inverter | Inverter064_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2986 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Operating State | Inverter | Inverter064_MODBUS.HR1123_currentStatus | Operating State | 2987 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Power Factor | Inverter | Inverter064_MODBUS.HR1011_pf3 | Power Factor | 2988 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV064 | Dagget 3_SUB1_INV064_Ramp Down | Inverter | Inverter064_MODBUS.HR0286_dropGradient_p | Ramp Down | 2989 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Ramp Up | Inverter | Inverter064_MODBUS.HR0282_riseGradient_p | Ramp Up | 2990 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power Delivered | Inverter | Inverter064_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2991 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Reactive Power Delivered | Inverter | Inverter064_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2992 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power | 2993 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Reactive Power | Inverter | Inverter064_MODBUS.HR1009_q3_kvar | Reactive Power | 2994 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Reactive Power Mode | Inverter | Inverter064_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2995 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Reactive Power Set Point Percent | Inverter | Inverter064_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2996 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power AC Percent | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2997 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power-AC | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power-AC | 2998 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power-DC | Inverter | Inverter064_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2999 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Air Intake | Inverter | Inverter064_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3000 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Cabinet | Inverter | Inverter064_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3001 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-IGBT | Inverter | Inverter064_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3002 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Temperature-Module | Inverter | Inverter064_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3003 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage A-B | Inverter | Inverter064_MODBUS.HR1004_vRS_V | Voltage A-B | 3004 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage B-C | Inverter | Inverter064_MODBUS.HR1002_vST_V | Voltage B-C | 3005 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage C-A | Inverter | Inverter064_MODBUS.HR1003_vTR_V | Voltage C-A | 3006 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Voltage DC | Inverter | Inverter064_MODBUS.HR1051_vdcBus_V | Voltage DC | 3007 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV065 | Dagget 3_SUB1_INV065_A Phase Current | Inverter | Inverter065_MODBUS.HR1004_i1_A | A Phase Current | 3008 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_B Phase Current | Inverter | Inverter065_MODBUS.HR1005_i2_A | B Phase Current | 3009 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_C Phase Current | Inverter | Inverter065_MODBUS.HR1006_i3_A | C Phase Current | 3010 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Bus Voltage | Inverter | Inverter065_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3011 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV065 | Dagget 3_SUB1_INV065_Apparent Power | Inverter | Inverter065_MODBUS.HR1010_s3_VA | Apparent Power | 3012 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input1 | Inverter | Inverter065_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3013 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC Input 1 | Inverter | Inverter065_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3014 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input2 | Inverter | Inverter065_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3015 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC input 2 | Inverter | Inverter065_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3016 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input3 | Inverter | Inverter065_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3017 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC input 3 | Inverter | Inverter065_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3018 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input4 | Inverter | Inverter065_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3019 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC input 4 | Inverter | Inverter065_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3020 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input5 | Inverter | Inverter065_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3021 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC input 5 | Inverter | Inverter065_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3022 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current DC Input6 | Inverter | Inverter065_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3023 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC input 6 | Inverter | Inverter065_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3024 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current-AC | Inverter | Inverter065_MODBUS.HR1007_i3Avg_A | Current-AC | 3025 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Current-DC | Inverter | Inverter065_MODBUS.HR1062_idcInput_A | Current-DC | 3026 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Daily Energy Delivered | Inverter | Inverter065_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3027 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power Set Point | Inverter | Inverter065_MODBUS.HR0553_pRef | Real Power Set Point | 3028 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Reactive Power Set Point | Inverter | Inverter065_MODBUS.HR0558_qRef | Reactive Power Set Point | 3029 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Frequency | Inverter | Inverter065_MODBUS.HR1012_f3_Hz | Frequency | 3030 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV065 | Dagget 3_SUB1_INV065_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Insulation Resistance | Inverter | Inverter065_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3031 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Number of DU Channels | Inverter | Inverter065_MODBUS.HR0653_duChannels | Number of DU Channels | 3032 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Number of Running Modules | Inverter | Inverter065_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3033 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Operating State | Inverter | Inverter065_MODBUS.HR1123_currentStatus | Operating State | 3034 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Power Factor | Inverter | Inverter065_MODBUS.HR1011_pf3 | Power Factor | 3035 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV065 | Dagget 3_SUB1_INV065_Ramp Down | Inverter | Inverter065_MODBUS.HR0286_dropGradient_p | Ramp Down | 3036 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Ramp Up | Inverter | Inverter065_MODBUS.HR0282_riseGradient_p | Ramp Up | 3037 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power Delivered | Inverter | Inverter065_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3038 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Reactive Power Delivered | Inverter | Inverter065_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3039 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power | 3040 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Reactive Power | Inverter | Inverter065_MODBUS.HR1009_q3_kvar | Reactive Power | 3041 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Reactive Power Mode | Inverter | Inverter065_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3042 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Reactive Power Set Point Percent | Inverter | Inverter065_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3043 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power AC Percent | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3044 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power-AC | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power-AC | 3045 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power-DC | Inverter | Inverter065_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3046 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Air Intake | Inverter | Inverter065_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3047 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Cabinet | Inverter | Inverter065_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3048 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-IGBT | Inverter | Inverter065_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3049 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Temperature-Module | Inverter | Inverter065_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3050 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage A-B | Inverter | Inverter065_MODBUS.HR1005_vRS_V | Voltage A-B | 3051 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage B-C | Inverter | Inverter065_MODBUS.HR1002_vST_V | Voltage B-C | 3052 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage C-A | Inverter | Inverter065_MODBUS.HR1003_vTR_V | Voltage C-A | 3053 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Voltage DC | Inverter | Inverter065_MODBUS.HR1051_vdcBus_V | Voltage DC | 3054 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV066 | Dagget 3_SUB1_INV066_A Phase Current | Inverter | Inverter066_MODBUS.HR1004_i1_A | A Phase Current | 3055 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_B Phase Current | Inverter | Inverter066_MODBUS.HR1005_i2_A | B Phase Current | 3056 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_C Phase Current | Inverter | Inverter066_MODBUS.HR1006_i3_A | C Phase Current | 3057 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Bus Voltage | Inverter | Inverter066_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3058 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV066 | Dagget 3_SUB1_INV066_Apparent Power | Inverter | Inverter066_MODBUS.HR1010_s3_VA | Apparent Power | 3059 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input1 | Inverter | Inverter066_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3060 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC Input 1 | Inverter | Inverter066_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3061 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input2 | Inverter | Inverter066_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3062 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC input 2 | Inverter | Inverter066_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3063 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input3 | Inverter | Inverter066_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3064 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC input 3 | Inverter | Inverter066_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3065 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input4 | Inverter | Inverter066_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3066 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC input 4 | Inverter | Inverter066_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3067 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input5 | Inverter | Inverter066_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3068 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC input 5 | Inverter | Inverter066_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3069 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current DC Input6 | Inverter | Inverter066_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3070 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC input 6 | Inverter | Inverter066_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3071 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current-AC | Inverter | Inverter066_MODBUS.HR1007_i3Avg_A | Current-AC | 3072 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Current-DC | Inverter | Inverter066_MODBUS.HR1062_idcInput_A | Current-DC | 3073 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Daily Energy Delivered | Inverter | Inverter066_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3074 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power Set Point | Inverter | Inverter066_MODBUS.HR0553_pRef | Real Power Set Point | 3075 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Reactive Power Set Point | Inverter | Inverter066_MODBUS.HR0558_qRef | Reactive Power Set Point | 3076 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Frequency | Inverter | Inverter066_MODBUS.HR1012_f3_Hz | Frequency | 3077 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV066 | Dagget 3_SUB1_INV066_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Insulation Resistance | Inverter | Inverter066_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3078 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Number of DU Channels | Inverter | Inverter066_MODBUS.HR0653_duChannels | Number of DU Channels | 3079 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Number of Running Modules | Inverter | Inverter066_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3080 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Operating State | Inverter | Inverter066_MODBUS.HR1123_currentStatus | Operating State | 3081 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Power Factor | Inverter | Inverter066_MODBUS.HR1011_pf3 | Power Factor | 3082 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV066 | Dagget 3_SUB1_INV066_Ramp Down | Inverter | Inverter066_MODBUS.HR0286_dropGradient_p | Ramp Down | 3083 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Ramp Up | Inverter | Inverter066_MODBUS.HR0282_riseGradient_p | Ramp Up | 3084 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power Delivered | Inverter | Inverter066_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3085 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Reactive Power Delivered | Inverter | Inverter066_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3086 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power | 3087 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Reactive Power | Inverter | Inverter066_MODBUS.HR1009_q3_kvar | Reactive Power | 3088 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Reactive Power Mode | Inverter | Inverter066_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3089 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Reactive Power Set Point Percent | Inverter | Inverter066_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3090 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power AC Percent | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3091 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power-AC | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power-AC | 3092 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power-DC | Inverter | Inverter066_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3093 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Air Intake | Inverter | Inverter066_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3094 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Cabinet | Inverter | Inverter066_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3095 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-IGBT | Inverter | Inverter066_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3096 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Temperature-Module | Inverter | Inverter066_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3097 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage A-B | Inverter | Inverter066_MODBUS.HR1006_vRS_V | Voltage A-B | 3098 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage B-C | Inverter | Inverter066_MODBUS.HR1002_vST_V | Voltage B-C | 3099 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage C-A | Inverter | Inverter066_MODBUS.HR1003_vTR_V | Voltage C-A | 3100 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Voltage DC | Inverter | Inverter066_MODBUS.HR1051_vdcBus_V | Voltage DC | 3101 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV067 | Dagget 3_SUB1_INV067_A Phase Current | Inverter | Inverter067_MODBUS.HR1004_i1_A | A Phase Current | 3102 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_B Phase Current | Inverter | Inverter067_MODBUS.HR1005_i2_A | B Phase Current | 3103 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_C Phase Current | Inverter | Inverter067_MODBUS.HR1006_i3_A | C Phase Current | 3104 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Bus Voltage | Inverter | Inverter067_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3105 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV067 | Dagget 3_SUB1_INV067_Apparent Power | Inverter | Inverter067_MODBUS.HR1010_s3_VA | Apparent Power | 3106 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input1 | Inverter | Inverter067_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3107 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC Input 1 | Inverter | Inverter067_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3108 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input2 | Inverter | Inverter067_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3109 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC input 2 | Inverter | Inverter067_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3110 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input3 | Inverter | Inverter067_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3111 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC input 3 | Inverter | Inverter067_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3112 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input4 | Inverter | Inverter067_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3113 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC input 4 | Inverter | Inverter067_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3114 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input5 | Inverter | Inverter067_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3115 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC input 5 | Inverter | Inverter067_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3116 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current DC Input6 | Inverter | Inverter067_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3117 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC input 6 | Inverter | Inverter067_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3118 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current-AC | Inverter | Inverter067_MODBUS.HR1007_i3Avg_A | Current-AC | 3119 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Current-DC | Inverter | Inverter067_MODBUS.HR1062_idcInput_A | Current-DC | 3120 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Daily Energy Delivered | Inverter | Inverter067_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3121 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power Set Point | Inverter | Inverter067_MODBUS.HR0553_pRef | Real Power Set Point | 3122 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Reactive Power Set Point | Inverter | Inverter067_MODBUS.HR0558_qRef | Reactive Power Set Point | 3123 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Frequency | Inverter | Inverter067_MODBUS.HR1012_f3_Hz | Frequency | 3124 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV067 | Dagget 3_SUB1_INV067_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Insulation Resistance | Inverter | Inverter067_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3125 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Number of DU Channels | Inverter | Inverter067_MODBUS.HR0653_duChannels | Number of DU Channels | 3126 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Number of Running Modules | Inverter | Inverter067_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3127 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Operating State | Inverter | Inverter067_MODBUS.HR1123_currentStatus | Operating State | 3128 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Power Factor | Inverter | Inverter067_MODBUS.HR1011_pf3 | Power Factor | 3129 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV067 | Dagget 3_SUB1_INV067_Ramp Down | Inverter | Inverter067_MODBUS.HR0286_dropGradient_p | Ramp Down | 3130 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Ramp Up | Inverter | Inverter067_MODBUS.HR0282_riseGradient_p | Ramp Up | 3131 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power Delivered | Inverter | Inverter067_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3132 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Reactive Power Delivered | Inverter | Inverter067_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3133 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power | 3134 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Reactive Power | Inverter | Inverter067_MODBUS.HR1009_q3_kvar | Reactive Power | 3135 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Reactive Power Mode | Inverter | Inverter067_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3136 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Reactive Power Set Point Percent | Inverter | Inverter067_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3137 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power AC Percent | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3138 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power-AC | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power-AC | 3139 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power-DC | Inverter | Inverter067_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3140 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Air Intake | Inverter | Inverter067_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3141 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Cabinet | Inverter | Inverter067_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3142 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-IGBT | Inverter | Inverter067_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3143 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Temperature-Module | Inverter | Inverter067_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3144 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage A-B | Inverter | Inverter067_MODBUS.HR1007_vRS_V | Voltage A-B | 3145 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage B-C | Inverter | Inverter067_MODBUS.HR1002_vST_V | Voltage B-C | 3146 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage C-A | Inverter | Inverter067_MODBUS.HR1003_vTR_V | Voltage C-A | 3147 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Voltage DC | Inverter | Inverter067_MODBUS.HR1051_vdcBus_V | Voltage DC | 3148 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV068 | Dagget 3_SUB1_INV068_A Phase Current | Inverter | Inverter068_MODBUS.HR1004_i1_A | A Phase Current | 3149 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_B Phase Current | Inverter | Inverter068_MODBUS.HR1005_i2_A | B Phase Current | 3150 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_C Phase Current | Inverter | Inverter068_MODBUS.HR1006_i3_A | C Phase Current | 3151 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Bus Voltage | Inverter | Inverter068_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3152 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV068 | Dagget 3_SUB1_INV068_Apparent Power | Inverter | Inverter068_MODBUS.HR1010_s3_VA | Apparent Power | 3153 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input1 | Inverter | Inverter068_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3154 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC Input 1 | Inverter | Inverter068_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3155 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input2 | Inverter | Inverter068_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3156 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC input 2 | Inverter | Inverter068_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3157 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input3 | Inverter | Inverter068_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3158 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC input 3 | Inverter | Inverter068_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3159 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input4 | Inverter | Inverter068_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3160 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC input 4 | Inverter | Inverter068_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3161 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input5 | Inverter | Inverter068_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3162 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC input 5 | Inverter | Inverter068_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3163 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current DC Input6 | Inverter | Inverter068_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3164 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC input 6 | Inverter | Inverter068_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3165 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current-AC | Inverter | Inverter068_MODBUS.HR1007_i3Avg_A | Current-AC | 3166 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Current-DC | Inverter | Inverter068_MODBUS.HR1062_idcInput_A | Current-DC | 3167 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Daily Energy Delivered | Inverter | Inverter068_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3168 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power Set Point | Inverter | Inverter068_MODBUS.HR0553_pRef | Real Power Set Point | 3169 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Reactive Power Set Point | Inverter | Inverter068_MODBUS.HR0558_qRef | Reactive Power Set Point | 3170 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Frequency | Inverter | Inverter068_MODBUS.HR1012_f3_Hz | Frequency | 3171 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV068 | Dagget 3_SUB1_INV068_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Insulation Resistance | Inverter | Inverter068_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3172 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Number of DU Channels | Inverter | Inverter068_MODBUS.HR0653_duChannels | Number of DU Channels | 3173 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Number of Running Modules | Inverter | Inverter068_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3174 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Operating State | Inverter | Inverter068_MODBUS.HR1123_currentStatus | Operating State | 3175 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Power Factor | Inverter | Inverter068_MODBUS.HR1011_pf3 | Power Factor | 3176 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV068 | Dagget 3_SUB1_INV068_Ramp Down | Inverter | Inverter068_MODBUS.HR0286_dropGradient_p | Ramp Down | 3177 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Ramp Up | Inverter | Inverter068_MODBUS.HR0282_riseGradient_p | Ramp Up | 3178 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power Delivered | Inverter | Inverter068_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3179 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Reactive Power Delivered | Inverter | Inverter068_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3180 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power | 3181 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Reactive Power | Inverter | Inverter068_MODBUS.HR1009_q3_kvar | Reactive Power | 3182 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Reactive Power Mode | Inverter | Inverter068_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3183 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Reactive Power Set Point Percent | Inverter | Inverter068_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3184 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power AC Percent | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3185 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power-AC | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power-AC | 3186 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power-DC | Inverter | Inverter068_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3187 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Air Intake | Inverter | Inverter068_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3188 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Cabinet | Inverter | Inverter068_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3189 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-IGBT | Inverter | Inverter068_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3190 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Temperature-Module | Inverter | Inverter068_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3191 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage A-B | Inverter | Inverter068_MODBUS.HR1008_vRS_V | Voltage A-B | 3192 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage B-C | Inverter | Inverter068_MODBUS.HR1002_vST_V | Voltage B-C | 3193 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage C-A | Inverter | Inverter068_MODBUS.HR1003_vTR_V | Voltage C-A | 3194 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Voltage DC | Inverter | Inverter068_MODBUS.HR1051_vdcBus_V | Voltage DC | 3195 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV069 | Dagget 3_SUB1_INV069_A Phase Current | Inverter | Inverter069_MODBUS.HR1004_i1_A | A Phase Current | 3196 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_B Phase Current | Inverter | Inverter069_MODBUS.HR1005_i2_A | B Phase Current | 3197 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_C Phase Current | Inverter | Inverter069_MODBUS.HR1006_i3_A | C Phase Current | 3198 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Bus Voltage | Inverter | Inverter069_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3199 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV069 | Dagget 3_SUB1_INV069_Apparent Power | Inverter | Inverter069_MODBUS.HR1010_s3_VA | Apparent Power | 3200 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input1 | Inverter | Inverter069_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3201 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC Input 1 | Inverter | Inverter069_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3202 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input2 | Inverter | Inverter069_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3203 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC input 2 | Inverter | Inverter069_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3204 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input3 | Inverter | Inverter069_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3205 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC input 3 | Inverter | Inverter069_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3206 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input4 | Inverter | Inverter069_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3207 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC input 4 | Inverter | Inverter069_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3208 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input5 | Inverter | Inverter069_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3209 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC input 5 | Inverter | Inverter069_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3210 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current DC Input6 | Inverter | Inverter069_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3211 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC input 6 | Inverter | Inverter069_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3212 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current-AC | Inverter | Inverter069_MODBUS.HR1007_i3Avg_A | Current-AC | 3213 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Current-DC | Inverter | Inverter069_MODBUS.HR1062_idcInput_A | Current-DC | 3214 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Daily Energy Delivered | Inverter | Inverter069_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3215 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power Set Point | Inverter | Inverter069_MODBUS.HR0553_pRef | Real Power Set Point | 3216 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Reactive Power Set Point | Inverter | Inverter069_MODBUS.HR0558_qRef | Reactive Power Set Point | 3217 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Frequency | Inverter | Inverter069_MODBUS.HR1012_f3_Hz | Frequency | 3218 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV069 | Dagget 3_SUB1_INV069_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Insulation Resistance | Inverter | Inverter069_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3219 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Number of DU Channels | Inverter | Inverter069_MODBUS.HR0653_duChannels | Number of DU Channels | 3220 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Number of Running Modules | Inverter | Inverter069_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3221 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Operating State | Inverter | Inverter069_MODBUS.HR1123_currentStatus | Operating State | 3222 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Power Factor | Inverter | Inverter069_MODBUS.HR1011_pf3 | Power Factor | 3223 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV069 | Dagget 3_SUB1_INV069_Ramp Down | Inverter | Inverter069_MODBUS.HR0286_dropGradient_p | Ramp Down | 3224 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Ramp Up | Inverter | Inverter069_MODBUS.HR0282_riseGradient_p | Ramp Up | 3225 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power Delivered | Inverter | Inverter069_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3226 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Reactive Power Delivered | Inverter | Inverter069_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3227 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power | 3228 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Reactive Power | Inverter | Inverter069_MODBUS.HR1009_q3_kvar | Reactive Power | 3229 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Reactive Power Mode | Inverter | Inverter069_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3230 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Reactive Power Set Point Percent | Inverter | Inverter069_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3231 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power AC Percent | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3232 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power-AC | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power-AC | 3233 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power-DC | Inverter | Inverter069_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3234 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Air Intake | Inverter | Inverter069_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3235 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Cabinet | Inverter | Inverter069_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3236 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-IGBT | Inverter | Inverter069_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3237 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Temperature-Module | Inverter | Inverter069_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3238 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage A-B | Inverter | Inverter069_MODBUS.HR1009_vRS_V | Voltage A-B | 3239 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage B-C | Inverter | Inverter069_MODBUS.HR1002_vST_V | Voltage B-C | 3240 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage C-A | Inverter | Inverter069_MODBUS.HR1003_vTR_V | Voltage C-A | 3241 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Voltage DC | Inverter | Inverter069_MODBUS.HR1051_vdcBus_V | Voltage DC | 3242 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV070 | Dagget 3_SUB1_INV070_A Phase Current | Inverter | inverter070_MODBUS.HR1004_i1_A | A Phase Current | 3243 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_B Phase Current | Inverter | inverter070_MODBUS.HR1005_i2_A | B Phase Current | 3244 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_C Phase Current | Inverter | inverter070_MODBUS.HR1006_i3_A | C Phase Current | 3245 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Bus Voltage | Inverter | inverter070_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3246 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV070 | Dagget 3_SUB1_INV070_Apparent Power | Inverter | inverter070_MODBUS.HR1010_s3_VA | Apparent Power | 3247 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input1 | Inverter | inverter070_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3248 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC Input 1 | Inverter | inverter070_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3249 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input2 | Inverter | inverter070_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3250 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC input 2 | Inverter | inverter070_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3251 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input3 | Inverter | inverter070_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3252 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC input 3 | Inverter | inverter070_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3253 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input4 | Inverter | inverter070_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3254 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC input 4 | Inverter | inverter070_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3255 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input5 | Inverter | inverter070_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3256 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC input 5 | Inverter | inverter070_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3257 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current DC Input6 | Inverter | inverter070_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3258 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC input 6 | Inverter | inverter070_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3259 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current-AC | Inverter | inverter070_MODBUS.HR1007_i3Avg_A | Current-AC | 3260 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Current-DC | Inverter | inverter070_MODBUS.HR1062_idcInput_A | Current-DC | 3261 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Daily Energy Delivered | Inverter | inverter070_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3262 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power Set Point | Inverter | inverter070_MODBUS.HR0553_pRef | Real Power Set Point | 3263 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Reactive Power Set Point | Inverter | inverter070_MODBUS.HR0558_qRef | Reactive Power Set Point | 3264 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Frequency | Inverter | inverter070_MODBUS.HR1012_f3_Hz | Frequency | 3265 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV070 | Dagget 3_SUB1_INV070_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Insulation Resistance | Inverter | inverter070_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3266 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Number of DU Channels | Inverter | inverter070_MODBUS.HR0653_duChannels | Number of DU Channels | 3267 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Number of Running Modules | Inverter | inverter070_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3268 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Operating State | Inverter | inverter070_MODBUS.HR1123_currentStatus | Operating State | 3269 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Power Factor | Inverter | inverter070_MODBUS.HR1011_pf3 | Power Factor | 3270 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV070 | Dagget 3_SUB1_INV070_Ramp Down | Inverter | inverter070_MODBUS.HR0286_dropGradient_p | Ramp Down | 3271 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Ramp Up | Inverter | inverter070_MODBUS.HR0282_riseGradient_p | Ramp Up | 3272 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power Delivered | Inverter | inverter070_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3273 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Reactive Power Delivered | Inverter | inverter070_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3274 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power | 3275 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Reactive Power | Inverter | inverter070_MODBUS.HR1009_q3_kvar | Reactive Power | 3276 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Reactive Power Mode | Inverter | inverter070_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3277 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Reactive Power Set Point Percent | Inverter | inverter070_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3278 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power AC Percent | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3279 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power-AC | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power-AC | 3280 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power-DC | Inverter | inverter070_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3281 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Air Intake | Inverter | inverter070_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3282 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Cabinet | Inverter | inverter070_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3283 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-IGBT | Inverter | inverter070_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3284 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Temperature-Module | Inverter | inverter070_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3285 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage A-B | Inverter | inverter070_MODBUS.HR1010_vRS_V | Voltage A-B | 3286 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage B-C | Inverter | inverter070_MODBUS.HR1002_vST_V | Voltage B-C | 3287 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage C-A | Inverter | inverter070_MODBUS.HR1003_vTR_V | Voltage C-A | 3288 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Voltage DC | Inverter | inverter070_MODBUS.HR1051_vdcBus_V | Voltage DC | 3289 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV071 | Dagget 3_SUB1_INV071_A Phase Current | Inverter | inverter071_MODBUS.HR1004_i1_A | A Phase Current | 3290 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_B Phase Current | Inverter | inverter071_MODBUS.HR1005_i2_A | B Phase Current | 3291 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_C Phase Current | Inverter | inverter071_MODBUS.HR1006_i3_A | C Phase Current | 3292 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Bus Voltage | Inverter | inverter071_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3293 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV071 | Dagget 3_SUB1_INV071_Apparent Power | Inverter | inverter071_MODBUS.HR1010_s3_VA | Apparent Power | 3294 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input1 | Inverter | inverter071_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3295 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC Input 1 | Inverter | inverter071_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3296 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input2 | Inverter | inverter071_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3297 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC input 2 | Inverter | inverter071_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3298 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input3 | Inverter | inverter071_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3299 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC input 3 | Inverter | inverter071_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3300 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input4 | Inverter | inverter071_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3301 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC input 4 | Inverter | inverter071_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3302 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input5 | Inverter | inverter071_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3303 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC input 5 | Inverter | inverter071_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3304 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current DC Input6 | Inverter | inverter071_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3305 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC input 6 | Inverter | inverter071_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3306 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current-AC | Inverter | inverter071_MODBUS.HR1007_i3Avg_A | Current-AC | 3307 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Current-DC | Inverter | inverter071_MODBUS.HR1062_idcInput_A | Current-DC | 3308 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Daily Energy Delivered | Inverter | inverter071_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3309 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power Set Point | Inverter | inverter071_MODBUS.HR0553_pRef | Real Power Set Point | 3310 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Reactive Power Set Point | Inverter | inverter071_MODBUS.HR0558_qRef | Reactive Power Set Point | 3311 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Frequency | Inverter | inverter071_MODBUS.HR1012_f3_Hz | Frequency | 3312 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV071 | Dagget 3_SUB1_INV071_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Insulation Resistance | Inverter | inverter071_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3313 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Number of DU Channels | Inverter | inverter071_MODBUS.HR0653_duChannels | Number of DU Channels | 3314 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Number of Running Modules | Inverter | inverter071_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3315 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Operating State | Inverter | inverter071_MODBUS.HR1123_currentStatus | Operating State | 3316 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Power Factor | Inverter | inverter071_MODBUS.HR1011_pf3 | Power Factor | 3317 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV071 | Dagget 3_SUB1_INV071_Ramp Down | Inverter | inverter071_MODBUS.HR0286_dropGradient_p | Ramp Down | 3318 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Ramp Up | Inverter | inverter071_MODBUS.HR0282_riseGradient_p | Ramp Up | 3319 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power Delivered | Inverter | inverter071_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3320 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Reactive Power Delivered | Inverter | inverter071_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3321 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power | 3322 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Reactive Power | Inverter | inverter071_MODBUS.HR1009_q3_kvar | Reactive Power | 3323 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Reactive Power Mode | Inverter | inverter071_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3324 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Reactive Power Set Point Percent | Inverter | inverter071_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3325 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power AC Percent | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3326 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power-AC | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power-AC | 3327 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power-DC | Inverter | inverter071_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3328 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Air Intake | Inverter | inverter071_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3329 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Cabinet | Inverter | inverter071_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3330 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-IGBT | Inverter | inverter071_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3331 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Temperature-Module | Inverter | inverter071_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3332 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage A-B | Inverter | inverter071_MODBUS.HR1001_vRS_V | Voltage A-B | 3333 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage B-C | Inverter | inverter071_MODBUS.HR1002_vST_V | Voltage B-C | 3334 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage C-A | Inverter | inverter071_MODBUS.HR1003_vTR_V | Voltage C-A | 3335 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Voltage DC | Inverter | inverter071_MODBUS.HR1051_vdcBus_V | Voltage DC | 3336 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV072 | Dagget 3_SUB1_INV072_A Phase Current | Inverter | inverter072_MODBUS.HR1004_i1_A | A Phase Current | 3337 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_B Phase Current | Inverter | inverter072_MODBUS.HR1005_i2_A | B Phase Current | 3338 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_C Phase Current | Inverter | inverter072_MODBUS.HR1006_i3_A | C Phase Current | 3339 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Bus Voltage | Inverter | inverter072_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3340 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV072 | Dagget 3_SUB1_INV072_Apparent Power | Inverter | inverter072_MODBUS.HR1010_s3_VA | Apparent Power | 3341 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input1 | Inverter | inverter072_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3342 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC Input 1 | Inverter | inverter072_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3343 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input2 | Inverter | inverter072_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3344 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC input 2 | Inverter | inverter072_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3345 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input3 | Inverter | inverter072_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3346 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC input 3 | Inverter | inverter072_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3347 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input4 | Inverter | inverter072_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3348 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC input 4 | Inverter | inverter072_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3349 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input5 | Inverter | inverter072_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3350 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC input 5 | Inverter | inverter072_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3351 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current DC Input6 | Inverter | inverter072_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3352 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC input 6 | Inverter | inverter072_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3353 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current-AC | Inverter | inverter072_MODBUS.HR1007_i3Avg_A | Current-AC | 3354 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Current-DC | Inverter | inverter072_MODBUS.HR1062_idcInput_A | Current-DC | 3355 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Daily Energy Delivered | Inverter | inverter072_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3356 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power Set Point | Inverter | inverter072_MODBUS.HR0553_pRef | Real Power Set Point | 3357 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Reactive Power Set Point | Inverter | inverter072_MODBUS.HR0558_qRef | Reactive Power Set Point | 3358 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Frequency | Inverter | inverter072_MODBUS.HR1012_f3_Hz | Frequency | 3359 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV072 | Dagget 3_SUB1_INV072_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Insulation Resistance | Inverter | inverter072_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3360 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Number of DU Channels | Inverter | inverter072_MODBUS.HR0653_duChannels | Number of DU Channels | 3361 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Number of Running Modules | Inverter | inverter072_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3362 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Operating State | Inverter | inverter072_MODBUS.HR1123_currentStatus | Operating State | 3363 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Power Factor | Inverter | inverter072_MODBUS.HR1011_pf3 | Power Factor | 3364 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV072 | Dagget 3_SUB1_INV072_Ramp Down | Inverter | inverter072_MODBUS.HR0286_dropGradient_p | Ramp Down | 3365 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Ramp Up | Inverter | inverter072_MODBUS.HR0282_riseGradient_p | Ramp Up | 3366 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power Delivered | Inverter | inverter072_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3367 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Reactive Power Delivered | Inverter | inverter072_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3368 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power | 3369 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Reactive Power | Inverter | inverter072_MODBUS.HR1009_q3_kvar | Reactive Power | 3370 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Reactive Power Mode | Inverter | inverter072_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3371 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Reactive Power Set Point Percent | Inverter | inverter072_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3372 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power AC Percent | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3373 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power-AC | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power-AC | 3374 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power-DC | Inverter | inverter072_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3375 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Air Intake | Inverter | inverter072_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3376 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Cabinet | Inverter | inverter072_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3377 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-IGBT | Inverter | inverter072_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3378 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Temperature-Module | Inverter | inverter072_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3379 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage A-B | Inverter | inverter072_MODBUS.HR1002_vRS_V | Voltage A-B | 3380 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage B-C | Inverter | inverter072_MODBUS.HR1002_vST_V | Voltage B-C | 3381 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage C-A | Inverter | inverter072_MODBUS.HR1003_vTR_V | Voltage C-A | 3382 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Voltage DC | Inverter | inverter072_MODBUS.HR1051_vdcBus_V | Voltage DC | 3383 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV073 | Dagget 3_SUB1_INV073_A Phase Current | Inverter | inverter073_MODBUS.HR1004_i1_A | A Phase Current | 3384 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_B Phase Current | Inverter | inverter073_MODBUS.HR1005_i2_A | B Phase Current | 3385 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_C Phase Current | Inverter | inverter073_MODBUS.HR1006_i3_A | C Phase Current | 3386 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Bus Voltage | Inverter | inverter073_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3387 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV073 | Dagget 3_SUB1_INV073_Apparent Power | Inverter | inverter073_MODBUS.HR1010_s3_VA | Apparent Power | 3388 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input1 | Inverter | inverter073_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3389 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC Input 1 | Inverter | inverter073_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3390 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input2 | Inverter | inverter073_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3391 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC input 2 | Inverter | inverter073_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3392 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input3 | Inverter | inverter073_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3393 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC input 3 | Inverter | inverter073_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3394 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input4 | Inverter | inverter073_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3395 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC input 4 | Inverter | inverter073_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3396 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input5 | Inverter | inverter073_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3397 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC input 5 | Inverter | inverter073_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3398 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current DC Input6 | Inverter | inverter073_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3399 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC input 6 | Inverter | inverter073_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3400 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current-AC | Inverter | inverter073_MODBUS.HR1007_i3Avg_A | Current-AC | 3401 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Current-DC | Inverter | inverter073_MODBUS.HR1062_idcInput_A | Current-DC | 3402 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Daily Energy Delivered | Inverter | inverter073_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3403 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power Set Point | Inverter | inverter073_MODBUS.HR0553_pRef | Real Power Set Point | 3404 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Reactive Power Set Point | Inverter | inverter073_MODBUS.HR0558_qRef | Reactive Power Set Point | 3405 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Frequency | Inverter | inverter073_MODBUS.HR1012_f3_Hz | Frequency | 3406 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV073 | Dagget 3_SUB1_INV073_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Insulation Resistance | Inverter | inverter073_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3407 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Number of DU Channels | Inverter | inverter073_MODBUS.HR0653_duChannels | Number of DU Channels | 3408 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Number of Running Modules | Inverter | inverter073_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3409 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Operating State | Inverter | inverter073_MODBUS.HR1123_currentStatus | Operating State | 3410 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Power Factor | Inverter | inverter073_MODBUS.HR1011_pf3 | Power Factor | 3411 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV073 | Dagget 3_SUB1_INV073_Ramp Down | Inverter | inverter073_MODBUS.HR0286_dropGradient_p | Ramp Down | 3412 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Ramp Up | Inverter | inverter073_MODBUS.HR0282_riseGradient_p | Ramp Up | 3413 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power Delivered | Inverter | inverter073_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3414 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Reactive Power Delivered | Inverter | inverter073_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3415 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power | 3416 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Reactive Power | Inverter | inverter073_MODBUS.HR1009_q3_kvar | Reactive Power | 3417 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Reactive Power Mode | Inverter | inverter073_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3418 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Reactive Power Set Point Percent | Inverter | inverter073_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3419 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power AC Percent | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3420 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power-AC | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power-AC | 3421 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power-DC | Inverter | inverter073_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3422 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Air Intake | Inverter | inverter073_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3423 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Cabinet | Inverter | inverter073_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3424 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-IGBT | Inverter | inverter073_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3425 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Temperature-Module | Inverter | inverter073_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3426 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage A-B | Inverter | inverter073_MODBUS.HR1003_vRS_V | Voltage A-B | 3427 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage B-C | Inverter | inverter073_MODBUS.HR1002_vST_V | Voltage B-C | 3428 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage C-A | Inverter | inverter073_MODBUS.HR1003_vTR_V | Voltage C-A | 3429 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Voltage DC | Inverter | inverter073_MODBUS.HR1051_vdcBus_V | Voltage DC | 3430 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV074 | Dagget 3_SUB1_INV074_A Phase Current | Inverter | inverter074_MODBUS.HR1004_i1_A | A Phase Current | 3431 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_B Phase Current | Inverter | inverter074_MODBUS.HR1005_i2_A | B Phase Current | 3432 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_C Phase Current | Inverter | inverter074_MODBUS.HR1006_i3_A | C Phase Current | 3433 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Bus Voltage | Inverter | inverter074_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3434 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV074 | Dagget 3_SUB1_INV074_Apparent Power | Inverter | inverter074_MODBUS.HR1010_s3_VA | Apparent Power | 3435 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input1 | Inverter | inverter074_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3436 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC Input 1 | Inverter | inverter074_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3437 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input2 | Inverter | inverter074_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3438 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC input 2 | Inverter | inverter074_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3439 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input3 | Inverter | inverter074_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3440 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC input 3 | Inverter | inverter074_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3441 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input4 | Inverter | inverter074_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3442 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC input 4 | Inverter | inverter074_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3443 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input5 | Inverter | inverter074_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3444 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC input 5 | Inverter | inverter074_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3445 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current DC Input6 | Inverter | inverter074_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3446 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC input 6 | Inverter | inverter074_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3447 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current-AC | Inverter | inverter074_MODBUS.HR1007_i3Avg_A | Current-AC | 3448 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Current-DC | Inverter | inverter074_MODBUS.HR1062_idcInput_A | Current-DC | 3449 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Daily Energy Delivered | Inverter | inverter074_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3450 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power Set Point | Inverter | inverter074_MODBUS.HR0553_pRef | Real Power Set Point | 3451 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Reactive Power Set Point | Inverter | inverter074_MODBUS.HR0558_qRef | Reactive Power Set Point | 3452 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Frequency | Inverter | inverter074_MODBUS.HR1012_f3_Hz | Frequency | 3453 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV074 | Dagget 3_SUB1_INV074_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Insulation Resistance | Inverter | inverter074_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3454 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Number of DU Channels | Inverter | inverter074_MODBUS.HR0653_duChannels | Number of DU Channels | 3455 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Number of Running Modules | Inverter | inverter074_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3456 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Operating State | Inverter | inverter074_MODBUS.HR1123_currentStatus | Operating State | 3457 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Power Factor | Inverter | inverter074_MODBUS.HR1011_pf3 | Power Factor | 3458 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV074 | Dagget 3_SUB1_INV074_Ramp Down | Inverter | inverter074_MODBUS.HR0286_dropGradient_p | Ramp Down | 3459 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Ramp Up | Inverter | inverter074_MODBUS.HR0282_riseGradient_p | Ramp Up | 3460 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power Delivered | Inverter | inverter074_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3461 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Reactive Power Delivered | Inverter | inverter074_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3462 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power | 3463 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Reactive Power | Inverter | inverter074_MODBUS.HR1009_q3_kvar | Reactive Power | 3464 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Reactive Power Mode | Inverter | inverter074_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3465 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Reactive Power Set Point Percent | Inverter | inverter074_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3466 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power AC Percent | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3467 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power-AC | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power-AC | 3468 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power-DC | Inverter | inverter074_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3469 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Air Intake | Inverter | inverter074_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3470 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Cabinet | Inverter | inverter074_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3471 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-IGBT | Inverter | inverter074_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3472 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Temperature-Module | Inverter | inverter074_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3473 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage A-B | Inverter | inverter074_MODBUS.HR1004_vRS_V | Voltage A-B | 3474 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage B-C | Inverter | inverter074_MODBUS.HR1002_vST_V | Voltage B-C | 3475 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage C-A | Inverter | inverter074_MODBUS.HR1003_vTR_V | Voltage C-A | 3476 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Voltage DC | Inverter | inverter074_MODBUS.HR1051_vdcBus_V | Voltage DC | 3477 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV075 | Dagget 3_SUB1_INV075_A Phase Current | Inverter | inverter075_MODBUS.HR1004_i1_A | A Phase Current | 3478 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_B Phase Current | Inverter | inverter075_MODBUS.HR1005_i2_A | B Phase Current | 3479 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_C Phase Current | Inverter | inverter075_MODBUS.HR1006_i3_A | C Phase Current | 3480 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Bus Voltage | Inverter | inverter075_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3481 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV075 | Dagget 3_SUB1_INV075_Apparent Power | Inverter | inverter075_MODBUS.HR1010_s3_VA | Apparent Power | 3482 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input1 | Inverter | inverter075_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3483 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC Input 1 | Inverter | inverter075_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3484 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input2 | Inverter | inverter075_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3485 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC input 2 | Inverter | inverter075_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3486 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input3 | Inverter | inverter075_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3487 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC input 3 | Inverter | inverter075_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3488 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input4 | Inverter | inverter075_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3489 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC input 4 | Inverter | inverter075_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3490 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input5 | Inverter | inverter075_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3491 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC input 5 | Inverter | inverter075_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3492 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current DC Input6 | Inverter | inverter075_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3493 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC input 6 | Inverter | inverter075_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3494 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current-AC | Inverter | inverter075_MODBUS.HR1007_i3Avg_A | Current-AC | 3495 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Current-DC | Inverter | inverter075_MODBUS.HR1062_idcInput_A | Current-DC | 3496 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Daily Energy Delivered | Inverter | inverter075_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3497 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power Set Point | Inverter | inverter075_MODBUS.HR0553_pRef | Real Power Set Point | 3498 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Reactive Power Set Point | Inverter | inverter075_MODBUS.HR0558_qRef | Reactive Power Set Point | 3499 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Frequency | Inverter | inverter075_MODBUS.HR1012_f3_Hz | Frequency | 3500 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV075 | Dagget 3_SUB1_INV075_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Insulation Resistance | Inverter | inverter075_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3501 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Number of DU Channels | Inverter | inverter075_MODBUS.HR0653_duChannels | Number of DU Channels | 3502 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Number of Running Modules | Inverter | inverter075_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3503 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Operating State | Inverter | inverter075_MODBUS.HR1123_currentStatus | Operating State | 3504 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Power Factor | Inverter | inverter075_MODBUS.HR1011_pf3 | Power Factor | 3505 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV075 | Dagget 3_SUB1_INV075_Ramp Down | Inverter | inverter075_MODBUS.HR0286_dropGradient_p | Ramp Down | 3506 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Ramp Up | Inverter | inverter075_MODBUS.HR0282_riseGradient_p | Ramp Up | 3507 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power Delivered | Inverter | inverter075_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3508 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Reactive Power Delivered | Inverter | inverter075_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3509 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power | 3510 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Reactive Power | Inverter | inverter075_MODBUS.HR1009_q3_kvar | Reactive Power | 3511 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Reactive Power Mode | Inverter | inverter075_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3512 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Reactive Power Set Point Percent | Inverter | inverter075_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3513 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power AC Percent | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3514 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power-AC | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power-AC | 3515 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power-DC | Inverter | inverter075_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3516 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Air Intake | Inverter | inverter075_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3517 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Cabinet | Inverter | inverter075_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3518 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-IGBT | Inverter | inverter075_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3519 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Temperature-Module | Inverter | inverter075_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3520 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage A-B | Inverter | inverter075_MODBUS.HR1005_vRS_V | Voltage A-B | 3521 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage B-C | Inverter | inverter075_MODBUS.HR1002_vST_V | Voltage B-C | 3522 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage C-A | Inverter | inverter075_MODBUS.HR1003_vTR_V | Voltage C-A | 3523 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Voltage DC | Inverter | inverter075_MODBUS.HR1051_vdcBus_V | Voltage DC | 3524 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV076 | Dagget 3_SUB1_INV076_A Phase Current | Inverter | inverter076_MODBUS.HR1004_i1_A | A Phase Current | 3525 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_B Phase Current | Inverter | inverter076_MODBUS.HR1005_i2_A | B Phase Current | 3526 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_C Phase Current | Inverter | inverter076_MODBUS.HR1006_i3_A | C Phase Current | 3527 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Bus Voltage | Inverter | inverter076_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3528 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV076 | Dagget 3_SUB1_INV076_Apparent Power | Inverter | inverter076_MODBUS.HR1010_s3_VA | Apparent Power | 3529 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input1 | Inverter | inverter076_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3530 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC Input 1 | Inverter | inverter076_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3531 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input2 | Inverter | inverter076_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3532 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC input 2 | Inverter | inverter076_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3533 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input3 | Inverter | inverter076_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3534 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC input 3 | Inverter | inverter076_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3535 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input4 | Inverter | inverter076_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3536 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC input 4 | Inverter | inverter076_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3537 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input5 | Inverter | inverter076_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3538 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC input 5 | Inverter | inverter076_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3539 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current DC Input6 | Inverter | inverter076_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3540 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC input 6 | Inverter | inverter076_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3541 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current-AC | Inverter | inverter076_MODBUS.HR1007_i3Avg_A | Current-AC | 3542 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Current-DC | Inverter | inverter076_MODBUS.HR1062_idcInput_A | Current-DC | 3543 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Daily Energy Delivered | Inverter | inverter076_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3544 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power Set Point | Inverter | inverter076_MODBUS.HR0553_pRef | Real Power Set Point | 3545 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Reactive Power Set Point | Inverter | inverter076_MODBUS.HR0558_qRef | Reactive Power Set Point | 3546 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Frequency | Inverter | inverter076_MODBUS.HR1012_f3_Hz | Frequency | 3547 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV076 | Dagget 3_SUB1_INV076_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Insulation Resistance | Inverter | inverter076_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3548 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Number of DU Channels | Inverter | inverter076_MODBUS.HR0653_duChannels | Number of DU Channels | 3549 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Number of Running Modules | Inverter | inverter076_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3550 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Operating State | Inverter | inverter076_MODBUS.HR1123_currentStatus | Operating State | 3551 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Power Factor | Inverter | inverter076_MODBUS.HR1011_pf3 | Power Factor | 3552 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV076 | Dagget 3_SUB1_INV076_Ramp Down | Inverter | inverter076_MODBUS.HR0286_dropGradient_p | Ramp Down | 3553 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Ramp Up | Inverter | inverter076_MODBUS.HR0282_riseGradient_p | Ramp Up | 3554 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power Delivered | Inverter | inverter076_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3555 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Reactive Power Delivered | Inverter | inverter076_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3556 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power | 3557 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Reactive Power | Inverter | inverter076_MODBUS.HR1009_q3_kvar | Reactive Power | 3558 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Reactive Power Mode | Inverter | inverter076_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3559 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Reactive Power Set Point Percent | Inverter | inverter076_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3560 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power AC Percent | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3561 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power-AC | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power-AC | 3562 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power-DC | Inverter | inverter076_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3563 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Air Intake | Inverter | inverter076_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3564 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Cabinet | Inverter | inverter076_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3565 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-IGBT | Inverter | inverter076_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3566 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Temperature-Module | Inverter | inverter076_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3567 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage A-B | Inverter | inverter076_MODBUS.HR1006_vRS_V | Voltage A-B | 3568 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage B-C | Inverter | inverter076_MODBUS.HR1002_vST_V | Voltage B-C | 3569 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage C-A | Inverter | inverter076_MODBUS.HR1003_vTR_V | Voltage C-A | 3570 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Voltage DC | Inverter | inverter076_MODBUS.HR1051_vdcBus_V | Voltage DC | 3571 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV077 | Dagget 3_SUB1_INV077_A Phase Current | Inverter | inverter077_MODBUS.HR1004_i1_A | A Phase Current | 3572 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_B Phase Current | Inverter | inverter077_MODBUS.HR1005_i2_A | B Phase Current | 3573 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_C Phase Current | Inverter | inverter077_MODBUS.HR1006_i3_A | C Phase Current | 3574 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Bus Voltage | Inverter | inverter077_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3575 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV077 | Dagget 3_SUB1_INV077_Apparent Power | Inverter | inverter077_MODBUS.HR1010_s3_VA | Apparent Power | 3576 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input1 | Inverter | inverter077_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3577 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC Input 1 | Inverter | inverter077_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3578 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input2 | Inverter | inverter077_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3579 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC input 2 | Inverter | inverter077_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3580 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input3 | Inverter | inverter077_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3581 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC input 3 | Inverter | inverter077_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3582 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input4 | Inverter | inverter077_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3583 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC input 4 | Inverter | inverter077_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3584 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input5 | Inverter | inverter077_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3585 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC input 5 | Inverter | inverter077_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3586 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current DC Input6 | Inverter | inverter077_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3587 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC input 6 | Inverter | inverter077_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3588 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current-AC | Inverter | inverter077_MODBUS.HR1007_i3Avg_A | Current-AC | 3589 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Current-DC | Inverter | inverter077_MODBUS.HR1062_idcInput_A | Current-DC | 3590 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Daily Energy Delivered | Inverter | inverter077_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3591 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power Set Point | Inverter | inverter077_MODBUS.HR0553_pRef | Real Power Set Point | 3592 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Reactive Power Set Point | Inverter | inverter077_MODBUS.HR0558_qRef | Reactive Power Set Point | 3593 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Frequency | Inverter | inverter077_MODBUS.HR1012_f3_Hz | Frequency | 3594 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV077 | Dagget 3_SUB1_INV077_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Insulation Resistance | Inverter | inverter077_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3595 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Number of DU Channels | Inverter | inverter077_MODBUS.HR0653_duChannels | Number of DU Channels | 3596 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Number of Running Modules | Inverter | inverter077_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3597 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Operating State | Inverter | inverter077_MODBUS.HR1123_currentStatus | Operating State | 3598 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Power Factor | Inverter | inverter077_MODBUS.HR1011_pf3 | Power Factor | 3599 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV077 | Dagget 3_SUB1_INV077_Ramp Down | Inverter | inverter077_MODBUS.HR0286_dropGradient_p | Ramp Down | 3600 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Ramp Up | Inverter | inverter077_MODBUS.HR0282_riseGradient_p | Ramp Up | 3601 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power Delivered | Inverter | inverter077_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3602 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Reactive Power Delivered | Inverter | inverter077_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3603 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power | 3604 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Reactive Power | Inverter | inverter077_MODBUS.HR1009_q3_kvar | Reactive Power | 3605 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Reactive Power Mode | Inverter | inverter077_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3606 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Reactive Power Set Point Percent | Inverter | inverter077_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3607 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power AC Percent | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3608 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power-AC | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power-AC | 3609 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power-DC | Inverter | inverter077_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3610 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Air Intake | Inverter | inverter077_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3611 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Cabinet | Inverter | inverter077_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3612 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-IGBT | Inverter | inverter077_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3613 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Temperature-Module | Inverter | inverter077_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3614 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage A-B | Inverter | inverter077_MODBUS.HR1007_vRS_V | Voltage A-B | 3615 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage B-C | Inverter | inverter077_MODBUS.HR1002_vST_V | Voltage B-C | 3616 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage C-A | Inverter | inverter077_MODBUS.HR1003_vTR_V | Voltage C-A | 3617 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Voltage DC | Inverter | inverter077_MODBUS.HR1051_vdcBus_V | Voltage DC | 3618 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV078 | Dagget 3_SUB1_INV078_A Phase Current | Inverter | inverter078_MODBUS.HR1004_i1_A | A Phase Current | 3619 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_B Phase Current | Inverter | inverter078_MODBUS.HR1005_i2_A | B Phase Current | 3620 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_C Phase Current | Inverter | inverter078_MODBUS.HR1006_i3_A | C Phase Current | 3621 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Bus Voltage | Inverter | inverter078_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3622 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV078 | Dagget 3_SUB1_INV078_Apparent Power | Inverter | inverter078_MODBUS.HR1010_s3_VA | Apparent Power | 3623 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input1 | Inverter | inverter078_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3624 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC Input 1 | Inverter | inverter078_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3625 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input2 | Inverter | inverter078_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3626 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC input 2 | Inverter | inverter078_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3627 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input3 | Inverter | inverter078_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3628 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC input 3 | Inverter | inverter078_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3629 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input4 | Inverter | inverter078_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3630 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC input 4 | Inverter | inverter078_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3631 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input5 | Inverter | inverter078_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3632 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC input 5 | Inverter | inverter078_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3633 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current DC Input6 | Inverter | inverter078_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3634 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC input 6 | Inverter | inverter078_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3635 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current-AC | Inverter | inverter078_MODBUS.HR1007_i3Avg_A | Current-AC | 3636 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Current-DC | Inverter | inverter078_MODBUS.HR1062_idcInput_A | Current-DC | 3637 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Daily Energy Delivered | Inverter | inverter078_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3638 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power Set Point | Inverter | inverter078_MODBUS.HR0553_pRef | Real Power Set Point | 3639 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Reactive Power Set Point | Inverter | inverter078_MODBUS.HR0558_qRef | Reactive Power Set Point | 3640 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Frequency | Inverter | inverter078_MODBUS.HR1012_f3_Hz | Frequency | 3641 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV078 | Dagget 3_SUB1_INV078_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Insulation Resistance | Inverter | inverter078_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3642 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Number of DU Channels | Inverter | inverter078_MODBUS.HR0653_duChannels | Number of DU Channels | 3643 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Number of Running Modules | Inverter | inverter078_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3644 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Operating State | Inverter | inverter078_MODBUS.HR1123_currentStatus | Operating State | 3645 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Power Factor | Inverter | inverter078_MODBUS.HR1011_pf3 | Power Factor | 3646 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV078 | Dagget 3_SUB1_INV078_Ramp Down | Inverter | inverter078_MODBUS.HR0286_dropGradient_p | Ramp Down | 3647 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Ramp Up | Inverter | inverter078_MODBUS.HR0282_riseGradient_p | Ramp Up | 3648 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power Delivered | Inverter | inverter078_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3649 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Reactive Power Delivered | Inverter | inverter078_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3650 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power | 3651 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Reactive Power | Inverter | inverter078_MODBUS.HR1009_q3_kvar | Reactive Power | 3652 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Reactive Power Mode | Inverter | inverter078_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3653 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Reactive Power Set Point Percent | Inverter | inverter078_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3654 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power AC Percent | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3655 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power-AC | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power-AC | 3656 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power-DC | Inverter | inverter078_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3657 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Air Intake | Inverter | inverter078_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3658 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Cabinet | Inverter | inverter078_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3659 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-IGBT | Inverter | inverter078_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3660 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Temperature-Module | Inverter | inverter078_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3661 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage A-B | Inverter | inverter078_MODBUS.HR1008_vRS_V | Voltage A-B | 3662 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage B-C | Inverter | inverter078_MODBUS.HR1002_vST_V | Voltage B-C | 3663 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage C-A | Inverter | inverter078_MODBUS.HR1003_vTR_V | Voltage C-A | 3664 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Voltage DC | Inverter | inverter078_MODBUS.HR1051_vdcBus_V | Voltage DC | 3665 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV079 | Dagget 3_SUB1_INV079_A Phase Current | Inverter | inverter079_MODBUS.HR1004_i1_A | A Phase Current | 3666 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_B Phase Current | Inverter | inverter079_MODBUS.HR1005_i2_A | B Phase Current | 3667 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_C Phase Current | Inverter | inverter079_MODBUS.HR1006_i3_A | C Phase Current | 3668 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Bus Voltage | Inverter | inverter079_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3669 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV079 | Dagget 3_SUB1_INV079_Apparent Power | Inverter | inverter079_MODBUS.HR1010_s3_VA | Apparent Power | 3670 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input1 | Inverter | inverter079_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3671 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC Input 1 | Inverter | inverter079_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3672 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input2 | Inverter | inverter079_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3673 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC input 2 | Inverter | inverter079_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3674 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input3 | Inverter | inverter079_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3675 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC input 3 | Inverter | inverter079_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3676 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input4 | Inverter | inverter079_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3677 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC input 4 | Inverter | inverter079_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3678 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input5 | Inverter | inverter079_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3679 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC input 5 | Inverter | inverter079_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3680 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current DC Input6 | Inverter | inverter079_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3681 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC input 6 | Inverter | inverter079_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3682 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current-AC | Inverter | inverter079_MODBUS.HR1007_i3Avg_A | Current-AC | 3683 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Current-DC | Inverter | inverter079_MODBUS.HR1062_idcInput_A | Current-DC | 3684 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Daily Energy Delivered | Inverter | inverter079_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3685 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power Set Point | Inverter | inverter079_MODBUS.HR0553_pRef | Real Power Set Point | 3686 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Reactive Power Set Point | Inverter | inverter079_MODBUS.HR0558_qRef | Reactive Power Set Point | 3687 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Frequency | Inverter | inverter079_MODBUS.HR1012_f3_Hz | Frequency | 3688 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV079 | Dagget 3_SUB1_INV079_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Insulation Resistance | Inverter | inverter079_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3689 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Number of DU Channels | Inverter | inverter079_MODBUS.HR0653_duChannels | Number of DU Channels | 3690 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Number of Running Modules | Inverter | inverter079_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3691 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Operating State | Inverter | inverter079_MODBUS.HR1123_currentStatus | Operating State | 3692 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Power Factor | Inverter | inverter079_MODBUS.HR1011_pf3 | Power Factor | 3693 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV079 | Dagget 3_SUB1_INV079_Ramp Down | Inverter | inverter079_MODBUS.HR0286_dropGradient_p | Ramp Down | 3694 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Ramp Up | Inverter | inverter079_MODBUS.HR0282_riseGradient_p | Ramp Up | 3695 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power Delivered | Inverter | inverter079_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3696 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Reactive Power Delivered | Inverter | inverter079_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3697 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power | 3698 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Reactive Power | Inverter | inverter079_MODBUS.HR1009_q3_kvar | Reactive Power | 3699 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Reactive Power Mode | Inverter | inverter079_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3700 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Reactive Power Set Point Percent | Inverter | inverter079_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3701 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power AC Percent | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3702 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power-AC | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power-AC | 3703 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power-DC | Inverter | inverter079_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3704 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Air Intake | Inverter | inverter079_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3705 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Cabinet | Inverter | inverter079_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3706 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-IGBT | Inverter | inverter079_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3707 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Temperature-Module | Inverter | inverter079_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3708 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage A-B | Inverter | inverter079_MODBUS.HR1009_vRS_V | Voltage A-B | 3709 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage B-C | Inverter | inverter079_MODBUS.HR1002_vST_V | Voltage B-C | 3710 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage C-A | Inverter | inverter079_MODBUS.HR1003_vTR_V | Voltage C-A | 3711 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Voltage DC | Inverter | inverter079_MODBUS.HR1051_vdcBus_V | Voltage DC | 3712 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV080 | Dagget 3_SUB1_INV080_A Phase Current | Inverter | inverter080_MODBUS.HR1004_i1_A | A Phase Current | 3713 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_B Phase Current | Inverter | inverter080_MODBUS.HR1005_i2_A | B Phase Current | 3714 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_C Phase Current | Inverter | inverter080_MODBUS.HR1006_i3_A | C Phase Current | 3715 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Bus Voltage | Inverter | inverter080_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3716 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV080 | Dagget 3_SUB1_INV080_Apparent Power | Inverter | inverter080_MODBUS.HR1010_s3_VA | Apparent Power | 3717 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input1 | Inverter | inverter080_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3718 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC Input 1 | Inverter | inverter080_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3719 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input2 | Inverter | inverter080_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3720 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC input 2 | Inverter | inverter080_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3721 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input3 | Inverter | inverter080_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3722 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC input 3 | Inverter | inverter080_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3723 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input4 | Inverter | inverter080_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3724 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC input 4 | Inverter | inverter080_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3725 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input5 | Inverter | inverter080_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3726 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC input 5 | Inverter | inverter080_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3727 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current DC Input6 | Inverter | inverter080_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3728 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC input 6 | Inverter | inverter080_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3729 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current-AC | Inverter | inverter080_MODBUS.HR1007_i3Avg_A | Current-AC | 3730 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Current-DC | Inverter | inverter080_MODBUS.HR1062_idcInput_A | Current-DC | 3731 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Daily Energy Delivered | Inverter | inverter080_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3732 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power Set Point | Inverter | inverter080_MODBUS.HR0553_pRef | Real Power Set Point | 3733 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Reactive Power Set Point | Inverter | inverter080_MODBUS.HR0558_qRef | Reactive Power Set Point | 3734 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Frequency | Inverter | inverter080_MODBUS.HR1012_f3_Hz | Frequency | 3735 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV080 | Dagget 3_SUB1_INV080_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Insulation Resistance | Inverter | inverter080_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3736 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Number of DU Channels | Inverter | inverter080_MODBUS.HR0653_duChannels | Number of DU Channels | 3737 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Number of Running Modules | Inverter | inverter080_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3738 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Operating State | Inverter | inverter080_MODBUS.HR1123_currentStatus | Operating State | 3739 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Power Factor | Inverter | inverter080_MODBUS.HR1011_pf3 | Power Factor | 3740 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV080 | Dagget 3_SUB1_INV080_Ramp Down | Inverter | inverter080_MODBUS.HR0286_dropGradient_p | Ramp Down | 3741 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Ramp Up | Inverter | inverter080_MODBUS.HR0282_riseGradient_p | Ramp Up | 3742 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power Delivered | Inverter | inverter080_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3743 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Reactive Power Delivered | Inverter | inverter080_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3744 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power | 3745 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Reactive Power | Inverter | inverter080_MODBUS.HR1009_q3_kvar | Reactive Power | 3746 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Reactive Power Mode | Inverter | inverter080_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3747 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Reactive Power Set Point Percent | Inverter | inverter080_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3748 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power AC Percent | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3749 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power-AC | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power-AC | 3750 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power-DC | Inverter | inverter080_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3751 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Air Intake | Inverter | inverter080_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3752 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Cabinet | Inverter | inverter080_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3753 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-IGBT | Inverter | inverter080_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3754 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Temperature-Module | Inverter | inverter080_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3755 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage A-B | Inverter | inverter080_MODBUS.HR1010_vRS_V | Voltage A-B | 3756 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage B-C | Inverter | inverter080_MODBUS.HR1002_vST_V | Voltage B-C | 3757 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage C-A | Inverter | inverter080_MODBUS.HR1003_vTR_V | Voltage C-A | 3758 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Voltage DC | Inverter | inverter080_MODBUS.HR1051_vdcBus_V | Voltage DC | 3759 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV081 | Dagget 3_SUB1_INV081_A Phase Current | Inverter | inverter081_MODBUS.HR1004_i1_A | A Phase Current | 3760 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_B Phase Current | Inverter | inverter081_MODBUS.HR1005_i2_A | B Phase Current | 3761 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_C Phase Current | Inverter | inverter081_MODBUS.HR1006_i3_A | C Phase Current | 3762 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Bus Voltage | Inverter | inverter081_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3763 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV081 | Dagget 3_SUB1_INV081_Apparent Power | Inverter | inverter081_MODBUS.HR1010_s3_VA | Apparent Power | 3764 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input1 | Inverter | inverter081_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3765 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC Input 1 | Inverter | inverter081_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3766 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input2 | Inverter | inverter081_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3767 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC input 2 | Inverter | inverter081_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3768 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input3 | Inverter | inverter081_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3769 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC input 3 | Inverter | inverter081_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3770 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input4 | Inverter | inverter081_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3771 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC input 4 | Inverter | inverter081_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3772 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input5 | Inverter | inverter081_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3773 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC input 5 | Inverter | inverter081_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3774 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current DC Input6 | Inverter | inverter081_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3775 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC input 6 | Inverter | inverter081_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3776 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current-AC | Inverter | inverter081_MODBUS.HR1007_i3Avg_A | Current-AC | 3777 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Current-DC | Inverter | inverter081_MODBUS.HR1062_idcInput_A | Current-DC | 3778 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Daily Energy Delivered | Inverter | inverter081_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3779 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power Set Point | Inverter | inverter081_MODBUS.HR0553_pRef | Real Power Set Point | 3780 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Reactive Power Set Point | Inverter | inverter081_MODBUS.HR0558_qRef | Reactive Power Set Point | 3781 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Frequency | Inverter | inverter081_MODBUS.HR1012_f3_Hz | Frequency | 3782 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV081 | Dagget 3_SUB1_INV081_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Insulation Resistance | Inverter | inverter081_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3783 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Number of DU Channels | Inverter | inverter081_MODBUS.HR0653_duChannels | Number of DU Channels | 3784 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Number of Running Modules | Inverter | inverter081_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3785 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Operating State | Inverter | inverter081_MODBUS.HR1123_currentStatus | Operating State | 3786 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Power Factor | Inverter | inverter081_MODBUS.HR1011_pf3 | Power Factor | 3787 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV081 | Dagget 3_SUB1_INV081_Ramp Down | Inverter | inverter081_MODBUS.HR0286_dropGradient_p | Ramp Down | 3788 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Ramp Up | Inverter | inverter081_MODBUS.HR0282_riseGradient_p | Ramp Up | 3789 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power Delivered | Inverter | inverter081_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3790 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Reactive Power Delivered | Inverter | inverter081_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3791 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power | 3792 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Reactive Power | Inverter | inverter081_MODBUS.HR1009_q3_kvar | Reactive Power | 3793 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Reactive Power Mode | Inverter | inverter081_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3794 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Reactive Power Set Point Percent | Inverter | inverter081_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3795 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power AC Percent | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3796 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power-AC | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power-AC | 3797 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power-DC | Inverter | inverter081_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3798 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Air Intake | Inverter | inverter081_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3799 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Cabinet | Inverter | inverter081_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3800 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-IGBT | Inverter | inverter081_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3801 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Temperature-Module | Inverter | inverter081_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3802 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage A-B | Inverter | inverter081_MODBUS.HR1001_vRS_V | Voltage A-B | 3803 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage B-C | Inverter | inverter081_MODBUS.HR1002_vST_V | Voltage B-C | 3804 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage C-A | Inverter | inverter081_MODBUS.HR1003_vTR_V | Voltage C-A | 3805 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Voltage DC | Inverter | inverter081_MODBUS.HR1051_vdcBus_V | Voltage DC | 3806 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV082 | Dagget 3_SUB1_INV082_A Phase Current | Inverter | inverter082_MODBUS.HR1004_i1_A | A Phase Current | 3807 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_B Phase Current | Inverter | inverter082_MODBUS.HR1005_i2_A | B Phase Current | 3808 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_C Phase Current | Inverter | inverter082_MODBUS.HR1006_i3_A | C Phase Current | 3809 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Bus Voltage | Inverter | inverter082_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3810 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV082 | Dagget 3_SUB1_INV082_Apparent Power | Inverter | inverter082_MODBUS.HR1010_s3_VA | Apparent Power | 3811 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input1 | Inverter | inverter082_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3812 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC Input 1 | Inverter | inverter082_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3813 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input2 | Inverter | inverter082_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3814 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC input 2 | Inverter | inverter082_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3815 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input3 | Inverter | inverter082_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3816 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC input 3 | Inverter | inverter082_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3817 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input4 | Inverter | inverter082_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3818 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC input 4 | Inverter | inverter082_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3819 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input5 | Inverter | inverter082_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3820 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC input 5 | Inverter | inverter082_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3821 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current DC Input6 | Inverter | inverter082_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3822 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC input 6 | Inverter | inverter082_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3823 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current-AC | Inverter | inverter082_MODBUS.HR1007_i3Avg_A | Current-AC | 3824 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Current-DC | Inverter | inverter082_MODBUS.HR1062_idcInput_A | Current-DC | 3825 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Daily Energy Delivered | Inverter | inverter082_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3826 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power Set Point | Inverter | inverter082_MODBUS.HR0553_pRef | Real Power Set Point | 3827 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Reactive Power Set Point | Inverter | inverter082_MODBUS.HR0558_qRef | Reactive Power Set Point | 3828 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Frequency | Inverter | inverter082_MODBUS.HR1012_f3_Hz | Frequency | 3829 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV082 | Dagget 3_SUB1_INV082_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Insulation Resistance | Inverter | inverter082_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3830 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Number of DU Channels | Inverter | inverter082_MODBUS.HR0653_duChannels | Number of DU Channels | 3831 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Number of Running Modules | Inverter | inverter082_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3832 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Operating State | Inverter | inverter082_MODBUS.HR1123_currentStatus | Operating State | 3833 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Power Factor | Inverter | inverter082_MODBUS.HR1011_pf3 | Power Factor | 3834 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV082 | Dagget 3_SUB1_INV082_Ramp Down | Inverter | inverter082_MODBUS.HR0286_dropGradient_p | Ramp Down | 3835 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Ramp Up | Inverter | inverter082_MODBUS.HR0282_riseGradient_p | Ramp Up | 3836 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power Delivered | Inverter | inverter082_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3837 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Reactive Power Delivered | Inverter | inverter082_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3838 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power | 3839 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Reactive Power | Inverter | inverter082_MODBUS.HR1009_q3_kvar | Reactive Power | 3840 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Reactive Power Mode | Inverter | inverter082_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3841 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Reactive Power Set Point Percent | Inverter | inverter082_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3842 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power AC Percent | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3843 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power-AC | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power-AC | 3844 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power-DC | Inverter | inverter082_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3845 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Air Intake | Inverter | inverter082_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3846 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Cabinet | Inverter | inverter082_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3847 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-IGBT | Inverter | inverter082_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3848 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Temperature-Module | Inverter | inverter082_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3849 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage A-B | Inverter | inverter082_MODBUS.HR1002_vRS_V | Voltage A-B | 3850 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage B-C | Inverter | inverter082_MODBUS.HR1002_vST_V | Voltage B-C | 3851 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage C-A | Inverter | inverter082_MODBUS.HR1003_vTR_V | Voltage C-A | 3852 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Voltage DC | Inverter | inverter082_MODBUS.HR1051_vdcBus_V | Voltage DC | 3853 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV083 | Dagget 3_SUB1_INV083_A Phase Current | Inverter | inverter083_MODBUS.HR1004_i1_A | A Phase Current | 3854 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_B Phase Current | Inverter | inverter083_MODBUS.HR1005_i2_A | B Phase Current | 3855 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_C Phase Current | Inverter | inverter083_MODBUS.HR1006_i3_A | C Phase Current | 3856 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Bus Voltage | Inverter | inverter083_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3857 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV083 | Dagget 3_SUB1_INV083_Apparent Power | Inverter | inverter083_MODBUS.HR1010_s3_VA | Apparent Power | 3858 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input1 | Inverter | inverter083_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3859 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC Input 1 | Inverter | inverter083_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3860 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input2 | Inverter | inverter083_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3861 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC input 2 | Inverter | inverter083_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3862 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input3 | Inverter | inverter083_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3863 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC input 3 | Inverter | inverter083_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3864 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input4 | Inverter | inverter083_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3865 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC input 4 | Inverter | inverter083_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3866 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input5 | Inverter | inverter083_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3867 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC input 5 | Inverter | inverter083_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3868 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current DC Input6 | Inverter | inverter083_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3869 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC input 6 | Inverter | inverter083_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3870 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current-AC | Inverter | inverter083_MODBUS.HR1007_i3Avg_A | Current-AC | 3871 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Current-DC | Inverter | inverter083_MODBUS.HR1062_idcInput_A | Current-DC | 3872 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Daily Energy Delivered | Inverter | inverter083_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3873 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power Set Point | Inverter | inverter083_MODBUS.HR0553_pRef | Real Power Set Point | 3874 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Reactive Power Set Point | Inverter | inverter083_MODBUS.HR0558_qRef | Reactive Power Set Point | 3875 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Frequency | Inverter | inverter083_MODBUS.HR1012_f3_Hz | Frequency | 3876 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV083 | Dagget 3_SUB1_INV083_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Insulation Resistance | Inverter | inverter083_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3877 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Number of DU Channels | Inverter | inverter083_MODBUS.HR0653_duChannels | Number of DU Channels | 3878 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Number of Running Modules | Inverter | inverter083_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3879 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Operating State | Inverter | inverter083_MODBUS.HR1123_currentStatus | Operating State | 3880 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Power Factor | Inverter | inverter083_MODBUS.HR1011_pf3 | Power Factor | 3881 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV083 | Dagget 3_SUB1_INV083_Ramp Down | Inverter | inverter083_MODBUS.HR0286_dropGradient_p | Ramp Down | 3882 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Ramp Up | Inverter | inverter083_MODBUS.HR0282_riseGradient_p | Ramp Up | 3883 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power Delivered | Inverter | inverter083_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3884 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Reactive Power Delivered | Inverter | inverter083_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3885 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power | 3886 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Reactive Power | Inverter | inverter083_MODBUS.HR1009_q3_kvar | Reactive Power | 3887 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Reactive Power Mode | Inverter | inverter083_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3888 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Reactive Power Set Point Percent | Inverter | inverter083_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3889 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power AC Percent | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3890 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power-AC | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power-AC | 3891 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power-DC | Inverter | inverter083_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3892 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Air Intake | Inverter | inverter083_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3893 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Cabinet | Inverter | inverter083_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3894 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-IGBT | Inverter | inverter083_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3895 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Temperature-Module | Inverter | inverter083_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3896 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage A-B | Inverter | inverter083_MODBUS.HR1003_vRS_V | Voltage A-B | 3897 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage B-C | Inverter | inverter083_MODBUS.HR1002_vST_V | Voltage B-C | 3898 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage C-A | Inverter | inverter083_MODBUS.HR1003_vTR_V | Voltage C-A | 3899 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Voltage DC | Inverter | inverter083_MODBUS.HR1051_vdcBus_V | Voltage DC | 3900 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV084 | Dagget 3_SUB1_INV084_A Phase Current | Inverter | inverter084_MODBUS.HR1004_i1_A | A Phase Current | 3901 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_B Phase Current | Inverter | inverter084_MODBUS.HR1005_i2_A | B Phase Current | 3902 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_C Phase Current | Inverter | inverter084_MODBUS.HR1006_i3_A | C Phase Current | 3903 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Bus Voltage | Inverter | inverter084_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3904 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV084 | Dagget 3_SUB1_INV084_Apparent Power | Inverter | inverter084_MODBUS.HR1010_s3_VA | Apparent Power | 3905 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input1 | Inverter | inverter084_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3906 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC Input 1 | Inverter | inverter084_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3907 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input2 | Inverter | inverter084_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3908 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC input 2 | Inverter | inverter084_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3909 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input3 | Inverter | inverter084_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3910 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC input 3 | Inverter | inverter084_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3911 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input4 | Inverter | inverter084_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3912 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC input 4 | Inverter | inverter084_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3913 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input5 | Inverter | inverter084_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3914 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC input 5 | Inverter | inverter084_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3915 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current DC Input6 | Inverter | inverter084_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3916 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC input 6 | Inverter | inverter084_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3917 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current-AC | Inverter | inverter084_MODBUS.HR1007_i3Avg_A | Current-AC | 3918 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Current-DC | Inverter | inverter084_MODBUS.HR1062_idcInput_A | Current-DC | 3919 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Daily Energy Delivered | Inverter | inverter084_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3920 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power Set Point | Inverter | inverter084_MODBUS.HR0553_pRef | Real Power Set Point | 3921 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Reactive Power Set Point | Inverter | inverter084_MODBUS.HR0558_qRef | Reactive Power Set Point | 3922 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Frequency | Inverter | inverter084_MODBUS.HR1012_f3_Hz | Frequency | 3923 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV084 | Dagget 3_SUB1_INV084_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Insulation Resistance | Inverter | inverter084_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3924 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Number of DU Channels | Inverter | inverter084_MODBUS.HR0653_duChannels | Number of DU Channels | 3925 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Number of Running Modules | Inverter | inverter084_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3926 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Operating State | Inverter | inverter084_MODBUS.HR1123_currentStatus | Operating State | 3927 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Power Factor | Inverter | inverter084_MODBUS.HR1011_pf3 | Power Factor | 3928 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV084 | Dagget 3_SUB1_INV084_Ramp Down | Inverter | inverter084_MODBUS.HR0286_dropGradient_p | Ramp Down | 3929 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Ramp Up | Inverter | inverter084_MODBUS.HR0282_riseGradient_p | Ramp Up | 3930 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power Delivered | Inverter | inverter084_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3931 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Reactive Power Delivered | Inverter | inverter084_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3932 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power | 3933 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Reactive Power | Inverter | inverter084_MODBUS.HR1009_q3_kvar | Reactive Power | 3934 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Reactive Power Mode | Inverter | inverter084_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3935 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Reactive Power Set Point Percent | Inverter | inverter084_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3936 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power AC Percent | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3937 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power-AC | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power-AC | 3938 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power-DC | Inverter | inverter084_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3939 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Air Intake | Inverter | inverter084_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3940 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Cabinet | Inverter | inverter084_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3941 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-IGBT | Inverter | inverter084_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3942 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Temperature-Module | Inverter | inverter084_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3943 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage A-B | Inverter | inverter084_MODBUS.HR1004_vRS_V | Voltage A-B | 3944 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage B-C | Inverter | inverter084_MODBUS.HR1002_vST_V | Voltage B-C | 3945 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage C-A | Inverter | inverter084_MODBUS.HR1003_vTR_V | Voltage C-A | 3946 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Voltage DC | Inverter | inverter084_MODBUS.HR1051_vdcBus_V | Voltage DC | 3947 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV085 | Dagget 3_SUB1_INV085_A Phase Current | Inverter | inverter085_MODBUS.HR1004_i1_A | A Phase Current | 3948 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_B Phase Current | Inverter | inverter085_MODBUS.HR1005_i2_A | B Phase Current | 3949 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_C Phase Current | Inverter | inverter085_MODBUS.HR1006_i3_A | C Phase Current | 3950 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Bus Voltage | Inverter | inverter085_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3951 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV085 | Dagget 3_SUB1_INV085_Apparent Power | Inverter | inverter085_MODBUS.HR1010_s3_VA | Apparent Power | 3952 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input1 | Inverter | inverter085_MODBUS.HR5005_m1_idc_A | Current DC Input# | 3953 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC Input 1 | Inverter | inverter085_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 3954 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input2 | Inverter | inverter085_MODBUS.HR5037_m2_idc_A | Current DC Input# | 3955 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC input 2 | Inverter | inverter085_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 3956 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input3 | Inverter | inverter085_MODBUS.HR5069_m3_idc_A | Current DC Input# | 3957 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC input 3 | Inverter | inverter085_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 3958 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input4 | Inverter | inverter085_MODBUS.HR5101_m4_idc_A | Current DC Input# | 3959 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC input 4 | Inverter | inverter085_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 3960 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input5 | Inverter | inverter085_MODBUS.HR5133_m5_idc_A | Current DC Input# | 3961 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC input 5 | Inverter | inverter085_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 3962 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current DC Input6 | Inverter | inverter085_MODBUS.HR5165_m6_idc_A | Current DC Input# | 3963 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC input 6 | Inverter | inverter085_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 3964 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current-AC | Inverter | inverter085_MODBUS.HR1007_i3Avg_A | Current-AC | 3965 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Current-DC | Inverter | inverter085_MODBUS.HR1062_idcInput_A | Current-DC | 3966 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Daily Energy Delivered | Inverter | inverter085_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3967 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power Set Point | Inverter | inverter085_MODBUS.HR0553_pRef | Real Power Set Point | 3968 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Reactive Power Set Point | Inverter | inverter085_MODBUS.HR0558_qRef | Reactive Power Set Point | 3969 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Frequency | Inverter | inverter085_MODBUS.HR1012_f3_Hz | Frequency | 3970 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV085 | Dagget 3_SUB1_INV085_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Insulation Resistance | Inverter | inverter085_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3971 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Number of DU Channels | Inverter | inverter085_MODBUS.HR0653_duChannels | Number of DU Channels | 3972 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Number of Running Modules | Inverter | inverter085_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3973 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Operating State | Inverter | inverter085_MODBUS.HR1123_currentStatus | Operating State | 3974 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Power Factor | Inverter | inverter085_MODBUS.HR1011_pf3 | Power Factor | 3975 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV085 | Dagget 3_SUB1_INV085_Ramp Down | Inverter | inverter085_MODBUS.HR0286_dropGradient_p | Ramp Down | 3976 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Ramp Up | Inverter | inverter085_MODBUS.HR0282_riseGradient_p | Ramp Up | 3977 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power Delivered | Inverter | inverter085_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3978 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Reactive Power Delivered | Inverter | inverter085_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3979 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power | 3980 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Reactive Power | Inverter | inverter085_MODBUS.HR1009_q3_kvar | Reactive Power | 3981 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Reactive Power Mode | Inverter | inverter085_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3982 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Reactive Power Set Point Percent | Inverter | inverter085_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3983 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power AC Percent | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3984 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power-AC | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power-AC | 3985 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power-DC | Inverter | inverter085_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3986 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Air Intake | Inverter | inverter085_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3987 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Cabinet | Inverter | inverter085_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3988 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-IGBT | Inverter | inverter085_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3989 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Temperature-Module | Inverter | inverter085_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3990 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage A-B | Inverter | inverter085_MODBUS.HR1005_vRS_V | Voltage A-B | 3991 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage B-C | Inverter | inverter085_MODBUS.HR1002_vST_V | Voltage B-C | 3992 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage C-A | Inverter | inverter085_MODBUS.HR1003_vTR_V | Voltage C-A | 3993 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Voltage DC | Inverter | inverter085_MODBUS.HR1051_vdcBus_V | Voltage DC | 3994 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV086 | Dagget 3_SUB1_INV086_A Phase Current | Inverter | inverter086_MODBUS.HR1004_i1_A | A Phase Current | 3995 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_B Phase Current | Inverter | inverter086_MODBUS.HR1005_i2_A | B Phase Current | 3996 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_C Phase Current | Inverter | inverter086_MODBUS.HR1006_i3_A | C Phase Current | 3997 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Bus Voltage | Inverter | inverter086_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3998 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV086 | Dagget 3_SUB1_INV086_Apparent Power | Inverter | inverter086_MODBUS.HR1010_s3_VA | Apparent Power | 3999 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input1 | Inverter | inverter086_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4000 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC Input 1 | Inverter | inverter086_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4001 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input2 | Inverter | inverter086_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4002 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC input 2 | Inverter | inverter086_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4003 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input3 | Inverter | inverter086_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4004 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC input 3 | Inverter | inverter086_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4005 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input4 | Inverter | inverter086_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4006 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC input 4 | Inverter | inverter086_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4007 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input5 | Inverter | inverter086_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4008 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC input 5 | Inverter | inverter086_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4009 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current DC Input6 | Inverter | inverter086_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4010 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC input 6 | Inverter | inverter086_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4011 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current-AC | Inverter | inverter086_MODBUS.HR1007_i3Avg_A | Current-AC | 4012 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Current-DC | Inverter | inverter086_MODBUS.HR1062_idcInput_A | Current-DC | 4013 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Daily Energy Delivered | Inverter | inverter086_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4014 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power Set Point | Inverter | inverter086_MODBUS.HR0553_pRef | Real Power Set Point | 4015 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Reactive Power Set Point | Inverter | inverter086_MODBUS.HR0558_qRef | Reactive Power Set Point | 4016 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Frequency | Inverter | inverter086_MODBUS.HR1012_f3_Hz | Frequency | 4017 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV086 | Dagget 3_SUB1_INV086_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Insulation Resistance | Inverter | inverter086_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4018 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Number of DU Channels | Inverter | inverter086_MODBUS.HR0653_duChannels | Number of DU Channels | 4019 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Number of Running Modules | Inverter | inverter086_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4020 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Operating State | Inverter | inverter086_MODBUS.HR1123_currentStatus | Operating State | 4021 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Power Factor | Inverter | inverter086_MODBUS.HR1011_pf3 | Power Factor | 4022 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV086 | Dagget 3_SUB1_INV086_Ramp Down | Inverter | inverter086_MODBUS.HR0286_dropGradient_p | Ramp Down | 4023 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Ramp Up | Inverter | inverter086_MODBUS.HR0282_riseGradient_p | Ramp Up | 4024 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power Delivered | Inverter | inverter086_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4025 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Reactive Power Delivered | Inverter | inverter086_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4026 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power | 4027 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Reactive Power | Inverter | inverter086_MODBUS.HR1009_q3_kvar | Reactive Power | 4028 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Reactive Power Mode | Inverter | inverter086_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4029 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Reactive Power Set Point Percent | Inverter | inverter086_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4030 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power AC Percent | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4031 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power-AC | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power-AC | 4032 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power-DC | Inverter | inverter086_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4033 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Air Intake | Inverter | inverter086_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4034 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Cabinet | Inverter | inverter086_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4035 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-IGBT | Inverter | inverter086_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4036 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Temperature-Module | Inverter | inverter086_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4037 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage A-B | Inverter | inverter086_MODBUS.HR1006_vRS_V | Voltage A-B | 4038 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage B-C | Inverter | inverter086_MODBUS.HR1002_vST_V | Voltage B-C | 4039 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage C-A | Inverter | inverter086_MODBUS.HR1003_vTR_V | Voltage C-A | 4040 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Voltage DC | Inverter | inverter086_MODBUS.HR1051_vdcBus_V | Voltage DC | 4041 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV087 | Dagget 3_SUB1_INV087_A Phase Current | Inverter | inverter087_MODBUS.HR1004_i1_A | A Phase Current | 4042 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_B Phase Current | Inverter | inverter087_MODBUS.HR1005_i2_A | B Phase Current | 4043 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_C Phase Current | Inverter | inverter087_MODBUS.HR1006_i3_A | C Phase Current | 4044 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Bus Voltage | Inverter | inverter087_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4045 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV087 | Dagget 3_SUB1_INV087_Apparent Power | Inverter | inverter087_MODBUS.HR1010_s3_VA | Apparent Power | 4046 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input1 | Inverter | inverter087_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4047 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC Input 1 | Inverter | inverter087_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4048 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input2 | Inverter | inverter087_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4049 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC input 2 | Inverter | inverter087_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4050 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input3 | Inverter | inverter087_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4051 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC input 3 | Inverter | inverter087_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4052 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input4 | Inverter | inverter087_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4053 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC input 4 | Inverter | inverter087_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4054 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input5 | Inverter | inverter087_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4055 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC input 5 | Inverter | inverter087_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4056 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current DC Input6 | Inverter | inverter087_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4057 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC input 6 | Inverter | inverter087_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4058 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current-AC | Inverter | inverter087_MODBUS.HR1007_i3Avg_A | Current-AC | 4059 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Current-DC | Inverter | inverter087_MODBUS.HR1062_idcInput_A | Current-DC | 4060 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Daily Energy Delivered | Inverter | inverter087_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4061 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power Set Point | Inverter | inverter087_MODBUS.HR0553_pRef | Real Power Set Point | 4062 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Reactive Power Set Point | Inverter | inverter087_MODBUS.HR0558_qRef | Reactive Power Set Point | 4063 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Frequency | Inverter | inverter087_MODBUS.HR1012_f3_Hz | Frequency | 4064 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV087 | Dagget 3_SUB1_INV087_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Insulation Resistance | Inverter | inverter087_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4065 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Number of DU Channels | Inverter | inverter087_MODBUS.HR0653_duChannels | Number of DU Channels | 4066 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Number of Running Modules | Inverter | inverter087_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4067 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Operating State | Inverter | inverter087_MODBUS.HR1123_currentStatus | Operating State | 4068 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Power Factor | Inverter | inverter087_MODBUS.HR1011_pf3 | Power Factor | 4069 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV087 | Dagget 3_SUB1_INV087_Ramp Down | Inverter | inverter087_MODBUS.HR0286_dropGradient_p | Ramp Down | 4070 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Ramp Up | Inverter | inverter087_MODBUS.HR0282_riseGradient_p | Ramp Up | 4071 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power Delivered | Inverter | inverter087_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4072 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Reactive Power Delivered | Inverter | inverter087_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4073 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power | 4074 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Reactive Power | Inverter | inverter087_MODBUS.HR1009_q3_kvar | Reactive Power | 4075 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Reactive Power Mode | Inverter | inverter087_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4076 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Reactive Power Set Point Percent | Inverter | inverter087_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4077 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power AC Percent | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4078 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power-AC | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power-AC | 4079 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power-DC | Inverter | inverter087_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4080 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Air Intake | Inverter | inverter087_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4081 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Cabinet | Inverter | inverter087_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4082 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-IGBT | Inverter | inverter087_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4083 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Temperature-Module | Inverter | inverter087_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4084 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage A-B | Inverter | inverter087_MODBUS.HR1007_vRS_V | Voltage A-B | 4085 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage B-C | Inverter | inverter087_MODBUS.HR1002_vST_V | Voltage B-C | 4086 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage C-A | Inverter | inverter087_MODBUS.HR1003_vTR_V | Voltage C-A | 4087 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Voltage DC | Inverter | inverter087_MODBUS.HR1051_vdcBus_V | Voltage DC | 4088 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV088 | Dagget 3_SUB1_INV088_A Phase Current | Inverter | inverter088_MODBUS.HR1004_i1_A | A Phase Current | 4089 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_B Phase Current | Inverter | inverter088_MODBUS.HR1005_i2_A | B Phase Current | 4090 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_C Phase Current | Inverter | inverter088_MODBUS.HR1006_i3_A | C Phase Current | 4091 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Bus Voltage | Inverter | inverter088_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4092 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV088 | Dagget 3_SUB1_INV088_Apparent Power | Inverter | inverter088_MODBUS.HR1010_s3_VA | Apparent Power | 4093 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input1 | Inverter | inverter088_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4094 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC Input 1 | Inverter | inverter088_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4095 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input2 | Inverter | inverter088_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4096 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC input 2 | Inverter | inverter088_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4097 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input3 | Inverter | inverter088_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4098 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC input 3 | Inverter | inverter088_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4099 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input4 | Inverter | inverter088_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4100 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC input 4 | Inverter | inverter088_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4101 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input5 | Inverter | inverter088_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4102 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC input 5 | Inverter | inverter088_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4103 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current DC Input6 | Inverter | inverter088_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4104 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC input 6 | Inverter | inverter088_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4105 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current-AC | Inverter | inverter088_MODBUS.HR1007_i3Avg_A | Current-AC | 4106 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Current-DC | Inverter | inverter088_MODBUS.HR1062_idcInput_A | Current-DC | 4107 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Daily Energy Delivered | Inverter | inverter088_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4108 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power Set Point | Inverter | inverter088_MODBUS.HR0553_pRef | Real Power Set Point | 4109 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Reactive Power Set Point | Inverter | inverter088_MODBUS.HR0558_qRef | Reactive Power Set Point | 4110 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Frequency | Inverter | inverter088_MODBUS.HR1012_f3_Hz | Frequency | 4111 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV088 | Dagget 3_SUB1_INV088_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Insulation Resistance | Inverter | inverter088_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4112 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Number of DU Channels | Inverter | inverter088_MODBUS.HR0653_duChannels | Number of DU Channels | 4113 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Number of Running Modules | Inverter | inverter088_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4114 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Operating State | Inverter | inverter088_MODBUS.HR1123_currentStatus | Operating State | 4115 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Power Factor | Inverter | inverter088_MODBUS.HR1011_pf3 | Power Factor | 4116 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV088 | Dagget 3_SUB1_INV088_Ramp Down | Inverter | inverter088_MODBUS.HR0286_dropGradient_p | Ramp Down | 4117 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Ramp Up | Inverter | inverter088_MODBUS.HR0282_riseGradient_p | Ramp Up | 4118 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power Delivered | Inverter | inverter088_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4119 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Reactive Power Delivered | Inverter | inverter088_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4120 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power | 4121 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Reactive Power | Inverter | inverter088_MODBUS.HR1009_q3_kvar | Reactive Power | 4122 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Reactive Power Mode | Inverter | inverter088_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4123 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Reactive Power Set Point Percent | Inverter | inverter088_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4124 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power AC Percent | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4125 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power-AC | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power-AC | 4126 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power-DC | Inverter | inverter088_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4127 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Air Intake | Inverter | inverter088_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4128 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Cabinet | Inverter | inverter088_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4129 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-IGBT | Inverter | inverter088_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4130 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Temperature-Module | Inverter | inverter088_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4131 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage A-B | Inverter | inverter088_MODBUS.HR1008_vRS_V | Voltage A-B | 4132 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage B-C | Inverter | inverter088_MODBUS.HR1002_vST_V | Voltage B-C | 4133 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage C-A | Inverter | inverter088_MODBUS.HR1003_vTR_V | Voltage C-A | 4134 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Voltage DC | Inverter | inverter088_MODBUS.HR1051_vdcBus_V | Voltage DC | 4135 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV089 | Dagget 3_SUB1_INV089_A Phase Current | Inverter | inverter089_MODBUS.HR1004_i1_A | A Phase Current | 4136 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_B Phase Current | Inverter | inverter089_MODBUS.HR1005_i2_A | B Phase Current | 4137 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_C Phase Current | Inverter | inverter089_MODBUS.HR1006_i3_A | C Phase Current | 4138 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Bus Voltage | Inverter | inverter089_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4139 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV089 | Dagget 3_SUB1_INV089_Apparent Power | Inverter | inverter089_MODBUS.HR1010_s3_VA | Apparent Power | 4140 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input1 | Inverter | inverter089_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4141 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC Input 1 | Inverter | inverter089_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4142 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input2 | Inverter | inverter089_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4143 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC input 2 | Inverter | inverter089_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4144 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input3 | Inverter | inverter089_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4145 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC input 3 | Inverter | inverter089_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4146 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input4 | Inverter | inverter089_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4147 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC input 4 | Inverter | inverter089_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4148 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input5 | Inverter | inverter089_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4149 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC input 5 | Inverter | inverter089_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4150 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current DC Input6 | Inverter | inverter089_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4151 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC input 6 | Inverter | inverter089_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4152 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current-AC | Inverter | inverter089_MODBUS.HR1007_i3Avg_A | Current-AC | 4153 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Current-DC | Inverter | inverter089_MODBUS.HR1062_idcInput_A | Current-DC | 4154 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Daily Energy Delivered | Inverter | inverter089_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4155 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power Set Point | Inverter | inverter089_MODBUS.HR0553_pRef | Real Power Set Point | 4156 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Reactive Power Set Point | Inverter | inverter089_MODBUS.HR0558_qRef | Reactive Power Set Point | 4157 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Frequency | Inverter | inverter089_MODBUS.HR1012_f3_Hz | Frequency | 4158 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV089 | Dagget 3_SUB1_INV089_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Insulation Resistance | Inverter | inverter089_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4159 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Number of DU Channels | Inverter | inverter089_MODBUS.HR0653_duChannels | Number of DU Channels | 4160 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Number of Running Modules | Inverter | inverter089_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4161 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Operating State | Inverter | inverter089_MODBUS.HR1123_currentStatus | Operating State | 4162 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Power Factor | Inverter | inverter089_MODBUS.HR1011_pf3 | Power Factor | 4163 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV089 | Dagget 3_SUB1_INV089_Ramp Down | Inverter | inverter089_MODBUS.HR0286_dropGradient_p | Ramp Down | 4164 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Ramp Up | Inverter | inverter089_MODBUS.HR0282_riseGradient_p | Ramp Up | 4165 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power Delivered | Inverter | inverter089_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4166 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Reactive Power Delivered | Inverter | inverter089_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4167 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power | 4168 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Reactive Power | Inverter | inverter089_MODBUS.HR1009_q3_kvar | Reactive Power | 4169 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Reactive Power Mode | Inverter | inverter089_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4170 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Reactive Power Set Point Percent | Inverter | inverter089_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4171 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power AC Percent | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4172 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power-AC | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power-AC | 4173 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power-DC | Inverter | inverter089_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4174 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Air Intake | Inverter | inverter089_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4175 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Cabinet | Inverter | inverter089_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4176 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-IGBT | Inverter | inverter089_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4177 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Temperature-Module | Inverter | inverter089_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4178 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage A-B | Inverter | inverter089_MODBUS.HR1009_vRS_V | Voltage A-B | 4179 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage B-C | Inverter | inverter089_MODBUS.HR1002_vST_V | Voltage B-C | 4180 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage C-A | Inverter | inverter089_MODBUS.HR1003_vTR_V | Voltage C-A | 4181 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Voltage DC | Inverter | inverter089_MODBUS.HR1051_vdcBus_V | Voltage DC | 4182 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV090 | Dagget 3_SUB1_INV090_A Phase Current | Inverter | inverter090_MODBUS.HR1004_i1_A | A Phase Current | 4183 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_B Phase Current | Inverter | inverter090_MODBUS.HR1005_i2_A | B Phase Current | 4184 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_C Phase Current | Inverter | inverter090_MODBUS.HR1006_i3_A | C Phase Current | 4185 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Bus Voltage | Inverter | inverter090_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4186 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV090 | Dagget 3_SUB1_INV090_Apparent Power | Inverter | inverter090_MODBUS.HR1010_s3_VA | Apparent Power | 4187 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input1 | Inverter | inverter090_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4188 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC Input 1 | Inverter | inverter090_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4189 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input2 | Inverter | inverter090_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4190 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC input 2 | Inverter | inverter090_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4191 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input3 | Inverter | inverter090_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4192 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC input 3 | Inverter | inverter090_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4193 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input4 | Inverter | inverter090_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4194 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC input 4 | Inverter | inverter090_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4195 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input5 | Inverter | inverter090_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4196 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC input 5 | Inverter | inverter090_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4197 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current DC Input6 | Inverter | inverter090_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4198 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC input 6 | Inverter | inverter090_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4199 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current-AC | Inverter | inverter090_MODBUS.HR1007_i3Avg_A | Current-AC | 4200 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Current-DC | Inverter | inverter090_MODBUS.HR1062_idcInput_A | Current-DC | 4201 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Daily Energy Delivered | Inverter | inverter090_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4202 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power Set Point | Inverter | inverter090_MODBUS.HR0553_pRef | Real Power Set Point | 4203 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Reactive Power Set Point | Inverter | inverter090_MODBUS.HR0558_qRef | Reactive Power Set Point | 4204 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Frequency | Inverter | inverter090_MODBUS.HR1012_f3_Hz | Frequency | 4205 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV090 | Dagget 3_SUB1_INV090_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Insulation Resistance | Inverter | inverter090_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4206 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Number of DU Channels | Inverter | inverter090_MODBUS.HR0653_duChannels | Number of DU Channels | 4207 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Number of Running Modules | Inverter | inverter090_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4208 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Operating State | Inverter | inverter090_MODBUS.HR1123_currentStatus | Operating State | 4209 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Power Factor | Inverter | inverter090_MODBUS.HR1011_pf3 | Power Factor | 4210 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV090 | Dagget 3_SUB1_INV090_Ramp Down | Inverter | inverter090_MODBUS.HR0286_dropGradient_p | Ramp Down | 4211 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Ramp Up | Inverter | inverter090_MODBUS.HR0282_riseGradient_p | Ramp Up | 4212 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power Delivered | Inverter | inverter090_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4213 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Reactive Power Delivered | Inverter | inverter090_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4214 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power | 4215 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Reactive Power | Inverter | inverter090_MODBUS.HR1009_q3_kvar | Reactive Power | 4216 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Reactive Power Mode | Inverter | inverter090_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4217 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Reactive Power Set Point Percent | Inverter | inverter090_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4218 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power AC Percent | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4219 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power-AC | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power-AC | 4220 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power-DC | Inverter | inverter090_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4221 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Air Intake | Inverter | inverter090_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4222 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Cabinet | Inverter | inverter090_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4223 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-IGBT | Inverter | inverter090_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4224 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Temperature-Module | Inverter | inverter090_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4225 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage A-B | Inverter | inverter090_MODBUS.HR1010_vRS_V | Voltage A-B | 4226 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage B-C | Inverter | inverter090_MODBUS.HR1002_vST_V | Voltage B-C | 4227 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage C-A | Inverter | inverter090_MODBUS.HR1003_vTR_V | Voltage C-A | 4228 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Voltage DC | Inverter | inverter090_MODBUS.HR1051_vdcBus_V | Voltage DC | 4229 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV091 | Dagget 3_SUB1_INV091_A Phase Current | Inverter | inverter091_MODBUS.HR1004_i1_A | A Phase Current | 4230 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_B Phase Current | Inverter | inverter091_MODBUS.HR1005_i2_A | B Phase Current | 4231 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_C Phase Current | Inverter | inverter091_MODBUS.HR1006_i3_A | C Phase Current | 4232 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Bus Voltage | Inverter | inverter091_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4233 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV091 | Dagget 3_SUB1_INV091_Apparent Power | Inverter | inverter091_MODBUS.HR1010_s3_VA | Apparent Power | 4234 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input1 | Inverter | inverter091_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4235 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC Input 1 | Inverter | inverter091_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4236 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input2 | Inverter | inverter091_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4237 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC input 2 | Inverter | inverter091_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4238 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input3 | Inverter | inverter091_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4239 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC input 3 | Inverter | inverter091_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4240 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input4 | Inverter | inverter091_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4241 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC input 4 | Inverter | inverter091_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4242 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input5 | Inverter | inverter091_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4243 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC input 5 | Inverter | inverter091_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4244 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current DC Input6 | Inverter | inverter091_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4245 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC input 6 | Inverter | inverter091_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4246 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current-AC | Inverter | inverter091_MODBUS.HR1007_i3Avg_A | Current-AC | 4247 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Current-DC | Inverter | inverter091_MODBUS.HR1062_idcInput_A | Current-DC | 4248 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Daily Energy Delivered | Inverter | inverter091_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4249 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power Set Point | Inverter | inverter091_MODBUS.HR0553_pRef | Real Power Set Point | 4250 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Reactive Power Set Point | Inverter | inverter091_MODBUS.HR0558_qRef | Reactive Power Set Point | 4251 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Frequency | Inverter | inverter091_MODBUS.HR1012_f3_Hz | Frequency | 4252 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV091 | Dagget 3_SUB1_INV091_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Insulation Resistance | Inverter | inverter091_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4253 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Number of DU Channels | Inverter | inverter091_MODBUS.HR0653_duChannels | Number of DU Channels | 4254 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Number of Running Modules | Inverter | inverter091_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4255 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Operating State | Inverter | inverter091_MODBUS.HR1123_currentStatus | Operating State | 4256 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Power Factor | Inverter | inverter091_MODBUS.HR1011_pf3 | Power Factor | 4257 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV091 | Dagget 3_SUB1_INV091_Ramp Down | Inverter | inverter091_MODBUS.HR0286_dropGradient_p | Ramp Down | 4258 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Ramp Up | Inverter | inverter091_MODBUS.HR0282_riseGradient_p | Ramp Up | 4259 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power Delivered | Inverter | inverter091_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4260 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Reactive Power Delivered | Inverter | inverter091_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4261 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power | 4262 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Reactive Power | Inverter | inverter091_MODBUS.HR1009_q3_kvar | Reactive Power | 4263 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Reactive Power Mode | Inverter | inverter091_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4264 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Reactive Power Set Point Percent | Inverter | inverter091_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4265 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power AC Percent | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4266 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power-AC | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power-AC | 4267 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power-DC | Inverter | inverter091_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4268 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Air Intake | Inverter | inverter091_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4269 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Cabinet | Inverter | inverter091_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4270 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-IGBT | Inverter | inverter091_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4271 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Temperature-Module | Inverter | inverter091_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4272 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage A-B | Inverter | inverter091_MODBUS.HR1001_vRS_V | Voltage A-B | 4273 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage B-C | Inverter | inverter091_MODBUS.HR1002_vST_V | Voltage B-C | 4274 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage C-A | Inverter | inverter091_MODBUS.HR1003_vTR_V | Voltage C-A | 4275 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Voltage DC | Inverter | inverter091_MODBUS.HR1051_vdcBus_V | Voltage DC | 4276 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV092 | Dagget 3_SUB1_INV092_A Phase Current | Inverter | inverter092_MODBUS.HR1004_i1_A | A Phase Current | 4277 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_B Phase Current | Inverter | inverter092_MODBUS.HR1005_i2_A | B Phase Current | 4278 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_C Phase Current | Inverter | inverter092_MODBUS.HR1006_i3_A | C Phase Current | 4279 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Bus Voltage | Inverter | inverter092_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4280 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV092 | Dagget 3_SUB1_INV092_Apparent Power | Inverter | inverter092_MODBUS.HR1010_s3_VA | Apparent Power | 4281 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input1 | Inverter | inverter092_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4282 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC Input 1 | Inverter | inverter092_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4283 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input2 | Inverter | inverter092_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4284 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC input 2 | Inverter | inverter092_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4285 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input3 | Inverter | inverter092_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4286 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC input 3 | Inverter | inverter092_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4287 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input4 | Inverter | inverter092_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4288 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC input 4 | Inverter | inverter092_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4289 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input5 | Inverter | inverter092_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4290 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC input 5 | Inverter | inverter092_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4291 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current DC Input6 | Inverter | inverter092_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4292 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC input 6 | Inverter | inverter092_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4293 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current-AC | Inverter | inverter092_MODBUS.HR1007_i3Avg_A | Current-AC | 4294 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Current-DC | Inverter | inverter092_MODBUS.HR1062_idcInput_A | Current-DC | 4295 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Daily Energy Delivered | Inverter | inverter092_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4296 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power Set Point | Inverter | inverter092_MODBUS.HR0553_pRef | Real Power Set Point | 4297 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Reactive Power Set Point | Inverter | inverter092_MODBUS.HR0558_qRef | Reactive Power Set Point | 4298 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Frequency | Inverter | inverter092_MODBUS.HR1012_f3_Hz | Frequency | 4299 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV092 | Dagget 3_SUB1_INV092_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Insulation Resistance | Inverter | inverter092_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4300 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Number of DU Channels | Inverter | inverter092_MODBUS.HR0653_duChannels | Number of DU Channels | 4301 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Number of Running Modules | Inverter | inverter092_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4302 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Operating State | Inverter | inverter092_MODBUS.HR1123_currentStatus | Operating State | 4303 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Power Factor | Inverter | inverter092_MODBUS.HR1011_pf3 | Power Factor | 4304 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV092 | Dagget 3_SUB1_INV092_Ramp Down | Inverter | inverter092_MODBUS.HR0286_dropGradient_p | Ramp Down | 4305 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Ramp Up | Inverter | inverter092_MODBUS.HR0282_riseGradient_p | Ramp Up | 4306 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power Delivered | Inverter | inverter092_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4307 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Reactive Power Delivered | Inverter | inverter092_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4308 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power | 4309 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Reactive Power | Inverter | inverter092_MODBUS.HR1009_q3_kvar | Reactive Power | 4310 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Reactive Power Mode | Inverter | inverter092_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4311 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Reactive Power Set Point Percent | Inverter | inverter092_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4312 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power AC Percent | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4313 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power-AC | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power-AC | 4314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power-DC | Inverter | inverter092_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4315 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Air Intake | Inverter | inverter092_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4316 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Cabinet | Inverter | inverter092_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4317 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-IGBT | Inverter | inverter092_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4318 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Temperature-Module | Inverter | inverter092_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4319 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage A-B | Inverter | inverter092_MODBUS.HR1002_vRS_V | Voltage A-B | 4320 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage B-C | Inverter | inverter092_MODBUS.HR1002_vST_V | Voltage B-C | 4321 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage C-A | Inverter | inverter092_MODBUS.HR1003_vTR_V | Voltage C-A | 4322 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Voltage DC | Inverter | inverter092_MODBUS.HR1051_vdcBus_V | Voltage DC | 4323 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV093 | Dagget 3_SUB1_INV093_A Phase Current | Inverter | inverter093_MODBUS.HR1004_i1_A | A Phase Current | 4324 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_B Phase Current | Inverter | inverter093_MODBUS.HR1005_i2_A | B Phase Current | 4325 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_C Phase Current | Inverter | inverter093_MODBUS.HR1006_i3_A | C Phase Current | 4326 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Bus Voltage | Inverter | inverter093_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4327 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV093 | Dagget 3_SUB1_INV093_Apparent Power | Inverter | inverter093_MODBUS.HR1010_s3_VA | Apparent Power | 4328 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input1 | Inverter | inverter093_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4329 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC Input 1 | Inverter | inverter093_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4330 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input2 | Inverter | inverter093_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4331 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC input 2 | Inverter | inverter093_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4332 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input3 | Inverter | inverter093_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4333 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC input 3 | Inverter | inverter093_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4334 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input4 | Inverter | inverter093_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4335 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC input 4 | Inverter | inverter093_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4336 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input5 | Inverter | inverter093_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4337 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC input 5 | Inverter | inverter093_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4338 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current DC Input6 | Inverter | inverter093_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4339 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC input 6 | Inverter | inverter093_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4340 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current-AC | Inverter | inverter093_MODBUS.HR1007_i3Avg_A | Current-AC | 4341 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Current-DC | Inverter | inverter093_MODBUS.HR1062_idcInput_A | Current-DC | 4342 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Daily Energy Delivered | Inverter | inverter093_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4343 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power Set Point | Inverter | inverter093_MODBUS.HR0553_pRef | Real Power Set Point | 4344 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Reactive Power Set Point | Inverter | inverter093_MODBUS.HR0558_qRef | Reactive Power Set Point | 4345 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Frequency | Inverter | inverter093_MODBUS.HR1012_f3_Hz | Frequency | 4346 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV093 | Dagget 3_SUB1_INV093_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Insulation Resistance | Inverter | inverter093_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4347 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Number of DU Channels | Inverter | inverter093_MODBUS.HR0653_duChannels | Number of DU Channels | 4348 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Number of Running Modules | Inverter | inverter093_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4349 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Operating State | Inverter | inverter093_MODBUS.HR1123_currentStatus | Operating State | 4350 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Power Factor | Inverter | inverter093_MODBUS.HR1011_pf3 | Power Factor | 4351 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV093 | Dagget 3_SUB1_INV093_Ramp Down | Inverter | inverter093_MODBUS.HR0286_dropGradient_p | Ramp Down | 4352 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Ramp Up | Inverter | inverter093_MODBUS.HR0282_riseGradient_p | Ramp Up | 4353 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power Delivered | Inverter | inverter093_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4354 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Reactive Power Delivered | Inverter | inverter093_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4355 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power | 4356 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Reactive Power | Inverter | inverter093_MODBUS.HR1009_q3_kvar | Reactive Power | 4357 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Reactive Power Mode | Inverter | inverter093_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4358 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Reactive Power Set Point Percent | Inverter | inverter093_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4359 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power AC Percent | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4360 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power-AC | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power-AC | 4361 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power-DC | Inverter | inverter093_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4362 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Air Intake | Inverter | inverter093_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4363 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Cabinet | Inverter | inverter093_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4364 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-IGBT | Inverter | inverter093_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4365 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Temperature-Module | Inverter | inverter093_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4366 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage A-B | Inverter | inverter093_MODBUS.HR1003_vRS_V | Voltage A-B | 4367 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage B-C | Inverter | inverter093_MODBUS.HR1002_vST_V | Voltage B-C | 4368 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage C-A | Inverter | inverter093_MODBUS.HR1003_vTR_V | Voltage C-A | 4369 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Voltage DC | Inverter | inverter093_MODBUS.HR1051_vdcBus_V | Voltage DC | 4370 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV094 | Dagget 3_SUB1_INV094_A Phase Current | Inverter | inverter094_MODBUS.HR1004_i1_A | A Phase Current | 4371 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_B Phase Current | Inverter | inverter094_MODBUS.HR1005_i2_A | B Phase Current | 4372 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_C Phase Current | Inverter | inverter094_MODBUS.HR1006_i3_A | C Phase Current | 4373 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Bus Voltage | Inverter | inverter094_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4374 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV094 | Dagget 3_SUB1_INV094_Apparent Power | Inverter | inverter094_MODBUS.HR1010_s3_VA | Apparent Power | 4375 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input1 | Inverter | inverter094_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4376 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC Input 1 | Inverter | inverter094_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4377 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input2 | Inverter | inverter094_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4378 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC input 2 | Inverter | inverter094_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4379 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input3 | Inverter | inverter094_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4380 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC input 3 | Inverter | inverter094_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4381 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input4 | Inverter | inverter094_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4382 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC input 4 | Inverter | inverter094_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4383 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input5 | Inverter | inverter094_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4384 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC input 5 | Inverter | inverter094_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4385 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current DC Input6 | Inverter | inverter094_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4386 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC input 6 | Inverter | inverter094_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4387 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current-AC | Inverter | inverter094_MODBUS.HR1007_i3Avg_A | Current-AC | 4388 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Current-DC | Inverter | inverter094_MODBUS.HR1062_idcInput_A | Current-DC | 4389 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Daily Energy Delivered | Inverter | inverter094_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4390 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power Set Point | Inverter | inverter094_MODBUS.HR0553_pRef | Real Power Set Point | 4391 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Reactive Power Set Point | Inverter | inverter094_MODBUS.HR0558_qRef | Reactive Power Set Point | 4392 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Frequency | Inverter | inverter094_MODBUS.HR1012_f3_Hz | Frequency | 4393 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV094 | Dagget 3_SUB1_INV094_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Insulation Resistance | Inverter | inverter094_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4394 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Number of DU Channels | Inverter | inverter094_MODBUS.HR0653_duChannels | Number of DU Channels | 4395 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Number of Running Modules | Inverter | inverter094_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4396 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Operating State | Inverter | inverter094_MODBUS.HR1123_currentStatus | Operating State | 4397 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Power Factor | Inverter | inverter094_MODBUS.HR1011_pf3 | Power Factor | 4398 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV094 | Dagget 3_SUB1_INV094_Ramp Down | Inverter | inverter094_MODBUS.HR0286_dropGradient_p | Ramp Down | 4399 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Ramp Up | Inverter | inverter094_MODBUS.HR0282_riseGradient_p | Ramp Up | 4400 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power Delivered | Inverter | inverter094_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4401 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Reactive Power Delivered | Inverter | inverter094_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4402 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power | 4403 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Reactive Power | Inverter | inverter094_MODBUS.HR1009_q3_kvar | Reactive Power | 4404 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Reactive Power Mode | Inverter | inverter094_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4405 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Reactive Power Set Point Percent | Inverter | inverter094_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4406 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power AC Percent | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4407 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power-AC | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power-AC | 4408 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power-DC | Inverter | inverter094_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4409 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Air Intake | Inverter | inverter094_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4410 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Cabinet | Inverter | inverter094_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4411 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-IGBT | Inverter | inverter094_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4412 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Temperature-Module | Inverter | inverter094_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4413 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage A-B | Inverter | inverter094_MODBUS.HR1004_vRS_V | Voltage A-B | 4414 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage B-C | Inverter | inverter094_MODBUS.HR1002_vST_V | Voltage B-C | 4415 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage C-A | Inverter | inverter094_MODBUS.HR1003_vTR_V | Voltage C-A | 4416 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Voltage DC | Inverter | inverter094_MODBUS.HR1051_vdcBus_V | Voltage DC | 4417 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV095 | Dagget 3_SUB1_INV095_A Phase Current | Inverter | inverter095_MODBUS.HR1004_i1_A | A Phase Current | 4418 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_B Phase Current | Inverter | inverter095_MODBUS.HR1005_i2_A | B Phase Current | 4419 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_C Phase Current | Inverter | inverter095_MODBUS.HR1006_i3_A | C Phase Current | 4420 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Bus Voltage | Inverter | inverter095_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4421 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV095 | Dagget 3_SUB1_INV095_Apparent Power | Inverter | inverter095_MODBUS.HR1010_s3_VA | Apparent Power | 4422 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input1 | Inverter | inverter095_MODBUS.HR5005_m1_idc_A | Current DC Input# | 4423 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC Input 1 | Inverter | inverter095_MODBUS.HR5008_m1_vdc_V | Voltage DC Input # | 4424 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input2 | Inverter | inverter095_MODBUS.HR5037_m2_idc_A | Current DC Input# | 4425 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC input 2 | Inverter | inverter095_MODBUS.HR5040_m2_vdc_V | Voltage DC Input # | 4426 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input3 | Inverter | inverter095_MODBUS.HR5069_m3_idc_A | Current DC Input# | 4427 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC input 3 | Inverter | inverter095_MODBUS.HR5072_m3_vdc_V | Voltage DC Input # | 4428 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input4 | Inverter | inverter095_MODBUS.HR5101_m4_idc_A | Current DC Input# | 4429 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC input 4 | Inverter | inverter095_MODBUS.HR5104_m4_vdc_V | Voltage DC Input # | 4430 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input5 | Inverter | inverter095_MODBUS.HR5133_m5_idc_A | Current DC Input# | 4431 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC input 5 | Inverter | inverter095_MODBUS.HR5136_m5_vdc_V | Voltage DC Input # | 4432 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current DC Input6 | Inverter | inverter095_MODBUS.HR5165_m6_idc_A | Current DC Input# | 4433 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC input 6 | Inverter | inverter095_MODBUS.HR5168_m6_vdc_V | Voltage DC Input # | 4434 | kV | Requested-Available | 0 | 35 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current-AC | Inverter | inverter095_MODBUS.HR1007_i3Avg_A | Current-AC | 4435 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Current-DC | Inverter | inverter095_MODBUS.HR1062_idcInput_A | Current-DC | 4436 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Daily Energy Delivered | Inverter | inverter095_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4437 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power Set Point | Inverter | inverter095_MODBUS.HR0553_pRef | Real Power Set Point | 4438 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Reactive Power Set Point | Inverter | inverter095_MODBUS.HR0558_qRef | Reactive Power Set Point | 4439 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Frequency | Inverter | inverter095_MODBUS.HR1012_f3_Hz | Frequency | 4440 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV095 | Dagget 3_SUB1_INV095_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Insulation Resistance | Inverter | inverter095_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4441 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Number of DU Channels | Inverter | inverter095_MODBUS.HR0653_duChannels | Number of DU Channels | 4442 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Number of Running Modules | Inverter | inverter095_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4443 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Operating State | Inverter | inverter095_MODBUS.HR1123_currentStatus | Operating State | 4444 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Power Factor | Inverter | inverter095_MODBUS.HR1011_pf3 | Power Factor | 4445 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV095 | Dagget 3_SUB1_INV095_Ramp Down | Inverter | inverter095_MODBUS.HR0286_dropGradient_p | Ramp Down | 4446 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Ramp Up | Inverter | inverter095_MODBUS.HR0282_riseGradient_p | Ramp Up | 4447 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power Delivered | Inverter | inverter095_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4448 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Reactive Power Delivered | Inverter | inverter095_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4449 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power | 4450 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Reactive Power | Inverter | inverter095_MODBUS.HR1009_q3_kvar | Reactive Power | 4451 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Reactive Power Mode | Inverter | inverter095_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4452 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Reactive Power Set Point Percent | Inverter | inverter095_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4453 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power AC Percent | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4454 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power-AC | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power-AC | 4455 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power-DC | Inverter | inverter095_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4456 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Air Intake | Inverter | inverter095_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4457 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Cabinet | Inverter | inverter095_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4458 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-IGBT | Inverter | inverter095_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4459 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Temperature-Module | Inverter | inverter095_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4460 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage A-B | Inverter | inverter095_MODBUS.HR1005_vRS_V | Voltage A-B | 4461 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage B-C | Inverter | inverter095_MODBUS.HR1002_vST_V | Voltage B-C | 4462 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage C-A | Inverter | inverter095_MODBUS.HR1003_vTR_V | Voltage C-A | 4463 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Voltage DC | Inverter | inverter095_MODBUS.HR1051_vdcBus_V | Voltage DC | 4464 | kV | Requested-Available | 0 | 35 | 0.001
Digital Inputs
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV001 | Dagget 3_SUB1_INV001_AutoStart On | Inverter | Inverter001_MODBUS.HR0501_restartEn | AutoStart On | 0 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Comm Fail | Inverter | Inverter001_commsFail | Comm Fail | 1 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Faulted | Inverter | Inverter001_fault | Faulted | 2 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Locked Out | Inverter | Inverter001_lockout | Locked Out | 3 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Master Control Enabled | Inverter | Inverter001_masterControl | Master Control Enabled | 4 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Offline | Inverter | Inverter001_offline | Offline | 5 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Ramp Up Enabled | Inverter | Inverter001_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 6 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Ramp Down Enabled | Inverter | Inverter001_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 7 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Real Power Curtailment Flag | Inverter | Inverter001_curtailed | Real Power Curtailment Flag | 8 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Following Setpoint | Inverter | Inverter001_follwing | Following Setpoint | 9 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_AutoStart On | Inverter | Inverter002_MODBUS.HR0501_restartEn | AutoStart On | 10 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Comm Fail | Inverter | Inverter002_commsFail | Comm Fail | 11 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Faulted | Inverter | Inverter002_fault | Faulted | 12 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Locked Out | Inverter | Inverter002_lockout | Locked Out | 13 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Master Control Enabled | Inverter | Inverter002_masterControl | Master Control Enabled | 14 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Offline | Inverter | Inverter002_offline | Offline | 15 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Ramp Up Enabled | Inverter | Inverter002_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 16 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Ramp Down Enabled | Inverter | Inverter002_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 17 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Real Power Curtailment Flag | Inverter | Inverter002_curtailed | Real Power Curtailment Flag | 18 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Following Setpoint | Inverter | Inverter002_follwing | Following Setpoint | 19 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_AutoStart On | Inverter | Inverter003_MODBUS.HR0501_restartEn | AutoStart On | 20 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Comm Fail | Inverter | Inverter003_commsFail | Comm Fail | 21 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Faulted | Inverter | Inverter003_fault | Faulted | 22 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Locked Out | Inverter | Inverter003_lockout | Locked Out | 23 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Master Control Enabled | Inverter | Inverter003_masterControl | Master Control Enabled | 24 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Offline | Inverter | Inverter003_offline | Offline | 25 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Ramp Up Enabled | Inverter | Inverter003_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 26 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Ramp Down Enabled | Inverter | Inverter003_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 27 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Real Power Curtailment Flag | Inverter | Inverter003_curtailed | Real Power Curtailment Flag | 28 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Following Setpoint | Inverter | Inverter003_follwing | Following Setpoint | 29 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_AutoStart On | Inverter | Inverter004_MODBUS.HR0501_restartEn | AutoStart On | 30 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Comm Fail | Inverter | Inverter004_commsFail | Comm Fail | 31 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Faulted | Inverter | Inverter004_fault | Faulted | 32 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Locked Out | Inverter | Inverter004_lockout | Locked Out | 33 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Master Control Enabled | Inverter | Inverter004_masterControl | Master Control Enabled | 34 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Offline | Inverter | Inverter004_offline | Offline | 35 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Ramp Up Enabled | Inverter | Inverter004_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 36 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Ramp Down Enabled | Inverter | Inverter004_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 37 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Real Power Curtailment Flag | Inverter | Inverter004_curtailed | Real Power Curtailment Flag | 38 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Following Setpoint | Inverter | Inverter004_follwing | Following Setpoint | 39 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_AutoStart On | Inverter | Inverter005_MODBUS.HR0501_restartEn | AutoStart On | 40 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Comm Fail | Inverter | Inverter005_commsFail | Comm Fail | 41 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Faulted | Inverter | Inverter005_fault | Faulted | 42 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Locked Out | Inverter | Inverter005_lockout | Locked Out | 43 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Master Control Enabled | Inverter | Inverter005_masterControl | Master Control Enabled | 44 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Offline | Inverter | Inverter005_offline | Offline | 45 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Ramp Up Enabled | Inverter | Inverter005_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 46 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Ramp Down Enabled | Inverter | Inverter005_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 47 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Real Power Curtailment Flag | Inverter | Inverter005_curtailed | Real Power Curtailment Flag | 48 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Following Setpoint | Inverter | Inverter005_follwing | Following Setpoint | 49 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_AutoStart On | Inverter | Inverter006_MODBUS.HR0501_restartEn | AutoStart On | 50 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Comm Fail | Inverter | Inverter006_commsFail | Comm Fail | 51 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Faulted | Inverter | Inverter006_fault | Faulted | 52 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Locked Out | Inverter | Inverter006_lockout | Locked Out | 53 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Master Control Enabled | Inverter | Inverter006_masterControl | Master Control Enabled | 54 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Offline | Inverter | Inverter006_offline | Offline | 55 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Ramp Up Enabled | Inverter | Inverter006_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 56 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Ramp Down Enabled | Inverter | Inverter006_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 57 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Real Power Curtailment Flag | Inverter | Inverter006_curtailed | Real Power Curtailment Flag | 58 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Following Setpoint | Inverter | Inverter006_follwing | Following Setpoint | 59 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_AutoStart On | Inverter | Inverter007_MODBUS.HR0501_restartEn | AutoStart On | 60 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Comm Fail | Inverter | Inverter007_commsFail | Comm Fail | 61 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Faulted | Inverter | Inverter007_fault | Faulted | 62 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Locked Out | Inverter | Inverter007_lockout | Locked Out | 63 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Master Control Enabled | Inverter | Inverter007_masterControl | Master Control Enabled | 64 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Offline | Inverter | Inverter007_offline | Offline | 65 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Ramp Up Enabled | Inverter | Inverter007_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 66 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Ramp Down Enabled | Inverter | Inverter007_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 67 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Real Power Curtailment Flag | Inverter | Inverter007_curtailed | Real Power Curtailment Flag | 68 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Following Setpoint | Inverter | Inverter007_follwing | Following Setpoint | 69 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_AutoStart On | Inverter | Inverter008_MODBUS.HR0501_restartEn | AutoStart On | 70 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Comm Fail | Inverter | Inverter008_commsFail | Comm Fail | 71 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Faulted | Inverter | Inverter008_fault | Faulted | 72 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Locked Out | Inverter | Inverter008_lockout | Locked Out | 73 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Master Control Enabled | Inverter | Inverter008_masterControl | Master Control Enabled | 74 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Offline | Inverter | Inverter008_offline | Offline | 75 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Ramp Up Enabled | Inverter | Inverter008_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 76 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Ramp Down Enabled | Inverter | Inverter008_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 77 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Real Power Curtailment Flag | Inverter | Inverter008_curtailed | Real Power Curtailment Flag | 78 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Following Setpoint | Inverter | Inverter008_follwing | Following Setpoint | 79 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_AutoStart On | Inverter | Inverter009_MODBUS.HR0501_restartEn | AutoStart On | 80 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Comm Fail | Inverter | Inverter009_commsFail | Comm Fail | 81 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Faulted | Inverter | Inverter009_fault | Faulted | 82 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Locked Out | Inverter | Inverter009_lockout | Locked Out | 83 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Master Control Enabled | Inverter | Inverter009_masterControl | Master Control Enabled | 84 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Offline | Inverter | Inverter009_offline | Offline | 85 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Ramp Up Enabled | Inverter | Inverter009_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 86 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Ramp Down Enabled | Inverter | Inverter009_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 87 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Real Power Curtailment Flag | Inverter | Inverter009_curtailed | Real Power Curtailment Flag | 88 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Following Setpoint | Inverter | Inverter009_follwing | Following Setpoint | 89 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_AutoStart On | Inverter | Inverter010_MODBUS.HR0501_restartEn | AutoStart On | 90 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Comm Fail | Inverter | Inverter010_commsFail | Comm Fail | 91 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Faulted | Inverter | Inverter010_fault | Faulted | 92 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Locked Out | Inverter | Inverter010_lockout | Locked Out | 93 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Master Control Enabled | Inverter | Inverter010_masterControl | Master Control Enabled | 94 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Offline | Inverter | Inverter010_offline | Offline | 95 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Ramp Up Enabled | Inverter | Inverter010_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 96 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Ramp Down Enabled | Inverter | Inverter010_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 97 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Real Power Curtailment Flag | Inverter | Inverter010_curtailed | Real Power Curtailment Flag | 98 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Following Setpoint | Inverter | Inverter010_follwing | Following Setpoint | 99 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_AutoStart On | Inverter | inverter011_MODBUS.HR0501_restartEn | AutoStart On | 100 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Comm Fail | Inverter | inverter011_commsFail | Comm Fail | 101 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Faulted | Inverter | inverter011_fault | Faulted | 102 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Locked Out | Inverter | inverter011_lockout | Locked Out | 103 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Master Control Enabled | Inverter | inverter011_masterControl | Master Control Enabled | 104 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Offline | Inverter | inverter011_offline | Offline | 105 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Ramp Up Enabled | Inverter | inverter011_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 106 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Ramp Down Enabled | Inverter | inverter011_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 107 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Real Power Curtailment Flag | Inverter | inverter011_curtailed | Real Power Curtailment Flag | 108 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Following Setpoint | Inverter | inverter011_follwing | Following Setpoint | 109 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_AutoStart On | Inverter | inverter012_MODBUS.HR0501_restartEn | AutoStart On | 110 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Comm Fail | Inverter | inverter012_commsFail | Comm Fail | 111 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Faulted | Inverter | inverter012_fault | Faulted | 112 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Locked Out | Inverter | inverter012_lockout | Locked Out | 113 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Master Control Enabled | Inverter | inverter012_masterControl | Master Control Enabled | 114 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Offline | Inverter | inverter012_offline | Offline | 115 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Ramp Up Enabled | Inverter | inverter012_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 116 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Ramp Down Enabled | Inverter | inverter012_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 117 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Real Power Curtailment Flag | Inverter | inverter012_curtailed | Real Power Curtailment Flag | 118 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Following Setpoint | Inverter | inverter012_follwing | Following Setpoint | 119 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_AutoStart On | Inverter | inverter013_MODBUS.HR0501_restartEn | AutoStart On | 120 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Comm Fail | Inverter | inverter013_commsFail | Comm Fail | 121 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Faulted | Inverter | inverter013_fault | Faulted | 122 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Locked Out | Inverter | inverter013_lockout | Locked Out | 123 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Master Control Enabled | Inverter | inverter013_masterControl | Master Control Enabled | 124 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Offline | Inverter | inverter013_offline | Offline | 125 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Ramp Up Enabled | Inverter | inverter013_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 126 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Ramp Down Enabled | Inverter | inverter013_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 127 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Real Power Curtailment Flag | Inverter | inverter013_curtailed | Real Power Curtailment Flag | 128 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Following Setpoint | Inverter | inverter013_follwing | Following Setpoint | 129 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_AutoStart On | Inverter | inverter014_MODBUS.HR0501_restartEn | AutoStart On | 130 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Comm Fail | Inverter | inverter014_commsFail | Comm Fail | 131 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Faulted | Inverter | inverter014_fault | Faulted | 132 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Locked Out | Inverter | inverter014_lockout | Locked Out | 133 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Master Control Enabled | Inverter | inverter014_masterControl | Master Control Enabled | 134 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Offline | Inverter | inverter014_offline | Offline | 135 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Ramp Up Enabled | Inverter | inverter014_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 136 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Ramp Down Enabled | Inverter | inverter014_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 137 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Real Power Curtailment Flag | Inverter | inverter014_curtailed | Real Power Curtailment Flag | 138 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Following Setpoint | Inverter | inverter014_follwing | Following Setpoint | 139 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_AutoStart On | Inverter | inverter015_MODBUS.HR0501_restartEn | AutoStart On | 140 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Comm Fail | Inverter | inverter015_commsFail | Comm Fail | 141 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Faulted | Inverter | inverter015_fault | Faulted | 142 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Locked Out | Inverter | inverter015_lockout | Locked Out | 143 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Master Control Enabled | Inverter | inverter015_masterControl | Master Control Enabled | 144 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Offline | Inverter | inverter015_offline | Offline | 145 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Ramp Up Enabled | Inverter | inverter015_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 146 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Ramp Down Enabled | Inverter | inverter015_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 147 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Real Power Curtailment Flag | Inverter | inverter015_curtailed | Real Power Curtailment Flag | 148 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Following Setpoint | Inverter | inverter015_follwing | Following Setpoint | 149 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_AutoStart On | Inverter | inverter016_MODBUS.HR0501_restartEn | AutoStart On | 150 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Comm Fail | Inverter | inverter016_commsFail | Comm Fail | 151 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Faulted | Inverter | inverter016_fault | Faulted | 152 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Locked Out | Inverter | inverter016_lockout | Locked Out | 153 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Master Control Enabled | Inverter | inverter016_masterControl | Master Control Enabled | 154 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Offline | Inverter | inverter016_offline | Offline | 155 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Ramp Up Enabled | Inverter | inverter016_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 156 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Ramp Down Enabled | Inverter | inverter016_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 157 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Real Power Curtailment Flag | Inverter | inverter016_curtailed | Real Power Curtailment Flag | 158 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Following Setpoint | Inverter | inverter016_follwing | Following Setpoint | 159 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_AutoStart On | Inverter | inverter017_MODBUS.HR0501_restartEn | AutoStart On | 160 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Comm Fail | Inverter | inverter017_commsFail | Comm Fail | 161 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Faulted | Inverter | inverter017_fault | Faulted | 162 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Locked Out | Inverter | inverter017_lockout | Locked Out | 163 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Master Control Enabled | Inverter | inverter017_masterControl | Master Control Enabled | 164 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Offline | Inverter | inverter017_offline | Offline | 165 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Ramp Up Enabled | Inverter | inverter017_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 166 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Ramp Down Enabled | Inverter | inverter017_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 167 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Real Power Curtailment Flag | Inverter | inverter017_curtailed | Real Power Curtailment Flag | 168 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Following Setpoint | Inverter | inverter017_follwing | Following Setpoint | 169 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_AutoStart On | Inverter | inverter018_MODBUS.HR0501_restartEn | AutoStart On | 170 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Comm Fail | Inverter | inverter018_commsFail | Comm Fail | 171 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Faulted | Inverter | inverter018_fault | Faulted | 172 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Locked Out | Inverter | inverter018_lockout | Locked Out | 173 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Master Control Enabled | Inverter | inverter018_masterControl | Master Control Enabled | 174 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Offline | Inverter | inverter018_offline | Offline | 175 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Ramp Up Enabled | Inverter | inverter018_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 176 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Ramp Down Enabled | Inverter | inverter018_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 177 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Real Power Curtailment Flag | Inverter | inverter018_curtailed | Real Power Curtailment Flag | 178 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Following Setpoint | Inverter | inverter018_follwing | Following Setpoint | 179 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_AutoStart On | Inverter | inverter019_MODBUS.HR0501_restartEn | AutoStart On | 180 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Comm Fail | Inverter | inverter019_commsFail | Comm Fail | 181 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Faulted | Inverter | inverter019_fault | Faulted | 182 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Locked Out | Inverter | inverter019_lockout | Locked Out | 183 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Master Control Enabled | Inverter | inverter019_masterControl | Master Control Enabled | 184 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Offline | Inverter | inverter019_offline | Offline | 185 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Ramp Up Enabled | Inverter | inverter019_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 186 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Ramp Down Enabled | Inverter | inverter019_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 187 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Real Power Curtailment Flag | Inverter | inverter019_curtailed | Real Power Curtailment Flag | 188 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Following Setpoint | Inverter | inverter019_follwing | Following Setpoint | 189 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_AutoStart On | Inverter | inverter020_MODBUS.HR0501_restartEn | AutoStart On | 190 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Comm Fail | Inverter | inverter020_commsFail | Comm Fail | 191 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Faulted | Inverter | inverter020_fault | Faulted | 192 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Locked Out | Inverter | inverter020_lockout | Locked Out | 193 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Master Control Enabled | Inverter | inverter020_masterControl | Master Control Enabled | 194 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Offline | Inverter | inverter020_offline | Offline | 195 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Ramp Up Enabled | Inverter | inverter020_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 196 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Ramp Down Enabled | Inverter | inverter020_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 197 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Real Power Curtailment Flag | Inverter | inverter020_curtailed | Real Power Curtailment Flag | 198 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Following Setpoint | Inverter | inverter020_follwing | Following Setpoint | 199 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_AutoStart On | Inverter | inverter021_MODBUS.HR0501_restartEn | AutoStart On | 200 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Comm Fail | Inverter | inverter021_commsFail | Comm Fail | 201 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Faulted | Inverter | inverter021_fault | Faulted | 202 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Locked Out | Inverter | inverter021_lockout | Locked Out | 203 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Master Control Enabled | Inverter | inverter021_masterControl | Master Control Enabled | 204 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Offline | Inverter | inverter021_offline | Offline | 205 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Ramp Up Enabled | Inverter | inverter021_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 206 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Ramp Down Enabled | Inverter | inverter021_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 207 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Real Power Curtailment Flag | Inverter | inverter021_curtailed | Real Power Curtailment Flag | 208 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Following Setpoint | Inverter | inverter021_follwing | Following Setpoint | 209 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_AutoStart On | Inverter | inverter022_MODBUS.HR0501_restartEn | AutoStart On | 210 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Comm Fail | Inverter | inverter022_commsFail | Comm Fail | 211 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Faulted | Inverter | inverter022_fault | Faulted | 212 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Locked Out | Inverter | inverter022_lockout | Locked Out | 213 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Master Control Enabled | Inverter | inverter022_masterControl | Master Control Enabled | 214 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Offline | Inverter | inverter022_offline | Offline | 215 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Ramp Up Enabled | Inverter | inverter022_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 216 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Ramp Down Enabled | Inverter | inverter022_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 217 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Real Power Curtailment Flag | Inverter | inverter022_curtailed | Real Power Curtailment Flag | 218 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Following Setpoint | Inverter | inverter022_follwing | Following Setpoint | 219 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_AutoStart On | Inverter | inverter023_MODBUS.HR0501_restartEn | AutoStart On | 220 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Comm Fail | Inverter | inverter023_commsFail | Comm Fail | 221 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Faulted | Inverter | inverter023_fault | Faulted | 222 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Locked Out | Inverter | inverter023_lockout | Locked Out | 223 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Master Control Enabled | Inverter | inverter023_masterControl | Master Control Enabled | 224 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Offline | Inverter | inverter023_offline | Offline | 225 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Ramp Up Enabled | Inverter | inverter023_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 226 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Ramp Down Enabled | Inverter | inverter023_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 227 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Real Power Curtailment Flag | Inverter | inverter023_curtailed | Real Power Curtailment Flag | 228 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Following Setpoint | Inverter | inverter023_follwing | Following Setpoint | 229 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_AutoStart On | Inverter | inverter024_MODBUS.HR0501_restartEn | AutoStart On | 230 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Comm Fail | Inverter | inverter024_commsFail | Comm Fail | 231 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Faulted | Inverter | inverter024_fault | Faulted | 232 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Locked Out | Inverter | inverter024_lockout | Locked Out | 233 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Master Control Enabled | Inverter | inverter024_masterControl | Master Control Enabled | 234 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Offline | Inverter | inverter024_offline | Offline | 235 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Ramp Up Enabled | Inverter | inverter024_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 236 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Ramp Down Enabled | Inverter | inverter024_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 237 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Real Power Curtailment Flag | Inverter | inverter024_curtailed | Real Power Curtailment Flag | 238 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Following Setpoint | Inverter | inverter024_follwing | Following Setpoint | 239 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_AutoStart On | Inverter | inverter025_MODBUS.HR0501_restartEn | AutoStart On | 240 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Comm Fail | Inverter | inverter025_commsFail | Comm Fail | 241 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Faulted | Inverter | inverter025_fault | Faulted | 242 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Locked Out | Inverter | inverter025_lockout | Locked Out | 243 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Master Control Enabled | Inverter | inverter025_masterControl | Master Control Enabled | 244 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Offline | Inverter | inverter025_offline | Offline | 245 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Ramp Up Enabled | Inverter | inverter025_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 246 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Ramp Down Enabled | Inverter | inverter025_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 247 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Real Power Curtailment Flag | Inverter | inverter025_curtailed | Real Power Curtailment Flag | 248 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Following Setpoint | Inverter | inverter025_follwing | Following Setpoint | 249 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_AutoStart On | Inverter | inverter026_MODBUS.HR0501_restartEn | AutoStart On | 250 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Comm Fail | Inverter | inverter026_commsFail | Comm Fail | 251 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Faulted | Inverter | inverter026_fault | Faulted | 252 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Locked Out | Inverter | inverter026_lockout | Locked Out | 253 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Master Control Enabled | Inverter | inverter026_masterControl | Master Control Enabled | 254 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Offline | Inverter | inverter026_offline | Offline | 255 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Ramp Up Enabled | Inverter | inverter026_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 256 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Ramp Down Enabled | Inverter | inverter026_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 257 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Real Power Curtailment Flag | Inverter | inverter026_curtailed | Real Power Curtailment Flag | 258 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Following Setpoint | Inverter | inverter026_follwing | Following Setpoint | 259 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_AutoStart On | Inverter | inverter027_MODBUS.HR0501_restartEn | AutoStart On | 260 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Comm Fail | Inverter | inverter027_commsFail | Comm Fail | 261 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Faulted | Inverter | inverter027_fault | Faulted | 262 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Locked Out | Inverter | inverter027_lockout | Locked Out | 263 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Master Control Enabled | Inverter | inverter027_masterControl | Master Control Enabled | 264 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Offline | Inverter | inverter027_offline | Offline | 265 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Ramp Up Enabled | Inverter | inverter027_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 266 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Ramp Down Enabled | Inverter | inverter027_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 267 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Real Power Curtailment Flag | Inverter | inverter027_curtailed | Real Power Curtailment Flag | 268 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Following Setpoint | Inverter | inverter027_follwing | Following Setpoint | 269 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_AutoStart On | Inverter | inverter028_MODBUS.HR0501_restartEn | AutoStart On | 270 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Comm Fail | Inverter | inverter028_commsFail | Comm Fail | 271 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Faulted | Inverter | inverter028_fault | Faulted | 272 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Locked Out | Inverter | inverter028_lockout | Locked Out | 273 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Master Control Enabled | Inverter | inverter028_masterControl | Master Control Enabled | 274 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Offline | Inverter | inverter028_offline | Offline | 275 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Ramp Up Enabled | Inverter | inverter028_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 276 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Ramp Down Enabled | Inverter | inverter028_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 277 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Real Power Curtailment Flag | Inverter | inverter028_curtailed | Real Power Curtailment Flag | 278 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Following Setpoint | Inverter | inverter028_follwing | Following Setpoint | 279 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_AutoStart On | Inverter | inverter029_MODBUS.HR0501_restartEn | AutoStart On | 280 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Comm Fail | Inverter | inverter029_commsFail | Comm Fail | 281 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Faulted | Inverter | inverter029_fault | Faulted | 282 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Locked Out | Inverter | inverter029_lockout | Locked Out | 283 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Master Control Enabled | Inverter | inverter029_masterControl | Master Control Enabled | 284 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Offline | Inverter | inverter029_offline | Offline | 285 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Ramp Up Enabled | Inverter | inverter029_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 286 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Ramp Down Enabled | Inverter | inverter029_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 287 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Real Power Curtailment Flag | Inverter | inverter029_curtailed | Real Power Curtailment Flag | 288 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Following Setpoint | Inverter | inverter029_follwing | Following Setpoint | 289 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_AutoStart On | Inverter | inverter030_MODBUS.HR0501_restartEn | AutoStart On | 290 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Comm Fail | Inverter | inverter030_commsFail | Comm Fail | 291 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Faulted | Inverter | inverter030_fault | Faulted | 292 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Locked Out | Inverter | inverter030_lockout | Locked Out | 293 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Master Control Enabled | Inverter | inverter030_masterControl | Master Control Enabled | 294 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Offline | Inverter | inverter030_offline | Offline | 295 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Ramp Up Enabled | Inverter | inverter030_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 296 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Ramp Down Enabled | Inverter | inverter030_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 297 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Real Power Curtailment Flag | Inverter | inverter030_curtailed | Real Power Curtailment Flag | 298 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Following Setpoint | Inverter | inverter030_follwing | Following Setpoint | 299 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_AutoStart On | Inverter | inverter031_MODBUS.HR0501_restartEn | AutoStart On | 300 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Comm Fail | Inverter | inverter031_commsFail | Comm Fail | 301 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Faulted | Inverter | inverter031_fault | Faulted | 302 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Locked Out | Inverter | inverter031_lockout | Locked Out | 303 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Master Control Enabled | Inverter | inverter031_masterControl | Master Control Enabled | 304 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Offline | Inverter | inverter031_offline | Offline | 305 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Ramp Up Enabled | Inverter | inverter031_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 306 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Ramp Down Enabled | Inverter | inverter031_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 307 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Real Power Curtailment Flag | Inverter | inverter031_curtailed | Real Power Curtailment Flag | 308 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Following Setpoint | Inverter | inverter031_follwing | Following Setpoint | 309 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_AutoStart On | Inverter | inverter032_MODBUS.HR0501_restartEn | AutoStart On | 310 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Comm Fail | Inverter | inverter032_commsFail | Comm Fail | 311 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Faulted | Inverter | inverter032_fault | Faulted | 312 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Locked Out | Inverter | inverter032_lockout | Locked Out | 313 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Master Control Enabled | Inverter | inverter032_masterControl | Master Control Enabled | 314 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Offline | Inverter | inverter032_offline | Offline | 315 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Ramp Up Enabled | Inverter | inverter032_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 316 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Ramp Down Enabled | Inverter | inverter032_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 317 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Real Power Curtailment Flag | Inverter | inverter032_curtailed | Real Power Curtailment Flag | 318 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Following Setpoint | Inverter | inverter032_follwing | Following Setpoint | 319 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_AutoStart On | Inverter | inverter033_MODBUS.HR0501_restartEn | AutoStart On | 320 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Comm Fail | Inverter | inverter033_commsFail | Comm Fail | 321 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Faulted | Inverter | inverter033_fault | Faulted | 322 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Locked Out | Inverter | inverter033_lockout | Locked Out | 323 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Master Control Enabled | Inverter | inverter033_masterControl | Master Control Enabled | 324 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Offline | Inverter | inverter033_offline | Offline | 325 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Ramp Up Enabled | Inverter | inverter033_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 326 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Ramp Down Enabled | Inverter | inverter033_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 327 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Real Power Curtailment Flag | Inverter | inverter033_curtailed | Real Power Curtailment Flag | 328 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Following Setpoint | Inverter | inverter033_follwing | Following Setpoint | 329 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_AutoStart On | Inverter | inverter034_MODBUS.HR0501_restartEn | AutoStart On | 330 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Comm Fail | Inverter | inverter034_commsFail | Comm Fail | 331 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Faulted | Inverter | inverter034_fault | Faulted | 332 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Locked Out | Inverter | inverter034_lockout | Locked Out | 333 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Master Control Enabled | Inverter | inverter034_masterControl | Master Control Enabled | 334 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Offline | Inverter | inverter034_offline | Offline | 335 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Ramp Up Enabled | Inverter | inverter034_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 336 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Ramp Down Enabled | Inverter | inverter034_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 337 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Real Power Curtailment Flag | Inverter | inverter034_curtailed | Real Power Curtailment Flag | 338 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Following Setpoint | Inverter | inverter034_follwing | Following Setpoint | 339 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_AutoStart On | Inverter | inverter035_MODBUS.HR0501_restartEn | AutoStart On | 340 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Comm Fail | Inverter | inverter035_commsFail | Comm Fail | 341 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Faulted | Inverter | inverter035_fault | Faulted | 342 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Locked Out | Inverter | inverter035_lockout | Locked Out | 343 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Master Control Enabled | Inverter | inverter035_masterControl | Master Control Enabled | 344 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Offline | Inverter | inverter035_offline | Offline | 345 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Ramp Up Enabled | Inverter | inverter035_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 346 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Ramp Down Enabled | Inverter | inverter035_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 347 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Real Power Curtailment Flag | Inverter | inverter035_curtailed | Real Power Curtailment Flag | 348 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Following Setpoint | Inverter | inverter035_follwing | Following Setpoint | 349 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_AutoStart On | Inverter | inverter036_MODBUS.HR0501_restartEn | AutoStart On | 350 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Comm Fail | Inverter | inverter036_commsFail | Comm Fail | 351 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Faulted | Inverter | inverter036_fault | Faulted | 352 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Locked Out | Inverter | inverter036_lockout | Locked Out | 353 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Master Control Enabled | Inverter | inverter036_masterControl | Master Control Enabled | 354 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Offline | Inverter | inverter036_offline | Offline | 355 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Ramp Up Enabled | Inverter | inverter036_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 356 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Ramp Down Enabled | Inverter | inverter036_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 357 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Real Power Curtailment Flag | Inverter | inverter036_curtailed | Real Power Curtailment Flag | 358 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Following Setpoint | Inverter | inverter036_follwing | Following Setpoint | 359 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_AutoStart On | Inverter | inverter037_MODBUS.HR0501_restartEn | AutoStart On | 360 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Comm Fail | Inverter | inverter037_commsFail | Comm Fail | 361 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Faulted | Inverter | inverter037_fault | Faulted | 362 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Locked Out | Inverter | inverter037_lockout | Locked Out | 363 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Master Control Enabled | Inverter | inverter037_masterControl | Master Control Enabled | 364 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Offline | Inverter | inverter037_offline | Offline | 365 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Ramp Up Enabled | Inverter | inverter037_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 366 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Ramp Down Enabled | Inverter | inverter037_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 367 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Real Power Curtailment Flag | Inverter | inverter037_curtailed | Real Power Curtailment Flag | 368 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Following Setpoint | Inverter | inverter037_follwing | Following Setpoint | 369 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_AutoStart On | Inverter | inverter038_MODBUS.HR0501_restartEn | AutoStart On | 370 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Comm Fail | Inverter | inverter038_commsFail | Comm Fail | 371 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Faulted | Inverter | inverter038_fault | Faulted | 372 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Locked Out | Inverter | inverter038_lockout | Locked Out | 373 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Master Control Enabled | Inverter | inverter038_masterControl | Master Control Enabled | 374 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Offline | Inverter | inverter038_offline | Offline | 375 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Ramp Up Enabled | Inverter | inverter038_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 376 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Ramp Down Enabled | Inverter | inverter038_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 377 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Real Power Curtailment Flag | Inverter | inverter038_curtailed | Real Power Curtailment Flag | 378 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Following Setpoint | Inverter | inverter038_follwing | Following Setpoint | 379 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_AutoStart On | Inverter | inverter039_MODBUS.HR0501_restartEn | AutoStart On | 380 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Comm Fail | Inverter | inverter039_commsFail | Comm Fail | 381 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Faulted | Inverter | inverter039_fault | Faulted | 382 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Locked Out | Inverter | inverter039_lockout | Locked Out | 383 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Master Control Enabled | Inverter | inverter039_masterControl | Master Control Enabled | 384 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Offline | Inverter | inverter039_offline | Offline | 385 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Ramp Up Enabled | Inverter | inverter039_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 386 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Ramp Down Enabled | Inverter | inverter039_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 387 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Real Power Curtailment Flag | Inverter | inverter039_curtailed | Real Power Curtailment Flag | 388 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Following Setpoint | Inverter | inverter039_follwing | Following Setpoint | 389 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_AutoStart On | Inverter | inverter040_MODBUS.HR0501_restartEn | AutoStart On | 390 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Comm Fail | Inverter | inverter040_commsFail | Comm Fail | 391 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Faulted | Inverter | inverter040_fault | Faulted | 392 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Locked Out | Inverter | inverter040_lockout | Locked Out | 393 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Master Control Enabled | Inverter | inverter040_masterControl | Master Control Enabled | 394 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Offline | Inverter | inverter040_offline | Offline | 395 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Ramp Up Enabled | Inverter | inverter040_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 396 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Ramp Down Enabled | Inverter | inverter040_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 397 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Real Power Curtailment Flag | Inverter | inverter040_curtailed | Real Power Curtailment Flag | 398 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Following Setpoint | Inverter | inverter040_follwing | Following Setpoint | 399 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_AutoStart On | Inverter | inverter041_MODBUS.HR0501_restartEn | AutoStart On | 400 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Comm Fail | Inverter | inverter041_commsFail | Comm Fail | 401 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Faulted | Inverter | inverter041_fault | Faulted | 402 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Locked Out | Inverter | inverter041_lockout | Locked Out | 403 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Master Control Enabled | Inverter | inverter041_masterControl | Master Control Enabled | 404 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Offline | Inverter | inverter041_offline | Offline | 405 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Ramp Up Enabled | Inverter | inverter041_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 406 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Ramp Down Enabled | Inverter | inverter041_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 407 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Real Power Curtailment Flag | Inverter | inverter041_curtailed | Real Power Curtailment Flag | 408 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Following Setpoint | Inverter | inverter041_follwing | Following Setpoint | 409 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_AutoStart On | Inverter | inverter042_MODBUS.HR0501_restartEn | AutoStart On | 410 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Comm Fail | Inverter | inverter042_commsFail | Comm Fail | 411 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Faulted | Inverter | inverter042_fault | Faulted | 412 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Locked Out | Inverter | inverter042_lockout | Locked Out | 413 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Master Control Enabled | Inverter | inverter042_masterControl | Master Control Enabled | 414 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Offline | Inverter | inverter042_offline | Offline | 415 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Ramp Up Enabled | Inverter | inverter042_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 416 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Ramp Down Enabled | Inverter | inverter042_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 417 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Real Power Curtailment Flag | Inverter | inverter042_curtailed | Real Power Curtailment Flag | 418 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Following Setpoint | Inverter | inverter042_follwing | Following Setpoint | 419 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_AutoStart On | Inverter | inverter043_MODBUS.HR0501_restartEn | AutoStart On | 420 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Comm Fail | Inverter | inverter043_commsFail | Comm Fail | 421 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Faulted | Inverter | inverter043_fault | Faulted | 422 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Locked Out | Inverter | inverter043_lockout | Locked Out | 423 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Master Control Enabled | Inverter | inverter043_masterControl | Master Control Enabled | 424 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Offline | Inverter | inverter043_offline | Offline | 425 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Ramp Up Enabled | Inverter | inverter043_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 426 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Ramp Down Enabled | Inverter | inverter043_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 427 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Real Power Curtailment Flag | Inverter | inverter043_curtailed | Real Power Curtailment Flag | 428 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Following Setpoint | Inverter | inverter043_follwing | Following Setpoint | 429 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_AutoStart On | Inverter | inverter044_MODBUS.HR0501_restartEn | AutoStart On | 430 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Comm Fail | Inverter | inverter044_commsFail | Comm Fail | 431 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Faulted | Inverter | inverter044_fault | Faulted | 432 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Locked Out | Inverter | inverter044_lockout | Locked Out | 433 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Master Control Enabled | Inverter | inverter044_masterControl | Master Control Enabled | 434 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Offline | Inverter | inverter044_offline | Offline | 435 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Ramp Up Enabled | Inverter | inverter044_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 436 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Ramp Down Enabled | Inverter | inverter044_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 437 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Real Power Curtailment Flag | Inverter | inverter044_curtailed | Real Power Curtailment Flag | 438 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Following Setpoint | Inverter | inverter044_follwing | Following Setpoint | 439 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_AutoStart On | Inverter | inverter045_MODBUS.HR0501_restartEn | AutoStart On | 440 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Comm Fail | Inverter | inverter045_commsFail | Comm Fail | 441 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Faulted | Inverter | inverter045_fault | Faulted | 442 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Locked Out | Inverter | inverter045_lockout | Locked Out | 443 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Master Control Enabled | Inverter | inverter045_masterControl | Master Control Enabled | 444 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Offline | Inverter | inverter045_offline | Offline | 445 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Ramp Up Enabled | Inverter | inverter045_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 446 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Ramp Down Enabled | Inverter | inverter045_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 447 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Real Power Curtailment Flag | Inverter | inverter045_curtailed | Real Power Curtailment Flag | 448 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Following Setpoint | Inverter | inverter045_follwing | Following Setpoint | 449 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_AutoStart On | Inverter | inverter046_MODBUS.HR0501_restartEn | AutoStart On | 450 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Comm Fail | Inverter | inverter046_commsFail | Comm Fail | 451 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Faulted | Inverter | inverter046_fault | Faulted | 452 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Locked Out | Inverter | inverter046_lockout | Locked Out | 453 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Master Control Enabled | Inverter | inverter046_masterControl | Master Control Enabled | 454 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Offline | Inverter | inverter046_offline | Offline | 455 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Ramp Up Enabled | Inverter | inverter046_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 456 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Ramp Down Enabled | Inverter | inverter046_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 457 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Real Power Curtailment Flag | Inverter | inverter046_curtailed | Real Power Curtailment Flag | 458 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Following Setpoint | Inverter | inverter046_follwing | Following Setpoint | 459 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_AutoStart On | Inverter | inverter047_MODBUS.HR0501_restartEn | AutoStart On | 460 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Comm Fail | Inverter | inverter047_commsFail | Comm Fail | 461 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Faulted | Inverter | inverter047_fault | Faulted | 462 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Locked Out | Inverter | inverter047_lockout | Locked Out | 463 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Master Control Enabled | Inverter | inverter047_masterControl | Master Control Enabled | 464 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Offline | Inverter | inverter047_offline | Offline | 465 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Ramp Up Enabled | Inverter | inverter047_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 466 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Ramp Down Enabled | Inverter | inverter047_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 467 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Real Power Curtailment Flag | Inverter | inverter047_curtailed | Real Power Curtailment Flag | 468 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Following Setpoint | Inverter | inverter047_follwing | Following Setpoint | 469 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_AutoStart On | Inverter | inverter048_MODBUS.HR0501_restartEn | AutoStart On | 470 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Comm Fail | Inverter | inverter048_commsFail | Comm Fail | 471 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Faulted | Inverter | inverter048_fault | Faulted | 472 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Locked Out | Inverter | inverter048_lockout | Locked Out | 473 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Master Control Enabled | Inverter | inverter048_masterControl | Master Control Enabled | 474 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Offline | Inverter | inverter048_offline | Offline | 475 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Ramp Up Enabled | Inverter | inverter048_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 476 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Ramp Down Enabled | Inverter | inverter048_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 477 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Real Power Curtailment Flag | Inverter | inverter048_curtailed | Real Power Curtailment Flag | 478 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Following Setpoint | Inverter | inverter048_follwing | Following Setpoint | 479 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_AutoStart On | Inverter | inverter049_MODBUS.HR0501_restartEn | AutoStart On | 480 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Comm Fail | Inverter | inverter049_commsFail | Comm Fail | 481 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Faulted | Inverter | inverter049_fault | Faulted | 482 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Locked Out | Inverter | inverter049_lockout | Locked Out | 483 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Master Control Enabled | Inverter | inverter049_masterControl | Master Control Enabled | 484 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Offline | Inverter | inverter049_offline | Offline | 485 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Ramp Up Enabled | Inverter | inverter049_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 486 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Ramp Down Enabled | Inverter | inverter049_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 487 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Real Power Curtailment Flag | Inverter | inverter049_curtailed | Real Power Curtailment Flag | 488 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Following Setpoint | Inverter | inverter049_follwing | Following Setpoint | 489 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_AutoStart On | Inverter | Inverter050_MODBUS.HR0501_restartEn | AutoStart On | 490 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Comm Fail | Inverter | Inverter050_commsFail | Comm Fail | 491 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Faulted | Inverter | Inverter050_fault | Faulted | 492 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Locked Out | Inverter | Inverter050_lockout | Locked Out | 493 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Master Control Enabled | Inverter | Inverter050_masterControl | Master Control Enabled | 494 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Offline | Inverter | Inverter050_offline | Offline | 495 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Ramp Up Enabled | Inverter | Inverter050_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 496 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Ramp Down Enabled | Inverter | Inverter050_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 497 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Real Power Curtailment Flag | Inverter | Inverter050_curtailed | Real Power Curtailment Flag | 498 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Following Setpoint | Inverter | Inverter050_follwing | Following Setpoint | 499 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_AutoStart On | Inverter | Inverter051_MODBUS.HR0501_restartEn | AutoStart On | 500 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Comm Fail | Inverter | Inverter051_commsFail | Comm Fail | 501 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Faulted | Inverter | Inverter051_fault | Faulted | 502 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Locked Out | Inverter | Inverter051_lockout | Locked Out | 503 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Master Control Enabled | Inverter | Inverter051_masterControl | Master Control Enabled | 504 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Offline | Inverter | Inverter051_offline | Offline | 505 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Ramp Up Enabled | Inverter | Inverter051_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 506 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Ramp Down Enabled | Inverter | Inverter051_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 507 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Real Power Curtailment Flag | Inverter | Inverter051_curtailed | Real Power Curtailment Flag | 508 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Following Setpoint | Inverter | Inverter051_follwing | Following Setpoint | 509 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_AutoStart On | Inverter | Inverter052_MODBUS.HR0501_restartEn | AutoStart On | 510 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Comm Fail | Inverter | Inverter052_commsFail | Comm Fail | 511 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Faulted | Inverter | Inverter052_fault | Faulted | 512 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Locked Out | Inverter | Inverter052_lockout | Locked Out | 513 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Master Control Enabled | Inverter | Inverter052_masterControl | Master Control Enabled | 514 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Offline | Inverter | Inverter052_offline | Offline | 515 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Ramp Up Enabled | Inverter | Inverter052_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 516 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Ramp Down Enabled | Inverter | Inverter052_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 517 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Real Power Curtailment Flag | Inverter | Inverter052_curtailed | Real Power Curtailment Flag | 518 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Following Setpoint | Inverter | Inverter052_follwing | Following Setpoint | 519 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_AutoStart On | Inverter | Inverter053_MODBUS.HR0501_restartEn | AutoStart On | 520 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Comm Fail | Inverter | Inverter053_commsFail | Comm Fail | 521 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Faulted | Inverter | Inverter053_fault | Faulted | 522 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Locked Out | Inverter | Inverter053_lockout | Locked Out | 523 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Master Control Enabled | Inverter | Inverter053_masterControl | Master Control Enabled | 524 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Offline | Inverter | Inverter053_offline | Offline | 525 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Ramp Up Enabled | Inverter | Inverter053_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 526 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Ramp Down Enabled | Inverter | Inverter053_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 527 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Real Power Curtailment Flag | Inverter | Inverter053_curtailed | Real Power Curtailment Flag | 528 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Following Setpoint | Inverter | Inverter053_follwing | Following Setpoint | 529 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_AutoStart On | Inverter | Inverter054_MODBUS.HR0501_restartEn | AutoStart On | 530 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Comm Fail | Inverter | Inverter054_commsFail | Comm Fail | 531 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Faulted | Inverter | Inverter054_fault | Faulted | 532 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Locked Out | Inverter | Inverter054_lockout | Locked Out | 533 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Master Control Enabled | Inverter | Inverter054_masterControl | Master Control Enabled | 534 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Offline | Inverter | Inverter054_offline | Offline | 535 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Ramp Up Enabled | Inverter | Inverter054_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 536 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Ramp Down Enabled | Inverter | Inverter054_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 537 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Real Power Curtailment Flag | Inverter | Inverter054_curtailed | Real Power Curtailment Flag | 538 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Following Setpoint | Inverter | Inverter054_follwing | Following Setpoint | 539 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_AutoStart On | Inverter | Inverter055_MODBUS.HR0501_restartEn | AutoStart On | 540 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Comm Fail | Inverter | Inverter055_commsFail | Comm Fail | 541 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Faulted | Inverter | Inverter055_fault | Faulted | 542 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Locked Out | Inverter | Inverter055_lockout | Locked Out | 543 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Master Control Enabled | Inverter | Inverter055_masterControl | Master Control Enabled | 544 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Offline | Inverter | Inverter055_offline | Offline | 545 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Ramp Up Enabled | Inverter | Inverter055_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 546 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Ramp Down Enabled | Inverter | Inverter055_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 547 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Real Power Curtailment Flag | Inverter | Inverter055_curtailed | Real Power Curtailment Flag | 548 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Following Setpoint | Inverter | Inverter055_follwing | Following Setpoint | 549 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_AutoStart On | Inverter | Inverter056_MODBUS.HR0501_restartEn | AutoStart On | 550 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Comm Fail | Inverter | Inverter056_commsFail | Comm Fail | 551 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Faulted | Inverter | Inverter056_fault | Faulted | 552 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Locked Out | Inverter | Inverter056_lockout | Locked Out | 553 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Master Control Enabled | Inverter | Inverter056_masterControl | Master Control Enabled | 554 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Offline | Inverter | Inverter056_offline | Offline | 555 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Ramp Up Enabled | Inverter | Inverter056_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 556 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Ramp Down Enabled | Inverter | Inverter056_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 557 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Real Power Curtailment Flag | Inverter | Inverter056_curtailed | Real Power Curtailment Flag | 558 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Following Setpoint | Inverter | Inverter056_follwing | Following Setpoint | 559 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_AutoStart On | Inverter | Inverter057_MODBUS.HR0501_restartEn | AutoStart On | 560 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Comm Fail | Inverter | Inverter057_commsFail | Comm Fail | 561 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Faulted | Inverter | Inverter057_fault | Faulted | 562 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Locked Out | Inverter | Inverter057_lockout | Locked Out | 563 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Master Control Enabled | Inverter | Inverter057_masterControl | Master Control Enabled | 564 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Offline | Inverter | Inverter057_offline | Offline | 565 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Ramp Up Enabled | Inverter | Inverter057_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 566 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Ramp Down Enabled | Inverter | Inverter057_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 567 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Real Power Curtailment Flag | Inverter | Inverter057_curtailed | Real Power Curtailment Flag | 568 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Following Setpoint | Inverter | Inverter057_follwing | Following Setpoint | 569 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_AutoStart On | Inverter | Inverter058_MODBUS.HR0501_restartEn | AutoStart On | 570 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Comm Fail | Inverter | Inverter058_commsFail | Comm Fail | 571 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Faulted | Inverter | Inverter058_fault | Faulted | 572 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Locked Out | Inverter | Inverter058_lockout | Locked Out | 573 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Master Control Enabled | Inverter | Inverter058_masterControl | Master Control Enabled | 574 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Offline | Inverter | Inverter058_offline | Offline | 575 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Ramp Up Enabled | Inverter | Inverter058_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 576 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Ramp Down Enabled | Inverter | Inverter058_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 577 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Real Power Curtailment Flag | Inverter | Inverter058_curtailed | Real Power Curtailment Flag | 578 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Following Setpoint | Inverter | Inverter058_follwing | Following Setpoint | 579 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_AutoStart On | Inverter | Inverter059_MODBUS.HR0501_restartEn | AutoStart On | 580 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Comm Fail | Inverter | Inverter059_commsFail | Comm Fail | 581 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Faulted | Inverter | Inverter059_fault | Faulted | 582 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Locked Out | Inverter | Inverter059_lockout | Locked Out | 583 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Master Control Enabled | Inverter | Inverter059_masterControl | Master Control Enabled | 584 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Offline | Inverter | Inverter059_offline | Offline | 585 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Ramp Up Enabled | Inverter | Inverter059_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 586 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Ramp Down Enabled | Inverter | Inverter059_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 587 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Real Power Curtailment Flag | Inverter | Inverter059_curtailed | Real Power Curtailment Flag | 588 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Following Setpoint | Inverter | Inverter059_follwing | Following Setpoint | 589 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_AutoStart On | Inverter | Inverter060_MODBUS.HR0501_restartEn | AutoStart On | 590 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Comm Fail | Inverter | Inverter060_commsFail | Comm Fail | 591 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Faulted | Inverter | Inverter060_fault | Faulted | 592 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Locked Out | Inverter | Inverter060_lockout | Locked Out | 593 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Master Control Enabled | Inverter | Inverter060_masterControl | Master Control Enabled | 594 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Offline | Inverter | Inverter060_offline | Offline | 595 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Ramp Up Enabled | Inverter | Inverter060_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 596 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Ramp Down Enabled | Inverter | Inverter060_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 597 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Real Power Curtailment Flag | Inverter | Inverter060_curtailed | Real Power Curtailment Flag | 598 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Following Setpoint | Inverter | Inverter060_follwing | Following Setpoint | 599 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_AutoStart On | Inverter | Inverter061_MODBUS.HR0501_restartEn | AutoStart On | 600 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Comm Fail | Inverter | Inverter061_commsFail | Comm Fail | 601 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Faulted | Inverter | Inverter061_fault | Faulted | 602 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Locked Out | Inverter | Inverter061_lockout | Locked Out | 603 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Master Control Enabled | Inverter | Inverter061_masterControl | Master Control Enabled | 604 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Offline | Inverter | Inverter061_offline | Offline | 605 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Ramp Up Enabled | Inverter | Inverter061_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 606 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Ramp Down Enabled | Inverter | Inverter061_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 607 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Real Power Curtailment Flag | Inverter | Inverter061_curtailed | Real Power Curtailment Flag | 608 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Following Setpoint | Inverter | Inverter061_follwing | Following Setpoint | 609 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_AutoStart On | Inverter | Inverter062_MODBUS.HR0501_restartEn | AutoStart On | 610 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Comm Fail | Inverter | Inverter062_commsFail | Comm Fail | 611 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Faulted | Inverter | Inverter062_fault | Faulted | 612 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Locked Out | Inverter | Inverter062_lockout | Locked Out | 613 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Master Control Enabled | Inverter | Inverter062_masterControl | Master Control Enabled | 614 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Offline | Inverter | Inverter062_offline | Offline | 615 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Ramp Up Enabled | Inverter | Inverter062_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 616 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Ramp Down Enabled | Inverter | Inverter062_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 617 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Real Power Curtailment Flag | Inverter | Inverter062_curtailed | Real Power Curtailment Flag | 618 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Following Setpoint | Inverter | Inverter062_follwing | Following Setpoint | 619 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_AutoStart On | Inverter | Inverter063_MODBUS.HR0501_restartEn | AutoStart On | 620 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Comm Fail | Inverter | Inverter063_commsFail | Comm Fail | 621 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Faulted | Inverter | Inverter063_fault | Faulted | 622 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Locked Out | Inverter | Inverter063_lockout | Locked Out | 623 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Master Control Enabled | Inverter | Inverter063_masterControl | Master Control Enabled | 624 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Offline | Inverter | Inverter063_offline | Offline | 625 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Ramp Up Enabled | Inverter | Inverter063_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 626 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Ramp Down Enabled | Inverter | Inverter063_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 627 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Real Power Curtailment Flag | Inverter | Inverter063_curtailed | Real Power Curtailment Flag | 628 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Following Setpoint | Inverter | Inverter063_follwing | Following Setpoint | 629 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_AutoStart On | Inverter | Inverter064_MODBUS.HR0501_restartEn | AutoStart On | 630 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Comm Fail | Inverter | Inverter064_commsFail | Comm Fail | 631 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Faulted | Inverter | Inverter064_fault | Faulted | 632 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Locked Out | Inverter | Inverter064_lockout | Locked Out | 633 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Master Control Enabled | Inverter | Inverter064_masterControl | Master Control Enabled | 634 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Offline | Inverter | Inverter064_offline | Offline | 635 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Ramp Up Enabled | Inverter | Inverter064_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 636 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Ramp Down Enabled | Inverter | Inverter064_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 637 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Real Power Curtailment Flag | Inverter | Inverter064_curtailed | Real Power Curtailment Flag | 638 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Following Setpoint | Inverter | Inverter064_follwing | Following Setpoint | 639 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_AutoStart On | Inverter | Inverter065_MODBUS.HR0501_restartEn | AutoStart On | 640 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Comm Fail | Inverter | Inverter065_commsFail | Comm Fail | 641 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Faulted | Inverter | Inverter065_fault | Faulted | 642 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Locked Out | Inverter | Inverter065_lockout | Locked Out | 643 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Master Control Enabled | Inverter | Inverter065_masterControl | Master Control Enabled | 644 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Offline | Inverter | Inverter065_offline | Offline | 645 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Ramp Up Enabled | Inverter | Inverter065_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 646 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Ramp Down Enabled | Inverter | Inverter065_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 647 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Real Power Curtailment Flag | Inverter | Inverter065_curtailed | Real Power Curtailment Flag | 648 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Following Setpoint | Inverter | Inverter065_follwing | Following Setpoint | 649 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_AutoStart On | Inverter | Inverter066_MODBUS.HR0501_restartEn | AutoStart On | 650 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Comm Fail | Inverter | Inverter066_commsFail | Comm Fail | 651 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Faulted | Inverter | Inverter066_fault | Faulted | 652 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Locked Out | Inverter | Inverter066_lockout | Locked Out | 653 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Master Control Enabled | Inverter | Inverter066_masterControl | Master Control Enabled | 654 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Offline | Inverter | Inverter066_offline | Offline | 655 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Ramp Up Enabled | Inverter | Inverter066_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 656 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Ramp Down Enabled | Inverter | Inverter066_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 657 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Real Power Curtailment Flag | Inverter | Inverter066_curtailed | Real Power Curtailment Flag | 658 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Following Setpoint | Inverter | Inverter066_follwing | Following Setpoint | 659 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_AutoStart On | Inverter | Inverter067_MODBUS.HR0501_restartEn | AutoStart On | 660 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Comm Fail | Inverter | Inverter067_commsFail | Comm Fail | 661 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Faulted | Inverter | Inverter067_fault | Faulted | 662 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Locked Out | Inverter | Inverter067_lockout | Locked Out | 663 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Master Control Enabled | Inverter | Inverter067_masterControl | Master Control Enabled | 664 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Offline | Inverter | Inverter067_offline | Offline | 665 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Ramp Up Enabled | Inverter | Inverter067_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 666 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Ramp Down Enabled | Inverter | Inverter067_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 667 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Real Power Curtailment Flag | Inverter | Inverter067_curtailed | Real Power Curtailment Flag | 668 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Following Setpoint | Inverter | Inverter067_follwing | Following Setpoint | 669 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_AutoStart On | Inverter | Inverter068_MODBUS.HR0501_restartEn | AutoStart On | 670 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Comm Fail | Inverter | Inverter068_commsFail | Comm Fail | 671 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Faulted | Inverter | Inverter068_fault | Faulted | 672 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Locked Out | Inverter | Inverter068_lockout | Locked Out | 673 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Master Control Enabled | Inverter | Inverter068_masterControl | Master Control Enabled | 674 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Offline | Inverter | Inverter068_offline | Offline | 675 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Ramp Up Enabled | Inverter | Inverter068_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 676 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Ramp Down Enabled | Inverter | Inverter068_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 677 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Real Power Curtailment Flag | Inverter | Inverter068_curtailed | Real Power Curtailment Flag | 678 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Following Setpoint | Inverter | Inverter068_follwing | Following Setpoint | 679 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_AutoStart On | Inverter | Inverter069_MODBUS.HR0501_restartEn | AutoStart On | 680 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Comm Fail | Inverter | Inverter069_commsFail | Comm Fail | 681 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Faulted | Inverter | Inverter069_fault | Faulted | 682 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Locked Out | Inverter | Inverter069_lockout | Locked Out | 683 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Master Control Enabled | Inverter | Inverter069_masterControl | Master Control Enabled | 684 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Offline | Inverter | Inverter069_offline | Offline | 685 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Ramp Up Enabled | Inverter | Inverter069_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 686 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Ramp Down Enabled | Inverter | Inverter069_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 687 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Real Power Curtailment Flag | Inverter | Inverter069_curtailed | Real Power Curtailment Flag | 688 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Following Setpoint | Inverter | Inverter069_follwing | Following Setpoint | 689 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_AutoStart On | Inverter | inverter070_MODBUS.HR0501_restartEn | AutoStart On | 690 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Comm Fail | Inverter | inverter070_commsFail | Comm Fail | 691 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Faulted | Inverter | inverter070_fault | Faulted | 692 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Locked Out | Inverter | inverter070_lockout | Locked Out | 693 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Master Control Enabled | Inverter | inverter070_masterControl | Master Control Enabled | 694 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Offline | Inverter | inverter070_offline | Offline | 695 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Ramp Up Enabled | Inverter | inverter070_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 696 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Ramp Down Enabled | Inverter | inverter070_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 697 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Real Power Curtailment Flag | Inverter | inverter070_curtailed | Real Power Curtailment Flag | 698 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Following Setpoint | Inverter | inverter070_follwing | Following Setpoint | 699 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_AutoStart On | Inverter | inverter071_MODBUS.HR0501_restartEn | AutoStart On | 700 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Comm Fail | Inverter | inverter071_commsFail | Comm Fail | 701 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Faulted | Inverter | inverter071_fault | Faulted | 702 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Locked Out | Inverter | inverter071_lockout | Locked Out | 703 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Master Control Enabled | Inverter | inverter071_masterControl | Master Control Enabled | 704 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Offline | Inverter | inverter071_offline | Offline | 705 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Ramp Up Enabled | Inverter | inverter071_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 706 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Ramp Down Enabled | Inverter | inverter071_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 707 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Real Power Curtailment Flag | Inverter | inverter071_curtailed | Real Power Curtailment Flag | 708 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Following Setpoint | Inverter | inverter071_follwing | Following Setpoint | 709 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_AutoStart On | Inverter | inverter072_MODBUS.HR0501_restartEn | AutoStart On | 710 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Comm Fail | Inverter | inverter072_commsFail | Comm Fail | 711 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Faulted | Inverter | inverter072_fault | Faulted | 712 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Locked Out | Inverter | inverter072_lockout | Locked Out | 713 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Master Control Enabled | Inverter | inverter072_masterControl | Master Control Enabled | 714 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Offline | Inverter | inverter072_offline | Offline | 715 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Ramp Up Enabled | Inverter | inverter072_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 716 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Ramp Down Enabled | Inverter | inverter072_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 717 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Real Power Curtailment Flag | Inverter | inverter072_curtailed | Real Power Curtailment Flag | 718 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Following Setpoint | Inverter | inverter072_follwing | Following Setpoint | 719 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_AutoStart On | Inverter | inverter073_MODBUS.HR0501_restartEn | AutoStart On | 720 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Comm Fail | Inverter | inverter073_commsFail | Comm Fail | 721 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Faulted | Inverter | inverter073_fault | Faulted | 722 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Locked Out | Inverter | inverter073_lockout | Locked Out | 723 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Master Control Enabled | Inverter | inverter073_masterControl | Master Control Enabled | 724 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Offline | Inverter | inverter073_offline | Offline | 725 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Ramp Up Enabled | Inverter | inverter073_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 726 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Ramp Down Enabled | Inverter | inverter073_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 727 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Real Power Curtailment Flag | Inverter | inverter073_curtailed | Real Power Curtailment Flag | 728 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Following Setpoint | Inverter | inverter073_follwing | Following Setpoint | 729 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_AutoStart On | Inverter | inverter074_MODBUS.HR0501_restartEn | AutoStart On | 730 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Comm Fail | Inverter | inverter074_commsFail | Comm Fail | 731 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Faulted | Inverter | inverter074_fault | Faulted | 732 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Locked Out | Inverter | inverter074_lockout | Locked Out | 733 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Master Control Enabled | Inverter | inverter074_masterControl | Master Control Enabled | 734 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Offline | Inverter | inverter074_offline | Offline | 735 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Ramp Up Enabled | Inverter | inverter074_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 736 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Ramp Down Enabled | Inverter | inverter074_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 737 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Real Power Curtailment Flag | Inverter | inverter074_curtailed | Real Power Curtailment Flag | 738 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Following Setpoint | Inverter | inverter074_follwing | Following Setpoint | 739 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_AutoStart On | Inverter | inverter075_MODBUS.HR0501_restartEn | AutoStart On | 740 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Comm Fail | Inverter | inverter075_commsFail | Comm Fail | 741 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Faulted | Inverter | inverter075_fault | Faulted | 742 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Locked Out | Inverter | inverter075_lockout | Locked Out | 743 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Master Control Enabled | Inverter | inverter075_masterControl | Master Control Enabled | 744 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Offline | Inverter | inverter075_offline | Offline | 745 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Ramp Up Enabled | Inverter | inverter075_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 746 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Ramp Down Enabled | Inverter | inverter075_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 747 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Real Power Curtailment Flag | Inverter | inverter075_curtailed | Real Power Curtailment Flag | 748 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Following Setpoint | Inverter | inverter075_follwing | Following Setpoint | 749 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_AutoStart On | Inverter | inverter076_MODBUS.HR0501_restartEn | AutoStart On | 750 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Comm Fail | Inverter | inverter076_commsFail | Comm Fail | 751 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Faulted | Inverter | inverter076_fault | Faulted | 752 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Locked Out | Inverter | inverter076_lockout | Locked Out | 753 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Master Control Enabled | Inverter | inverter076_masterControl | Master Control Enabled | 754 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Offline | Inverter | inverter076_offline | Offline | 755 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Ramp Up Enabled | Inverter | inverter076_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 756 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Ramp Down Enabled | Inverter | inverter076_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 757 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Real Power Curtailment Flag | Inverter | inverter076_curtailed | Real Power Curtailment Flag | 758 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Following Setpoint | Inverter | inverter076_follwing | Following Setpoint | 759 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_AutoStart On | Inverter | inverter077_MODBUS.HR0501_restartEn | AutoStart On | 760 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Comm Fail | Inverter | inverter077_commsFail | Comm Fail | 761 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Faulted | Inverter | inverter077_fault | Faulted | 762 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Locked Out | Inverter | inverter077_lockout | Locked Out | 763 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Master Control Enabled | Inverter | inverter077_masterControl | Master Control Enabled | 764 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Offline | Inverter | inverter077_offline | Offline | 765 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Ramp Up Enabled | Inverter | inverter077_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 766 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Ramp Down Enabled | Inverter | inverter077_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 767 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Real Power Curtailment Flag | Inverter | inverter077_curtailed | Real Power Curtailment Flag | 768 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Following Setpoint | Inverter | inverter077_follwing | Following Setpoint | 769 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_AutoStart On | Inverter | inverter078_MODBUS.HR0501_restartEn | AutoStart On | 770 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Comm Fail | Inverter | inverter078_commsFail | Comm Fail | 771 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Faulted | Inverter | inverter078_fault | Faulted | 772 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Locked Out | Inverter | inverter078_lockout | Locked Out | 773 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Master Control Enabled | Inverter | inverter078_masterControl | Master Control Enabled | 774 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Offline | Inverter | inverter078_offline | Offline | 775 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Ramp Up Enabled | Inverter | inverter078_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 776 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Ramp Down Enabled | Inverter | inverter078_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 777 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Real Power Curtailment Flag | Inverter | inverter078_curtailed | Real Power Curtailment Flag | 778 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Following Setpoint | Inverter | inverter078_follwing | Following Setpoint | 779 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_AutoStart On | Inverter | inverter079_MODBUS.HR0501_restartEn | AutoStart On | 780 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Comm Fail | Inverter | inverter079_commsFail | Comm Fail | 781 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Faulted | Inverter | inverter079_fault | Faulted | 782 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Locked Out | Inverter | inverter079_lockout | Locked Out | 783 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Master Control Enabled | Inverter | inverter079_masterControl | Master Control Enabled | 784 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Offline | Inverter | inverter079_offline | Offline | 785 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Ramp Up Enabled | Inverter | inverter079_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 786 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Ramp Down Enabled | Inverter | inverter079_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 787 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Real Power Curtailment Flag | Inverter | inverter079_curtailed | Real Power Curtailment Flag | 788 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Following Setpoint | Inverter | inverter079_follwing | Following Setpoint | 789 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_AutoStart On | Inverter | inverter080_MODBUS.HR0501_restartEn | AutoStart On | 790 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Comm Fail | Inverter | inverter080_commsFail | Comm Fail | 791 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Faulted | Inverter | inverter080_fault | Faulted | 792 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Locked Out | Inverter | inverter080_lockout | Locked Out | 793 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Master Control Enabled | Inverter | inverter080_masterControl | Master Control Enabled | 794 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Offline | Inverter | inverter080_offline | Offline | 795 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Ramp Up Enabled | Inverter | inverter080_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 796 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Ramp Down Enabled | Inverter | inverter080_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 797 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Real Power Curtailment Flag | Inverter | inverter080_curtailed | Real Power Curtailment Flag | 798 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Following Setpoint | Inverter | inverter080_follwing | Following Setpoint | 799 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_AutoStart On | Inverter | inverter081_MODBUS.HR0501_restartEn | AutoStart On | 800 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Comm Fail | Inverter | inverter081_commsFail | Comm Fail | 801 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Faulted | Inverter | inverter081_fault | Faulted | 802 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Locked Out | Inverter | inverter081_lockout | Locked Out | 803 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Master Control Enabled | Inverter | inverter081_masterControl | Master Control Enabled | 804 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Offline | Inverter | inverter081_offline | Offline | 805 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Ramp Up Enabled | Inverter | inverter081_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 806 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Ramp Down Enabled | Inverter | inverter081_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 807 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Real Power Curtailment Flag | Inverter | inverter081_curtailed | Real Power Curtailment Flag | 808 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Following Setpoint | Inverter | inverter081_follwing | Following Setpoint | 809 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_AutoStart On | Inverter | inverter082_MODBUS.HR0501_restartEn | AutoStart On | 810 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Comm Fail | Inverter | inverter082_commsFail | Comm Fail | 811 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Faulted | Inverter | inverter082_fault | Faulted | 812 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Locked Out | Inverter | inverter082_lockout | Locked Out | 813 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Master Control Enabled | Inverter | inverter082_masterControl | Master Control Enabled | 814 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Offline | Inverter | inverter082_offline | Offline | 815 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Ramp Up Enabled | Inverter | inverter082_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 816 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Ramp Down Enabled | Inverter | inverter082_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 817 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Real Power Curtailment Flag | Inverter | inverter082_curtailed | Real Power Curtailment Flag | 818 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Following Setpoint | Inverter | inverter082_follwing | Following Setpoint | 819 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_AutoStart On | Inverter | inverter083_MODBUS.HR0501_restartEn | AutoStart On | 820 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Comm Fail | Inverter | inverter083_commsFail | Comm Fail | 821 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Faulted | Inverter | inverter083_fault | Faulted | 822 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Locked Out | Inverter | inverter083_lockout | Locked Out | 823 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Master Control Enabled | Inverter | inverter083_masterControl | Master Control Enabled | 824 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Offline | Inverter | inverter083_offline | Offline | 825 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Ramp Up Enabled | Inverter | inverter083_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 826 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Ramp Down Enabled | Inverter | inverter083_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 827 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Real Power Curtailment Flag | Inverter | inverter083_curtailed | Real Power Curtailment Flag | 828 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Following Setpoint | Inverter | inverter083_follwing | Following Setpoint | 829 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_AutoStart On | Inverter | inverter084_MODBUS.HR0501_restartEn | AutoStart On | 830 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Comm Fail | Inverter | inverter084_commsFail | Comm Fail | 831 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Faulted | Inverter | inverter084_fault | Faulted | 832 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Locked Out | Inverter | inverter084_lockout | Locked Out | 833 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Master Control Enabled | Inverter | inverter084_masterControl | Master Control Enabled | 834 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Offline | Inverter | inverter084_offline | Offline | 835 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Ramp Up Enabled | Inverter | inverter084_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 836 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Ramp Down Enabled | Inverter | inverter084_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 837 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Real Power Curtailment Flag | Inverter | inverter084_curtailed | Real Power Curtailment Flag | 838 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Following Setpoint | Inverter | inverter084_follwing | Following Setpoint | 839 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_AutoStart On | Inverter | inverter085_MODBUS.HR0501_restartEn | AutoStart On | 840 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Comm Fail | Inverter | inverter085_commsFail | Comm Fail | 841 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Faulted | Inverter | inverter085_fault | Faulted | 842 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Locked Out | Inverter | inverter085_lockout | Locked Out | 843 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Master Control Enabled | Inverter | inverter085_masterControl | Master Control Enabled | 844 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Offline | Inverter | inverter085_offline | Offline | 845 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Ramp Up Enabled | Inverter | inverter085_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 846 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Ramp Down Enabled | Inverter | inverter085_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 847 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Real Power Curtailment Flag | Inverter | inverter085_curtailed | Real Power Curtailment Flag | 848 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Following Setpoint | Inverter | inverter085_follwing | Following Setpoint | 849 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_AutoStart On | Inverter | inverter086_MODBUS.HR0501_restartEn | AutoStart On | 850 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Comm Fail | Inverter | inverter086_commsFail | Comm Fail | 851 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Faulted | Inverter | inverter086_fault | Faulted | 852 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Locked Out | Inverter | inverter086_lockout | Locked Out | 853 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Master Control Enabled | Inverter | inverter086_masterControl | Master Control Enabled | 854 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Offline | Inverter | inverter086_offline | Offline | 855 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Ramp Up Enabled | Inverter | inverter086_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 856 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Ramp Down Enabled | Inverter | inverter086_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 857 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Real Power Curtailment Flag | Inverter | inverter086_curtailed | Real Power Curtailment Flag | 858 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Following Setpoint | Inverter | inverter086_follwing | Following Setpoint | 859 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_AutoStart On | Inverter | inverter087_MODBUS.HR0501_restartEn | AutoStart On | 860 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Comm Fail | Inverter | inverter087_commsFail | Comm Fail | 861 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Faulted | Inverter | inverter087_fault | Faulted | 862 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Locked Out | Inverter | inverter087_lockout | Locked Out | 863 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Master Control Enabled | Inverter | inverter087_masterControl | Master Control Enabled | 864 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Offline | Inverter | inverter087_offline | Offline | 865 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Ramp Up Enabled | Inverter | inverter087_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 866 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Ramp Down Enabled | Inverter | inverter087_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 867 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Real Power Curtailment Flag | Inverter | inverter087_curtailed | Real Power Curtailment Flag | 868 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Following Setpoint | Inverter | inverter087_follwing | Following Setpoint | 869 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_AutoStart On | Inverter | inverter088_MODBUS.HR0501_restartEn | AutoStart On | 870 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Comm Fail | Inverter | inverter088_commsFail | Comm Fail | 871 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Faulted | Inverter | inverter088_fault | Faulted | 872 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Locked Out | Inverter | inverter088_lockout | Locked Out | 873 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Master Control Enabled | Inverter | inverter088_masterControl | Master Control Enabled | 874 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Offline | Inverter | inverter088_offline | Offline | 875 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Ramp Up Enabled | Inverter | inverter088_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 876 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Ramp Down Enabled | Inverter | inverter088_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 877 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Real Power Curtailment Flag | Inverter | inverter088_curtailed | Real Power Curtailment Flag | 878 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Following Setpoint | Inverter | inverter088_follwing | Following Setpoint | 879 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_AutoStart On | Inverter | inverter089_MODBUS.HR0501_restartEn | AutoStart On | 880 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Comm Fail | Inverter | inverter089_commsFail | Comm Fail | 881 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Faulted | Inverter | inverter089_fault | Faulted | 882 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Locked Out | Inverter | inverter089_lockout | Locked Out | 883 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Master Control Enabled | Inverter | inverter089_masterControl | Master Control Enabled | 884 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Offline | Inverter | inverter089_offline | Offline | 885 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Ramp Up Enabled | Inverter | inverter089_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 886 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Ramp Down Enabled | Inverter | inverter089_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 887 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Real Power Curtailment Flag | Inverter | inverter089_curtailed | Real Power Curtailment Flag | 888 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Following Setpoint | Inverter | inverter089_follwing | Following Setpoint | 889 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_AutoStart On | Inverter | inverter090_MODBUS.HR0501_restartEn | AutoStart On | 890 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Comm Fail | Inverter | inverter090_commsFail | Comm Fail | 891 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Faulted | Inverter | inverter090_fault | Faulted | 892 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Locked Out | Inverter | inverter090_lockout | Locked Out | 893 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Master Control Enabled | Inverter | inverter090_masterControl | Master Control Enabled | 894 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Offline | Inverter | inverter090_offline | Offline | 895 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Ramp Up Enabled | Inverter | inverter090_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 896 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Ramp Down Enabled | Inverter | inverter090_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 897 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Real Power Curtailment Flag | Inverter | inverter090_curtailed | Real Power Curtailment Flag | 898 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Following Setpoint | Inverter | inverter090_follwing | Following Setpoint | 899 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_AutoStart On | Inverter | inverter091_MODBUS.HR0501_restartEn | AutoStart On | 900 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Comm Fail | Inverter | inverter091_commsFail | Comm Fail | 901 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Faulted | Inverter | inverter091_fault | Faulted | 902 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Locked Out | Inverter | inverter091_lockout | Locked Out | 903 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Master Control Enabled | Inverter | inverter091_masterControl | Master Control Enabled | 904 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Offline | Inverter | inverter091_offline | Offline | 905 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Ramp Up Enabled | Inverter | inverter091_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 906 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Ramp Down Enabled | Inverter | inverter091_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 907 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Real Power Curtailment Flag | Inverter | inverter091_curtailed | Real Power Curtailment Flag | 908 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Following Setpoint | Inverter | inverter091_follwing | Following Setpoint | 909 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_AutoStart On | Inverter | inverter092_MODBUS.HR0501_restartEn | AutoStart On | 910 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Comm Fail | Inverter | inverter092_commsFail | Comm Fail | 911 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Faulted | Inverter | inverter092_fault | Faulted | 912 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Locked Out | Inverter | inverter092_lockout | Locked Out | 913 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Master Control Enabled | Inverter | inverter092_masterControl | Master Control Enabled | 914 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Offline | Inverter | inverter092_offline | Offline | 915 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Ramp Up Enabled | Inverter | inverter092_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 916 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Ramp Down Enabled | Inverter | inverter092_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 917 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Real Power Curtailment Flag | Inverter | inverter092_curtailed | Real Power Curtailment Flag | 918 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Following Setpoint | Inverter | inverter092_follwing | Following Setpoint | 919 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_AutoStart On | Inverter | inverter093_MODBUS.HR0501_restartEn | AutoStart On | 920 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Comm Fail | Inverter | inverter093_commsFail | Comm Fail | 921 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Faulted | Inverter | inverter093_fault | Faulted | 922 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Locked Out | Inverter | inverter093_lockout | Locked Out | 923 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Master Control Enabled | Inverter | inverter093_masterControl | Master Control Enabled | 924 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Offline | Inverter | inverter093_offline | Offline | 925 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Ramp Up Enabled | Inverter | inverter093_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 926 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Ramp Down Enabled | Inverter | inverter093_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 927 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Real Power Curtailment Flag | Inverter | inverter093_curtailed | Real Power Curtailment Flag | 928 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Following Setpoint | Inverter | inverter093_follwing | Following Setpoint | 929 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_AutoStart On | Inverter | inverter094_MODBUS.HR0501_restartEn | AutoStart On | 930 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Comm Fail | Inverter | inverter094_commsFail | Comm Fail | 931 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Faulted | Inverter | inverter094_fault | Faulted | 932 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Locked Out | Inverter | inverter094_lockout | Locked Out | 933 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Master Control Enabled | Inverter | inverter094_masterControl | Master Control Enabled | 934 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Offline | Inverter | inverter094_offline | Offline | 935 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Ramp Up Enabled | Inverter | inverter094_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 936 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Ramp Down Enabled | Inverter | inverter094_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 937 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Real Power Curtailment Flag | Inverter | inverter094_curtailed | Real Power Curtailment Flag | 938 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Following Setpoint | Inverter | inverter094_follwing | Following Setpoint | 939 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_AutoStart On | Inverter | inverter095_MODBUS.HR0501_restartEn | AutoStart On | 940 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Comm Fail | Inverter | inverter095_commsFail | Comm Fail | 941 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Faulted | Inverter | inverter095_fault | Faulted | 942 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Locked Out | Inverter | inverter095_lockout | Locked Out | 943 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Master Control Enabled | Inverter | inverter095_masterControl | Master Control Enabled | 944 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Offline | Inverter | inverter095_offline | Offline | 945 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Ramp Up Enabled | Inverter | inverter095_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 946 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Ramp Down Enabled | Inverter | inverter095_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 947 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Real Power Curtailment Flag | Inverter | inverter095_curtailed | Real Power Curtailment Flag | 948 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Following Setpoint | Inverter | inverter095_follwing | Following Setpoint | 949 | 0=False, 1=TRUE | Requested-Available
Counters
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | ROLLOVER VALUE
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV001 | Dagget 3_SUB1_INV001_Start | Inverter | Inverter001_start | Start | 0 | LatchOff/LatchOn | Requested-Available
SUB1 | INV001 | Dagget 3_SUB1_INV001_Stop | Inverter | Inverter001_stop | Stop | 1 | LatchOff/LatchOn | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Start | Inverter | Inverter002_start | Start | 2 | LatchOff/LatchOn | Requested-Available
SUB1 | INV002 | Dagget 3_SUB1_INV002_Stop | Inverter | Inverter002_stop | Stop | 3 | LatchOff/LatchOn | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Start | Inverter | Inverter003_start | Start | 4 | LatchOff/LatchOn | Requested-Available
SUB1 | INV003 | Dagget 3_SUB1_INV003_Stop | Inverter | Inverter003_stop | Stop | 5 | LatchOff/LatchOn | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Start | Inverter | Inverter004_start | Start | 6 | LatchOff/LatchOn | Requested-Available
SUB1 | INV004 | Dagget 3_SUB1_INV004_Stop | Inverter | Inverter004_stop | Stop | 7 | LatchOff/LatchOn | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Start | Inverter | Inverter005_start | Start | 8 | LatchOff/LatchOn | Requested-Available
SUB1 | INV005 | Dagget 3_SUB1_INV005_Stop | Inverter | Inverter005_stop | Stop | 9 | LatchOff/LatchOn | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Start | Inverter | Inverter006_start | Start | 10 | LatchOff/LatchOn | Requested-Available
SUB1 | INV006 | Dagget 3_SUB1_INV006_Stop | Inverter | Inverter006_stop | Stop | 11 | LatchOff/LatchOn | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Start | Inverter | Inverter007_start | Start | 12 | LatchOff/LatchOn | Requested-Available
SUB1 | INV007 | Dagget 3_SUB1_INV007_Stop | Inverter | Inverter007_stop | Stop | 13 | LatchOff/LatchOn | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Start | Inverter | Inverter008_start | Start | 14 | LatchOff/LatchOn | Requested-Available
SUB1 | INV008 | Dagget 3_SUB1_INV008_Stop | Inverter | Inverter008_stop | Stop | 15 | LatchOff/LatchOn | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Start | Inverter | Inverter009_start | Start | 16 | LatchOff/LatchOn | Requested-Available
SUB1 | INV009 | Dagget 3_SUB1_INV009_Stop | Inverter | Inverter009_stop | Stop | 17 | LatchOff/LatchOn | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Start | Inverter | Inverter010_start | Start | 18 | LatchOff/LatchOn | Requested-Available
SUB1 | INV010 | Dagget 3_SUB1_INV010_Stop | Inverter | Inverter010_stop | Stop | 19 | LatchOff/LatchOn | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Start | Inverter | inverter011_start | Start | 20 | LatchOff/LatchOn | Requested-Available
SUB1 | INV011 | Dagget 3_SUB1_INV011_Stop | Inverter | inverter011_stop | Stop | 21 | LatchOff/LatchOn | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Start | Inverter | inverter012_start | Start | 22 | LatchOff/LatchOn | Requested-Available
SUB1 | INV012 | Dagget 3_SUB1_INV012_Stop | Inverter | inverter012_stop | Stop | 23 | LatchOff/LatchOn | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Start | Inverter | inverter013_start | Start | 24 | LatchOff/LatchOn | Requested-Available
SUB1 | INV013 | Dagget 3_SUB1_INV013_Stop | Inverter | inverter013_stop | Stop | 25 | LatchOff/LatchOn | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Start | Inverter | inverter014_start | Start | 26 | LatchOff/LatchOn | Requested-Available
SUB1 | INV014 | Dagget 3_SUB1_INV014_Stop | Inverter | inverter014_stop | Stop | 27 | LatchOff/LatchOn | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Start | Inverter | inverter015_start | Start | 28 | LatchOff/LatchOn | Requested-Available
SUB1 | INV015 | Dagget 3_SUB1_INV015_Stop | Inverter | inverter015_stop | Stop | 29 | LatchOff/LatchOn | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Start | Inverter | inverter016_start | Start | 30 | LatchOff/LatchOn | Requested-Available
SUB1 | INV016 | Dagget 3_SUB1_INV016_Stop | Inverter | inverter016_stop | Stop | 31 | LatchOff/LatchOn | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Start | Inverter | inverter017_start | Start | 32 | LatchOff/LatchOn | Requested-Available
SUB1 | INV017 | Dagget 3_SUB1_INV017_Stop | Inverter | inverter017_stop | Stop | 33 | LatchOff/LatchOn | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Start | Inverter | inverter018_start | Start | 34 | LatchOff/LatchOn | Requested-Available
SUB1 | INV018 | Dagget 3_SUB1_INV018_Stop | Inverter | inverter018_stop | Stop | 35 | LatchOff/LatchOn | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Start | Inverter | inverter019_start | Start | 36 | LatchOff/LatchOn | Requested-Available
SUB1 | INV019 | Dagget 3_SUB1_INV019_Stop | Inverter | inverter019_stop | Stop | 37 | LatchOff/LatchOn | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Start | Inverter | inverter020_start | Start | 38 | LatchOff/LatchOn | Requested-Available
SUB1 | INV020 | Dagget 3_SUB1_INV020_Stop | Inverter | inverter020_stop | Stop | 39 | LatchOff/LatchOn | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Start | Inverter | inverter021_start | Start | 40 | LatchOff/LatchOn | Requested-Available
SUB1 | INV021 | Dagget 3_SUB1_INV021_Stop | Inverter | inverter021_stop | Stop | 41 | LatchOff/LatchOn | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Start | Inverter | inverter022_start | Start | 42 | LatchOff/LatchOn | Requested-Available
SUB1 | INV022 | Dagget 3_SUB1_INV022_Stop | Inverter | inverter022_stop | Stop | 43 | LatchOff/LatchOn | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Start | Inverter | inverter023_start | Start | 44 | LatchOff/LatchOn | Requested-Available
SUB1 | INV023 | Dagget 3_SUB1_INV023_Stop | Inverter | inverter023_stop | Stop | 45 | LatchOff/LatchOn | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Start | Inverter | inverter024_start | Start | 46 | LatchOff/LatchOn | Requested-Available
SUB1 | INV024 | Dagget 3_SUB1_INV024_Stop | Inverter | inverter024_stop | Stop | 47 | LatchOff/LatchOn | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Start | Inverter | inverter025_start | Start | 48 | LatchOff/LatchOn | Requested-Available
SUB1 | INV025 | Dagget 3_SUB1_INV025_Stop | Inverter | inverter025_stop | Stop | 49 | LatchOff/LatchOn | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Start | Inverter | inverter026_start | Start | 50 | LatchOff/LatchOn | Requested-Available
SUB1 | INV026 | Dagget 3_SUB1_INV026_Stop | Inverter | inverter026_stop | Stop | 51 | LatchOff/LatchOn | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Start | Inverter | inverter027_start | Start | 52 | LatchOff/LatchOn | Requested-Available
SUB1 | INV027 | Dagget 3_SUB1_INV027_Stop | Inverter | inverter027_stop | Stop | 53 | LatchOff/LatchOn | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Start | Inverter | inverter028_start | Start | 54 | LatchOff/LatchOn | Requested-Available
SUB1 | INV028 | Dagget 3_SUB1_INV028_Stop | Inverter | inverter028_stop | Stop | 55 | LatchOff/LatchOn | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Start | Inverter | inverter029_start | Start | 56 | LatchOff/LatchOn | Requested-Available
SUB1 | INV029 | Dagget 3_SUB1_INV029_Stop | Inverter | inverter029_stop | Stop | 57 | LatchOff/LatchOn | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Start | Inverter | inverter030_start | Start | 58 | LatchOff/LatchOn | Requested-Available
SUB1 | INV030 | Dagget 3_SUB1_INV030_Stop | Inverter | inverter030_stop | Stop | 59 | LatchOff/LatchOn | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Start | Inverter | inverter031_start | Start | 60 | LatchOff/LatchOn | Requested-Available
SUB1 | INV031 | Dagget 3_SUB1_INV031_Stop | Inverter | inverter031_stop | Stop | 61 | LatchOff/LatchOn | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Start | Inverter | inverter032_start | Start | 62 | LatchOff/LatchOn | Requested-Available
SUB1 | INV032 | Dagget 3_SUB1_INV032_Stop | Inverter | inverter032_stop | Stop | 63 | LatchOff/LatchOn | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Start | Inverter | inverter033_start | Start | 64 | LatchOff/LatchOn | Requested-Available
SUB1 | INV033 | Dagget 3_SUB1_INV033_Stop | Inverter | inverter033_stop | Stop | 65 | LatchOff/LatchOn | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Start | Inverter | inverter034_start | Start | 66 | LatchOff/LatchOn | Requested-Available
SUB1 | INV034 | Dagget 3_SUB1_INV034_Stop | Inverter | inverter034_stop | Stop | 67 | LatchOff/LatchOn | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Start | Inverter | inverter035_start | Start | 68 | LatchOff/LatchOn | Requested-Available
SUB1 | INV035 | Dagget 3_SUB1_INV035_Stop | Inverter | inverter035_stop | Stop | 69 | LatchOff/LatchOn | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Start | Inverter | inverter036_start | Start | 70 | LatchOff/LatchOn | Requested-Available
SUB1 | INV036 | Dagget 3_SUB1_INV036_Stop | Inverter | inverter036_stop | Stop | 71 | LatchOff/LatchOn | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Start | Inverter | inverter037_start | Start | 72 | LatchOff/LatchOn | Requested-Available
SUB1 | INV037 | Dagget 3_SUB1_INV037_Stop | Inverter | inverter037_stop | Stop | 73 | LatchOff/LatchOn | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Start | Inverter | inverter038_start | Start | 74 | LatchOff/LatchOn | Requested-Available
SUB1 | INV038 | Dagget 3_SUB1_INV038_Stop | Inverter | inverter038_stop | Stop | 75 | LatchOff/LatchOn | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Start | Inverter | inverter039_start | Start | 76 | LatchOff/LatchOn | Requested-Available
SUB1 | INV039 | Dagget 3_SUB1_INV039_Stop | Inverter | inverter039_stop | Stop | 77 | LatchOff/LatchOn | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Start | Inverter | inverter040_start | Start | 78 | LatchOff/LatchOn | Requested-Available
SUB1 | INV040 | Dagget 3_SUB1_INV040_Stop | Inverter | inverter040_stop | Stop | 79 | LatchOff/LatchOn | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Start | Inverter | inverter041_start | Start | 80 | LatchOff/LatchOn | Requested-Available
SUB1 | INV041 | Dagget 3_SUB1_INV041_Stop | Inverter | inverter041_stop | Stop | 81 | LatchOff/LatchOn | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Start | Inverter | inverter042_start | Start | 82 | LatchOff/LatchOn | Requested-Available
SUB1 | INV042 | Dagget 3_SUB1_INV042_Stop | Inverter | inverter042_stop | Stop | 83 | LatchOff/LatchOn | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Start | Inverter | inverter043_start | Start | 84 | LatchOff/LatchOn | Requested-Available
SUB1 | INV043 | Dagget 3_SUB1_INV043_Stop | Inverter | inverter043_stop | Stop | 85 | LatchOff/LatchOn | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Start | Inverter | inverter044_start | Start | 86 | LatchOff/LatchOn | Requested-Available
SUB1 | INV044 | Dagget 3_SUB1_INV044_Stop | Inverter | inverter044_stop | Stop | 87 | LatchOff/LatchOn | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Start | Inverter | inverter045_start | Start | 88 | LatchOff/LatchOn | Requested-Available
SUB1 | INV045 | Dagget 3_SUB1_INV045_Stop | Inverter | inverter045_stop | Stop | 89 | LatchOff/LatchOn | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Start | Inverter | inverter046_start | Start | 90 | LatchOff/LatchOn | Requested-Available
SUB1 | INV046 | Dagget 3_SUB1_INV046_Stop | Inverter | inverter046_stop | Stop | 91 | LatchOff/LatchOn | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Start | Inverter | inverter047_start | Start | 92 | LatchOff/LatchOn | Requested-Available
SUB1 | INV047 | Dagget 3_SUB1_INV047_Stop | Inverter | inverter047_stop | Stop | 93 | LatchOff/LatchOn | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Start | Inverter | inverter048_start | Start | 94 | LatchOff/LatchOn | Requested-Available
SUB1 | INV048 | Dagget 3_SUB1_INV048_Stop | Inverter | inverter048_stop | Stop | 95 | LatchOff/LatchOn | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Start | Inverter | inverter049_start | Start | 96 | LatchOff/LatchOn | Requested-Available
SUB1 | INV049 | Dagget 3_SUB1_INV049_Stop | Inverter | inverter049_stop | Stop | 97 | LatchOff/LatchOn | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Start | Inverter | Inverter050_start | Start | 98 | LatchOff/LatchOn | Requested-Available
SUB1 | INV050 | Dagget 3_SUB1_INV050_Stop | Inverter | Inverter050_stop | Stop | 99 | LatchOff/LatchOn | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Start | Inverter | Inverter051_start | Start | 100 | LatchOff/LatchOn | Requested-Available
SUB1 | INV051 | Dagget 3_SUB1_INV051_Stop | Inverter | Inverter051_stop | Stop | 101 | LatchOff/LatchOn | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Start | Inverter | Inverter052_start | Start | 102 | LatchOff/LatchOn | Requested-Available
SUB1 | INV052 | Dagget 3_SUB1_INV052_Stop | Inverter | Inverter052_stop | Stop | 103 | LatchOff/LatchOn | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Start | Inverter | Inverter053_start | Start | 104 | LatchOff/LatchOn | Requested-Available
SUB1 | INV053 | Dagget 3_SUB1_INV053_Stop | Inverter | Inverter053_stop | Stop | 105 | LatchOff/LatchOn | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Start | Inverter | Inverter054_start | Start | 106 | LatchOff/LatchOn | Requested-Available
SUB1 | INV054 | Dagget 3_SUB1_INV054_Stop | Inverter | Inverter054_stop | Stop | 107 | LatchOff/LatchOn | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Start | Inverter | Inverter055_start | Start | 108 | LatchOff/LatchOn | Requested-Available
SUB1 | INV055 | Dagget 3_SUB1_INV055_Stop | Inverter | Inverter055_stop | Stop | 109 | LatchOff/LatchOn | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Start | Inverter | Inverter056_start | Start | 110 | LatchOff/LatchOn | Requested-Available
SUB1 | INV056 | Dagget 3_SUB1_INV056_Stop | Inverter | Inverter056_stop | Stop | 111 | LatchOff/LatchOn | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Start | Inverter | Inverter057_start | Start | 112 | LatchOff/LatchOn | Requested-Available
SUB1 | INV057 | Dagget 3_SUB1_INV057_Stop | Inverter | Inverter057_stop | Stop | 113 | LatchOff/LatchOn | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Start | Inverter | Inverter058_start | Start | 114 | LatchOff/LatchOn | Requested-Available
SUB1 | INV058 | Dagget 3_SUB1_INV058_Stop | Inverter | Inverter058_stop | Stop | 115 | LatchOff/LatchOn | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Start | Inverter | Inverter059_start | Start | 116 | LatchOff/LatchOn | Requested-Available
SUB1 | INV059 | Dagget 3_SUB1_INV059_Stop | Inverter | Inverter059_stop | Stop | 117 | LatchOff/LatchOn | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Start | Inverter | Inverter060_start | Start | 118 | LatchOff/LatchOn | Requested-Available
SUB1 | INV060 | Dagget 3_SUB1_INV060_Stop | Inverter | Inverter060_stop | Stop | 119 | LatchOff/LatchOn | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Start | Inverter | Inverter061_start | Start | 120 | LatchOff/LatchOn | Requested-Available
SUB1 | INV061 | Dagget 3_SUB1_INV061_Stop | Inverter | Inverter061_stop | Stop | 121 | LatchOff/LatchOn | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Start | Inverter | Inverter062_start | Start | 122 | LatchOff/LatchOn | Requested-Available
SUB1 | INV062 | Dagget 3_SUB1_INV062_Stop | Inverter | Inverter062_stop | Stop | 123 | LatchOff/LatchOn | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Start | Inverter | Inverter063_start | Start | 124 | LatchOff/LatchOn | Requested-Available
SUB1 | INV063 | Dagget 3_SUB1_INV063_Stop | Inverter | Inverter063_stop | Stop | 125 | LatchOff/LatchOn | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Start | Inverter | Inverter064_start | Start | 126 | LatchOff/LatchOn | Requested-Available
SUB1 | INV064 | Dagget 3_SUB1_INV064_Stop | Inverter | Inverter064_stop | Stop | 127 | LatchOff/LatchOn | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Start | Inverter | Inverter065_start | Start | 128 | LatchOff/LatchOn | Requested-Available
SUB1 | INV065 | Dagget 3_SUB1_INV065_Stop | Inverter | Inverter065_stop | Stop | 129 | LatchOff/LatchOn | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Start | Inverter | Inverter066_start | Start | 130 | LatchOff/LatchOn | Requested-Available
SUB1 | INV066 | Dagget 3_SUB1_INV066_Stop | Inverter | Inverter066_stop | Stop | 131 | LatchOff/LatchOn | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Start | Inverter | Inverter067_start | Start | 132 | LatchOff/LatchOn | Requested-Available
SUB1 | INV067 | Dagget 3_SUB1_INV067_Stop | Inverter | Inverter067_stop | Stop | 133 | LatchOff/LatchOn | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Start | Inverter | Inverter068_start | Start | 134 | LatchOff/LatchOn | Requested-Available
SUB1 | INV068 | Dagget 3_SUB1_INV068_Stop | Inverter | Inverter068_stop | Stop | 135 | LatchOff/LatchOn | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Start | Inverter | Inverter069_start | Start | 136 | LatchOff/LatchOn | Requested-Available
SUB1 | INV069 | Dagget 3_SUB1_INV069_Stop | Inverter | Inverter069_stop | Stop | 137 | LatchOff/LatchOn | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Start | Inverter | inverter070_start | Start | 138 | LatchOff/LatchOn | Requested-Available
SUB1 | INV070 | Dagget 3_SUB1_INV070_Stop | Inverter | inverter070_stop | Stop | 139 | LatchOff/LatchOn | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Start | Inverter | inverter071_start | Start | 140 | LatchOff/LatchOn | Requested-Available
SUB1 | INV071 | Dagget 3_SUB1_INV071_Stop | Inverter | inverter071_stop | Stop | 141 | LatchOff/LatchOn | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Start | Inverter | inverter072_start | Start | 142 | LatchOff/LatchOn | Requested-Available
SUB1 | INV072 | Dagget 3_SUB1_INV072_Stop | Inverter | inverter072_stop | Stop | 143 | LatchOff/LatchOn | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Start | Inverter | inverter073_start | Start | 144 | LatchOff/LatchOn | Requested-Available
SUB1 | INV073 | Dagget 3_SUB1_INV073_Stop | Inverter | inverter073_stop | Stop | 145 | LatchOff/LatchOn | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Start | Inverter | inverter074_start | Start | 146 | LatchOff/LatchOn | Requested-Available
SUB1 | INV074 | Dagget 3_SUB1_INV074_Stop | Inverter | inverter074_stop | Stop | 147 | LatchOff/LatchOn | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Start | Inverter | inverter075_start | Start | 148 | LatchOff/LatchOn | Requested-Available
SUB1 | INV075 | Dagget 3_SUB1_INV075_Stop | Inverter | inverter075_stop | Stop | 149 | LatchOff/LatchOn | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Start | Inverter | inverter076_start | Start | 150 | LatchOff/LatchOn | Requested-Available
SUB1 | INV076 | Dagget 3_SUB1_INV076_Stop | Inverter | inverter076_stop | Stop | 151 | LatchOff/LatchOn | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Start | Inverter | inverter077_start | Start | 152 | LatchOff/LatchOn | Requested-Available
SUB1 | INV077 | Dagget 3_SUB1_INV077_Stop | Inverter | inverter077_stop | Stop | 153 | LatchOff/LatchOn | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Start | Inverter | inverter078_start | Start | 154 | LatchOff/LatchOn | Requested-Available
SUB1 | INV078 | Dagget 3_SUB1_INV078_Stop | Inverter | inverter078_stop | Stop | 155 | LatchOff/LatchOn | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Start | Inverter | inverter079_start | Start | 156 | LatchOff/LatchOn | Requested-Available
SUB1 | INV079 | Dagget 3_SUB1_INV079_Stop | Inverter | inverter079_stop | Stop | 157 | LatchOff/LatchOn | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Start | Inverter | inverter080_start | Start | 158 | LatchOff/LatchOn | Requested-Available
SUB1 | INV080 | Dagget 3_SUB1_INV080_Stop | Inverter | inverter080_stop | Stop | 159 | LatchOff/LatchOn | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Start | Inverter | inverter081_start | Start | 160 | LatchOff/LatchOn | Requested-Available
SUB1 | INV081 | Dagget 3_SUB1_INV081_Stop | Inverter | inverter081_stop | Stop | 161 | LatchOff/LatchOn | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Start | Inverter | inverter082_start | Start | 162 | LatchOff/LatchOn | Requested-Available
SUB1 | INV082 | Dagget 3_SUB1_INV082_Stop | Inverter | inverter082_stop | Stop | 163 | LatchOff/LatchOn | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Start | Inverter | inverter083_start | Start | 164 | LatchOff/LatchOn | Requested-Available
SUB1 | INV083 | Dagget 3_SUB1_INV083_Stop | Inverter | inverter083_stop | Stop | 165 | LatchOff/LatchOn | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Start | Inverter | inverter084_start | Start | 166 | LatchOff/LatchOn | Requested-Available
SUB1 | INV084 | Dagget 3_SUB1_INV084_Stop | Inverter | inverter084_stop | Stop | 167 | LatchOff/LatchOn | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Start | Inverter | inverter085_start | Start | 168 | LatchOff/LatchOn | Requested-Available
SUB1 | INV085 | Dagget 3_SUB1_INV085_Stop | Inverter | inverter085_stop | Stop | 169 | LatchOff/LatchOn | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Start | Inverter | inverter086_start | Start | 170 | LatchOff/LatchOn | Requested-Available
SUB1 | INV086 | Dagget 3_SUB1_INV086_Stop | Inverter | inverter086_stop | Stop | 171 | LatchOff/LatchOn | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Start | Inverter | inverter087_start | Start | 172 | LatchOff/LatchOn | Requested-Available
SUB1 | INV087 | Dagget 3_SUB1_INV087_Stop | Inverter | inverter087_stop | Stop | 173 | LatchOff/LatchOn | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Start | Inverter | inverter088_start | Start | 174 | LatchOff/LatchOn | Requested-Available
SUB1 | INV088 | Dagget 3_SUB1_INV088_Stop | Inverter | inverter088_stop | Stop | 175 | LatchOff/LatchOn | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Start | Inverter | inverter089_start | Start | 176 | LatchOff/LatchOn | Requested-Available
SUB1 | INV089 | Dagget 3_SUB1_INV089_Stop | Inverter | inverter089_stop | Stop | 177 | LatchOff/LatchOn | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Start | Inverter | inverter090_start | Start | 178 | LatchOff/LatchOn | Requested-Available
SUB1 | INV090 | Dagget 3_SUB1_INV090_Stop | Inverter | inverter090_stop | Stop | 179 | LatchOff/LatchOn | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Start | Inverter | inverter091_start | Start | 180 | LatchOff/LatchOn | Requested-Available
SUB1 | INV091 | Dagget 3_SUB1_INV091_Stop | Inverter | inverter091_stop | Stop | 181 | LatchOff/LatchOn | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Start | Inverter | inverter092_start | Start | 182 | LatchOff/LatchOn | Requested-Available
SUB1 | INV092 | Dagget 3_SUB1_INV092_Stop | Inverter | inverter092_stop | Stop | 183 | LatchOff/LatchOn | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Start | Inverter | inverter093_start | Start | 184 | LatchOff/LatchOn | Requested-Available
SUB1 | INV093 | Dagget 3_SUB1_INV093_Stop | Inverter | inverter093_stop | Stop | 185 | LatchOff/LatchOn | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Start | Inverter | inverter094_start | Start | 186 | LatchOff/LatchOn | Requested-Available
SUB1 | INV094 | Dagget 3_SUB1_INV094_Stop | Inverter | inverter094_stop | Stop | 187 | LatchOff/LatchOn | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Start | Inverter | inverter095_start | Start | 188 | LatchOff/LatchOn | Requested-Available
SUB1 | INV095 | Dagget 3_SUB1_INV095_Stop | Inverter | inverter095_stop | Stop | 189 | LatchOff/LatchOn | Requested-Available