## test
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | IP Address |  | DNP Server | IP_Address
DNP Server Port# | 20001, (20002 if more than 1 port is needed) |  | DNP Server Port# | 20010_(PROD);_20011_(QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 1 |  | RTAC DNP Server address | 1
| Data Type | DNP Event Class | Event Obj/Var | Static_Obj_Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30_5
Digitals | Status with Flags | 1 | 2/2 | 1_2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20_1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each Of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband Of 0.01 for all points except 0.001 for Frequency and Power Factor | [5 empty] | n/a
Substation | DeviceID | Point Name | Device Type | Native_RTAC_Point_Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX
SUB1 | SEL-487v | TSN1_SUB1_SEL-735-MTRL1 HS_MVAR Contribution | Reactive Power Relay | GMS_MAP_DNP.SEL_735_MTRL1_MVAR Contribution | AC Real Power | 0 | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Reactive Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Reactive_Power | AC Reactive Power | 3 | MVAR | Requested-Not Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Power Factor | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Power_Factor | Power Factor | 2 | N/A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage A-B | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_A_B | Phase-Phase Voltages | 3 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage B-C | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_B_C | Phase-Phase Voltages | 4 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage C-A | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_C_A | Phase-Phase Voltages | 5 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Current | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_A_Phase_Current | Phase Currents | 6 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Current | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_B_Phase_Current | Phase Currents | 7 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Current | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_C_Phase_Current | Phase Currents | 8 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Frequency | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Frequency | Frequency | 9 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Current THD A | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD IA | Phase Total Harmonic Current Distortion | 10 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Current THD B | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD IB | Phase Total Harmonic Current Distortion | 11 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Current THD C | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD IC | Phase Total Harmonic Current Distortion | 12 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage THD A | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD VA | Phase Total Harmonic Voltage Distortion | 13 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage THD B | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD VB | Phase Total Harmonic Voltage Distortion | 14 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage THD C | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_THD VC | Phase Total Harmonic Voltage Distortion | 15 | % | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_A_Phase_Power | Phase Power | 16 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_B_Phase_Power | Phase Power | 17 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_C_Phase_Power | Phase Power | 18 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage A-N | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_A_N | L-N Phase Voltages | 19 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage B-N | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_B_N | L-N Phase Voltages | 20 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Voltage C-N | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_Voltage_C_N | L-N Phase Voltages | 21 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Apparent Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_A_Phase_Apparent_Power | Phase Apparent Power | 22 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Apparent Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_B_Phase_Apparent_Power | Phase Apparent Power | 23 | MVA | Requested-Available |  | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Apparent Power | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_C_Phase_Apparent_Power | Phase Apparent Power | 24 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Power Factor | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_A_Phase_Power_Factor | Phase Power Factor | 25 | N/A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Power Factor | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_B_Phase_Power_Factor | Phase Power Factor | 26 | N/A | Requested-Available | -32767 | 32767
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Power Factor | Meter | GMS_MAP_DNP.SEL_735_MTRL1_HS_C_Phase_Power_Factor | Phase Power Factor |  | N/A | Requested-Availables | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Real Power-AC | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Real Power AC | AC Real Power | 27 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_AC Reactive Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_AC Reactive Power | AC Reactive Power | 28 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Power Factor | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Power Factor | Power Factor | 29 | Unitless | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage A-B | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage A-B | Phase-Phase Voltages | 30 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage B-C | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage B-C | Phase-Phase Voltages | 31 | kV | Requested-Available | -32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage C-A | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage C-A | Phase-Phase Voltages | 32 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_A Phase Current | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_A_Phase_Current | Phase Currents | 33 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_B Phase Current | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_B_Phase_Current | Phase Currents | 34 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_C Phase Current | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_C_Phase_Current | Phase Currents | 35 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Frequency | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Frequency | Frequency | 36 | Hz | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_A Phase Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_A_Phase_Power | Phase Power | 37 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_B Phase Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_B_Phase_Power | Phase Power | 38 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_C Phase Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_C_Phase_Power | Phase Power | 39 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage A-N | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage_A-N | L-N Phase Voltages | 40 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage B-N | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage_B-N | L-N Phase Voltages | 41 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Voltage C-N | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Voltage_C-N | L-N Phase Voltages | 42 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_A Phase Apparent Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_SA_MVA | Phase Apparent Power | 43 | MVA | Requested-Available | apple | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_B Phase Apparent Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_SB_MVA | Phase Apparent Power | 44 | MVA | Requested-Available | -32767 | orange
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_C Phase Apparent Power | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_SC_MVA | Phase Apparent Power | 45 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_A Phase Power Factor | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_A_Phase_Power_Factor | Phase Power Factor | 46 | Unitless | Requested-Available | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_B Phase Power Factor | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_B_Phase_Power_Factor | Phase Power Factor |  | Unitless | Blah | -32767 | 32767
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_C Phase Power Factor | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_C_Phase_Power_Factor | Phase Power Factor | 47 | Unitless | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Real Power-AC | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Real_Power-AC | AC Real Power | 48 | MW | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_AC Reactive Power | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_AC_Reactive_Power | AC Reactive Power | 49 | MVAR | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Power Factor | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Power_Factor | Power Factor | 50 | Unitless | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage A-B | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage_A-B | Phase-Phase Voltages | 51 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage B-C | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage B-C | Phase-Phase Voltages | 52 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage C-A | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage C-A | Phase-Phase Voltages | 53 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_A Phase Current | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_A Phase Current | Phase Currents | 54 | A | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_B Phase Current | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_B Phase Current | Phase Currents | 55 | A | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_C Phase Current | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_C Phase Current | Phase Currents | 56 | A | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Frequency | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Frequency | Frequency | 57 | Hz | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_A Phase Power | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_A Phase Power | Phase Power | 58 | MW | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_B Phase Power | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_B Phase Power | Phase Power | 59 | MW | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_C Phase Power | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_C Phase Power | Phase Power | 60 | MW | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage A-N | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage A-N | L-N Phase Voltages | 61 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage B-N | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage B-N | L-N Phase Voltages | 62 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Voltage C-N | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_Voltage C-N | L-N Phase Voltages | 63 | kV | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_A Phase Apparent Power | Line Relay |  | Phase Apparent Power | 5 | MVA | Requested-Not Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_B Phase Apparent Power | Line Relay |  | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_C Phase Apparent Power | Line Relay |  | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_A Phase Power Factor | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_A Phase Power Factor | Phase Power Factor | 65 | Unitless | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_B Phase Power Factor | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_B Phase Power Factor | Phase Power Factor | 66 | Unitless | Requested-Available | -32767 | 32767
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_C Phase Power Factor | Line Relay | GMS_MAP_DNP.GE_L90_87L1S_C Phase Power Factor | Phase Power Factor | 67 | Unitless | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Real Power-AC | AC Real Power | 68 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Reactive Power | AC Reactive Power | 69 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage A-B | Phase-Phase Voltages | 70 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage B-C | Phase-Phase Voltages | 71 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage C-A | Phase-Phase Voltages | 72 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A Phase Current | Phase Currents | 73 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B Phase Current | Phase Currents | 74 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C Phase Current | Phase Currents | 75 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Frequency | Frequency | 76 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A Phase Power | Phase Power | 77 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B Phase Power | Phase Power | 78 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C Phase Power | Phase Power | 79 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage A-N | L-N Phase Voltages | 80 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage B-N | L-N Phase Voltages | 81 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Voltage C-N | L-N Phase Voltages | 82 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A Phase Apparent Power | Phase Apparent Power | 83 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B Phase Apparent Power | Phase Apparent Power | 84 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C Phase Apparent Power | Phase Apparent Power | 85 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C Phase Power Factor | Phase Power Factor | 33 | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_VBAT | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_VBAT | Station Battery Voltage | 87 | V | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Real Power-AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Real Power-AC | AC Real Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Reactive Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Reactive Power | AC Reactive Power |  | MVAR | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage A-B | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage A-B | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage B-C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage B-C | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage C-A | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage C-A | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A Phase Current HV | Phase Currents | 88 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B Phase Current HV | Phase Currents | 89 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C Phase Current HV | Phase Currents | 90 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A Phase Current MV | Phase Currents | 91 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1p | TSN1_SUB1_SEL-387A-T1P_B Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B Phase Current MV | Phase Currents | 92 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C Phase Current MV | Phase Currents | 93 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Frequency | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Frequency | Frequency |  | Hz | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage A-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage A-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage B-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage B-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Voltage C-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Voltage C-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B Phase Power Factor | Phase Power Factor | 78 | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Ground Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Ground Current HV | Phase Currents | 95 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Ground Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Ground Current MV | Phase Currents | 96 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Real Power-AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Real Power-AC | AC Real Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Reactive Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Reactive Power | AC Reactive Power |  | MVAR | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage A-B | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage A-B | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage B-C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage B-C | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage C-A | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage C-A | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A Phase Current HV | Phase Currents | 97 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B Phase Current HV | Phase Currents | 98 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C Phase Current HV | Phase Currents | 99 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A Phase Current MV | Phase Currents | 100 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B Phase Current MV | Phase Currents | 101 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C Phase Current MV | Phase Currents | 102 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Frequency | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Frequency | Frequency |  | Hz | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage A-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage A-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage B-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage B-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Voltage C-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Voltage C-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Ground Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Ground Current HV | Phase Currents | 103 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Ground Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Ground Current MV | Phase Currents | 104 | A | Not Requested-Available | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Hydran Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_Hydran_Hydran Level | T2 HYDRAN Hydran Level | 105 | PPM | Not Requested-Available | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_RH Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_Hydran_RH_Level | T2 HYDRAN Relative Humidity Level | 106 | % | Not Requested-Available | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Temperature_Oil | Oil Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Temperature_Winding | Winding Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Pressure | Pressure |  | hPa | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Oil_Level | Oil Level |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_ Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Tap Position | Transformer Tap Position |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Available | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Temperature_Oil | Oil Temperature | 107 | °C | Requested-Available | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Temperature_Winding | Winding Temperature | 108 | °C | Requested-Available | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Pressure | Pressure |  | hPa | Requested-Not Available | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Oil_Level | Oil Level |  | % | Requested-Not Available | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Tap_Position | Transformer Tap Position |  | Tap Number | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Temperature Ambient | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Temperature_Ambient | Ambient Temperature | 109 | °C | Not Requested-Available | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Temperature_Oil | Oil Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Temperature_Winding | Winding Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Pressure | Pressure |  | hPa | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Oil_Level | Oil Level |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Tap_Position | Transformer Tap Position | 110 | Tap Number | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Real Power-AC | AC Real Power | 111 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Reactive Power | AC Reactive Power | 112 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage A-B | Phase-Phase Voltages | 113 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage B-C | Phase-Phase Voltages | 114 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage C-A | Phase-Phase Voltages | 115 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A Phase Current | Phase Currents | 116 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B Phase Current | Phase Currents | 117 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C Phase Current | Phase Currents | 118 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Frequency | Frequency | 119 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A Phase Power | Phase Power | 120 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B Phase Power | Phase Power | 121 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C Phase Power | Phase Power | 122 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage A-N | L-N Phase Voltages | 123 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage B-N | L-N Phase Voltages | 124 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Voltage C-N | L-N Phase Voltages | 125 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A Phase Apparent Power | Phase Apparent Power | 126 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B Phase Apparent Power | Phase Apparent Power | 127 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C Phase Apparent Power | Phase Apparent Power | 128 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_A Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_A Phase Current | Communication Status | 129 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_B Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_B Phase Current | Communication Status | 130 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_C Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_C Phase Current | Communication Status | 131 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Real Power-AC | AC Real Power | 132 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Reactive Power | AC Reactive Power | 133 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage A-B | Phase-Phase Voltages | 134 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage B-C | Phase-Phase Voltages | 135 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage C-A | Phase-Phase Voltages | 136 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A Phase Current | Phase Currents | 137 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B Phase Current | Phase Currents | 138 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C Phase Current | Phase Currents | 139 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_#Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Frequency | Candle | 140 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A Phase Power | Phase Power | 141 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B Phase Power | Phase Power | 142 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C Phase Power | Phase Power | 143 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage A-N | L-N Phase Voltages | 144 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage B-N | L-N Phase Voltages | 145 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Voltage C-N | L-N Phase Voltages | 146 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A Phase Apparent Power | Phase Apparent Power | 147 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B Phase Apparent Power | Phase Apparent Power | 148 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C Phase Apparent Power | Phase Apparent Power | 149 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Real Power-AC | AC Real Power | 150 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Reactive Power | AC Reactive Power | 151 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage A-B | Phase-Phase Voltages | 152 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage B-C | Phase-Phase Voltages | 153 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage C-A | Phase-Phase Voltages | 154 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A Phase Current | Phase Currents | 155 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B Phase Current | Phase Currents | 156 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C Phase Current | Phase Currents | 157 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Frequency | Frequency | 158 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A Phase Power | Phase Power | 159 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B Phase Power | Phase Power | 160 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C Phase Power | Phase Power | 161 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage A-N | L-N Phase Voltages | 162 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage B-N | L-N Phase Voltages | 163 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Voltage C-N | L-N Phase Voltages | 164 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A Phase Apparent Power | Phase Apparent Power | 165 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B Phase Apparent Power | Phase Apparent Power | 166 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C Phase Apparent Power | Phase Apparent Power | 167 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Real Power-AC | AC Real Power | 168 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Reactive Power | AC Reactive Power | 169 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage A-B | Phase-Phase Voltages | 170 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage B-C | Phase-Phase Voltages | 171 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage C-A | Phase-Phase Voltages | 172 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A Phase Current | Phase Currents | 173 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B Phase Current | Phase Currents | 174 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C Phase Current | Phase Currents | 175 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Frequency | Frequency | 176 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A Phase Power | Phase Power | 177 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B Phase Power | Phase Power | 178 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C Phase Power | Phase Power | 179 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage A-N | L-N Phase Voltages | 180 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage B-N | L-N Phase Voltages | 181 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Voltage C-N | L-N Phase Voltages | 182 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A Phase Apparent Power | Phase Apparent Power | 183 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B Phase Apparent Power | Phase Apparent Power | 184 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C Phase Apparent Power | Phase Apparent Power | 185 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Real Power-AC | AC Real Power | 186 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Reactive Power | AC Reactive Power | 187 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage A-B | Phase-Phase Voltages | 188 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage B-C | Phase-Phase Voltages | 189 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage C-A | Phase-Phase Voltages | 190 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_A Phase Current | Phase Currents | 191 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_B Phase Current | Phase Currents | 192 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_C Phase Current | Phase Currents | 193 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Frequency | Frequency | 194 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_A Phase Power | Phase Power | 195 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_B Phase Power | Phase Power | 196 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_C Phase Power | Phase Power | 197 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage A-N | L-N Phase Voltages | 198 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage B-N | L-N Phase Voltages | 199 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_Voltage C-N | L-N Phase Voltages | 200 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_A Phase Apparent Power | Phase Apparent Power | 201 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_B Phase Apparent Power | Phase Apparent Power | 202 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_C Phase Apparent Power | Phase Apparent Power | 203 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V1_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Real Power-AC | AC Real Power | 204 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Reactive Power | AC Reactive Power | 205 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage A-B | Phase-Phase Voltages | 206 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage B-C | Phase-Phase Voltages | 207 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage C-A | Phase-Phase Voltages | 208 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A Phase Current | Phase Currents | 209 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B Phase Current | Phase Currents | 210 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C Phase Current | Phase Currents | 211 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Frequency | Frequency | 212 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A Phase Power | Phase Power | 213 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B Phase Power | Phase Power | 214 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C Phase Power | Phase Power | 215 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage A-N | L-N Phase Voltages | 216 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage B-N | L-N Phase Voltages | 217 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Voltage C-N | L-N Phase Voltages | 218 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A Phase Apparent Power | Phase Apparent Power | 219 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B Phase Apparent Power | Phase Apparent Power | 220 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C Phase Apparent Power | Phase Apparent Power | 221 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_VBat | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_VBAT | Station Battery Voltage | 222 | V | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Real Power-AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Real Power-AC | AC Real Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Reactive Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Reactive Power | AC Reactive Power |  | MVAR | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage A-B | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage A-B | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage B-C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage B-C | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage C-A | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage C-A | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A Phase Current HV | Phase Currents | 223 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B Phase Current HV | Phase Currents | 224 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C Phase Current HV | Phase Currents | 225 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A Phase Current MV | Phase Currents | 226 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B Phase Current MV | Phase Currents | 227 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C Phase Current MV | Phase Currents | 228 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Frequency | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Frequency | Frequency |  | Hz | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage A-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage A-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage B-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage B-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Voltage C-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Voltage C-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Ground Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Ground Current HV | Phase Currents | 229 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Ground Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Ground Current MV | Phase Currents | 230 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Real Power-AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Real Power-AC | AC Real Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Reactive Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Reactive Power | AC Reactive Power |  | MVAR | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage A-B | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage A-B | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage B-C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage B-C | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage C-A | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage C-A | Phase-Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A Phase Current HV | Phase Currents | 231 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B Phase Current HV | Phase Currents | 232 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C Phase Current HV | Phase Currents | 233 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A Phase Current MV | Phase Currents | 234 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B Phase Current MV | Phase Currents | 235 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C Phase Current MV | Phase Currents | 236 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Frequency | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Frequency | Frequency |  | Hz | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C Phase Power | Phase Power |  | MW | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage A-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage A-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage B-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage B-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Voltage C-N | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Voltage C-N | L-N Phase Voltages |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Apparent Power | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C Phase Apparent Power | Phase Apparent Power |  | MVA | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Power Factor | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Ground Current HV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Ground Current HV | Phase Currents | 237 | A | Not Requested-Available | -32767 | 32767
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Ground Current MV | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Ground Current MV | Phase Currents | 238 | A | Not Requested-Available | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Hydran Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_Hydran_Hydran Level | T2 HYDRAN Hydran Level | 239 | PPM | Not Requested-Available | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_RH Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_Hydran_RH_Level | T2 HYDRAN Relative Humidity Level | 240 | % | Not Requested-Available | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Temperature_Oil | Oil Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Temperature_Winding | Winding Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Pressure | Pressure |  | hPa | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Oil_Level | Oil Level |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Available | -32767 | 32767
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_ Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Tap Position | Transformer Tap Position |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Temperature_Oil | Oil Temperature | 241 | °C | Requested-Available | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Temperature_Winding | Winding Temperature | 242 | °C | Requested-Available | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Pressure | Pressure |  | hPa | Requested-Not Available | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Oil_Level | Oil Level |  | % | Requested-Not Available | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Tap_Position | Transformer Tap Position |  | Tap Number | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Temperature Ambient | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Temperature_Ambient | Ambient Temperature | 243 | °C | Not Requested-Available | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_ Fan Stage | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Fan_Stage | Stage fan status |  | 0,1,2 | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_ Temperature Oil | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Temperature_Oil | Oil Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_ Temperature Winding | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Temperature_Winding | Winding Temperature |  | °C | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_ Pressure | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Pressure | Pressure |  | hPa | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_ Oil Level | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Oil_Level | Oil Level |  | % | Requested-Not Applicable | -32767 | 32767
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Tap Position | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Tap_Position | Transformer Tap Position | 244 | Tap Number | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Real Power-AC | AC Real Power | 245 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Reactive Power | AC Reactive Power | 246 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage A-B | Phase-Phase Voltages | 247 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage B-C | Phase-Phase Voltages | 248 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage C-A | Phase-Phase Voltages | 249 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A Phase Current | Phase Currents | 250 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B Phase Current | Phase Currents | 251 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C Phase Current | Phase Currents | 252 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Frequency | Frequency | 253 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A Phase Power | Phase Power | 254 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B Phase Power | Phase Power | 255 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C Phase Power | Phase Power | 256 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage A-N | L-N Phase Voltages | 257 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage B-N | L-N Phase Voltages | 258 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Voltage C-N | L-N Phase Voltages | 259 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A Phase Apparent Power | Phase Apparent Power | 260 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B Phase Apparent Power | Phase Apparent Power | 261 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C Phase Apparent Power | Phase Apparent Power | 262 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_A Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_A Phase Current | Communication Status | 263 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_B Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_B Phase Current | Communication Status | 264 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_C Phase Current | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_C Phase Current | Communication Status | 265 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Real Power-AC | AC Real Power | 266 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Reactive Power | AC Reactive Power | 267 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage A-B | Phase-Phase Voltages | 268 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage B-C | Phase-Phase Voltages | 269 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage C-A | Phase-Phase Voltages | 270 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A Phase Current | Phase Currents | 271 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B Phase Current | Phase Currents | 272 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C Phase Current | Phase Currents | 273 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Frequency | Frequency | 274 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A Phase Power | Phase Power | 275 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B Phase Power | Phase Power | 276 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C Phase Power | Phase Power | 277 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage A-N | L-N Phase Voltages | 278 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage B-N | L-N Phase Voltages | 279 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Voltage C-N | L-N Phase Voltages | 280 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A Phase Apparent Power | Phase Apparent Power | 281 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B Phase Apparent Power | Phase Apparent Power | 282 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C Phase Apparent Power | Phase Apparent Power | 283 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Real Power-AC | AC Real Power | 284 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Reactive Power | AC Reactive Power | 285 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage A-B | Phase-Phase Voltages | 286 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage B-C | Phase-Phase Voltages | 287 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage C-A | Phase-Phase Voltages | 288 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A Phase Current | Phase Currents | 289 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B Phase Current | Phase Currents | 290 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C Phase Current | Phase Currents | 291 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Frequency | Frequency | 292 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A Phase Power | Phase Power | 293 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B Phase Power | Phase Power | 294 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C Phase Power | Phase Power | 295 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage A-N | L-N Phase Voltages | 296 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage B-N | L-N Phase Voltages | 297 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Voltage C-N | L-N Phase Voltages | 298 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A Phase Apparent Power | Phase Apparent Power | 299 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B Phase Apparent Power | Phase Apparent Power | 300 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C Phase Apparent Power | Phase Apparent Power | 301 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Real Power-AC | AC Real Power | 302 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Reactive Power | AC Reactive Power | 303 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage A-B | Phase-Phase Voltages | 304 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage B-C | Phase-Phase Voltages | 305 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage C-A | Phase-Phase Voltages | 306 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A Phase Current | Phase Currents | 307 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B Phase Current | Phase Currents | 308 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C Phase Current | Phase Currents | 309 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Frequency | Frequency | 310 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A Phase Power | Phase Power | 311 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B Phase Power | Phase Power | 312 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C Phase Power | Phase Power | 313 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage A-N | L-N Phase Voltages | 314 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage B-N | L-N Phase Voltages | 315 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Voltage C-N | L-N Phase Voltages | 316 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A Phase Apparent Power | Phase Apparent Power | 317 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B Phase Apparent Power | Phase Apparent Power | 318 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C Phase Apparent Power | Phase Apparent Power | 319 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Real Power-AC | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Real Power-AC | AC Real Power | 320 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Reactive Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Reactive Power | AC Reactive Power | 321 | MVAR | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Power Factor | Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage A-B | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage A-B | Phase-Phase Voltages | 322 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage B-C | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage B-C | Phase-Phase Voltages | 323 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage C-A | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage C-A | Phase-Phase Voltages | 324 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_A Phase Current | Phase Currents | 325 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_B Phase Current | Phase Currents | 326 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Current | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_C Phase Current | Phase Currents | 327 | A | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Frequency | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Frequency | Frequency | 328 | Hz | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_A Phase Power | Phase Power | 329 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_B Phase Power | Phase Power | 330 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_C Phase Power | Phase Power | 331 | MW | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage A-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage A-N | L-N Phase Voltages | 332 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage B-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage B-N | L-N Phase Voltages | 333 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Voltage C-N | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_Voltage C-N | L-N Phase Voltages | 334 | kV | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_A Phase Apparent Power | Phase Apparent Power | 335 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_B Phase Apparent Power | Phase Apparent Power | 336 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Apparent Power | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_C Phase Apparent Power | Phase Apparent Power | 337 | MVA | Requested-Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_A Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_B Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Power Factor | Breaker Relay | GMS_MAP_DNP.SEL_487V_11V2_C Phase Power Factor | Phase Power Factor |  | Unitless | Requested-Not Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Gen Gross MW | ERCOT | GMS_MAP_DNP.ERCOT_T1_Gross_MW | ERCOT Transformer T1 - Gen Gross Megawatts | 338 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Gen Gross MVAR | ERCOT | GMS_MAP_DNP._ERCOT_T1_Gross_MVAR | ERCOT Transformer T1 - Gen Gross Megavars | 339 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Load MW | ERCOT | GMS_MAP_DNP.ERCOT_T1_Load_MW | ERCOT Transformer T1 - Load Megawatts | 340 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Load MVAR | ERCOT | GMS_MAP_DNP.ERCOT_T1_Load_MVAR | ERCOT Transformer T1 - Load Megavars | 341 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Gen Net MW | ERCOT | GMS_MAP_DNP.ERCOT_T1_Net_MW | ERCOT Transformer T1 - Gen Net Megawatts | 342 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 - Gen Net MVAR | ERCOT | GMS_MAP_DNP.ERCOT_T1_Net_MVAR | ERCOT Transformer T1 - Gen Net Megavars | 343 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 High Side Real Power | ERCOT | GMS_MAP_DNP.ERCOT_T1_HS_MW | ERCOT T1 High Side Real Power | 344 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 High Side Reactive Power | ERCOT | GMS_MAP_DNP.ERCOT_T1_HS_MVAR | ERCOT T1 High Side Reactive Power | 345 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 High Side Voltage VAB | ERCOT | GMS_MAP_DNP.ERCOT_T1_HS_KVAB | ERCOT T1 High Side Voltage VAB | 346 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 High Side Voltage VBC | ERCOT | GMS_MAP_DNP.ERCOT_T1_HS_KVBC | ERCOT T1 High Side Voltage VBC | 347 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 High Side Voltage VCA | ERCOT | GMS_MAP_DNP.ERCOT_T1_HS_KVCA | ERCOT T1 High Side Voltage VCA | 348 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 Low Side Voltage VAB | ERCOT | GMS_MAP_DNP.ERCOT_T1_LS_KVAB | ERCOT T1 Low Side Voltage VAB | 349 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 Low Side Voltage VBC | ERCOT | GMS_MAP_DNP.ERCOT_T1_LS_KVBC | ERCOT T1 Low Side Voltage VBC | 350 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T1 Low Side Voltage VCA | ERCOT | GMS_MAP_DNP.ERCOT_T1_LS_KVCA | ERCOT T1 Low Side Voltage VCA | 351 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Gen Gross MW | ERCOT | GMS_MAP_DNP.ERCOT_T2_Gross_MW | ERCOT Transformer T2 - Gen Gross Megawatts | 352 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Gen Gross MVAR | ERCOT | GMS_MAP_DNP.ERCOT_T2_Gross_MVAR | ERCOT Transformer T2 - Gen Gross Megavars | 353 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Load MW | ERCOT | GMS_MAP_DNP.ERCOT_T2_Load_MW | ERCOT Transformer T2 - Load Megawatts | 354 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Load MVAR | ERCOT | GMS_MAP_DNP.ERCOT_T2_Load_MVAR | ERCOT Transformer T2 - Load Megavars | 355 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Gen Net MW | ERCOT | GMS_MAP_DNP.ERCOT_T2_Net_MW | ERCOT Transformer T2 - Gen Net Megawatts | 356 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 - Gen Net MVAR | ERCOT | GMS_MAP_DNP.ERCOT_T2_Net_MVAR | ERCOT Transformer T2 - Gen Net Megavars | 357 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 High Side Real Power | ERCOT | GMS_MAP_DNP.ERCOT_T2_HS_MW | ERCOT T2 High Side Real Power | 358 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 High Side Reactive Power | ERCOT | GMS_MAP_DNP.ERCOT_T2_HS_MVAR | ERCOT T2 High Side Reactive Power | 359 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 High Side Voltage VAB | ERCOT | GMS_MAP_DNP.ERCOT_T2_HS_KVAB | ERCOT T2 High Side Voltage VAB | 360 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 High Side Voltage VBC | ERCOT | GMS_MAP_DNP.ERCOT_T2_HS_KVBC | ERCOT T2 High Side Voltage VBC | 361 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 High Side Voltage VCA | ERCOT | GMS_MAP_DNP.ERCOT_T2_HS_KVCA | ERCOT T2 High Side Voltage VCA | 362 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 Low Side Voltage VAB | ERCOT | GMS_MAP_DNP.ERCOT_T2_LS_KVAB | ERCOT T2 Low Side Voltage VAB | 363 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 Low Side Voltage VBC | ERCOT | GMS_MAP_DNP.ERCOT_T2_LS_KVBC | ERCOT T2 Low Side Voltage VBC | 364 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT T2 Low Side Voltage VCA | ERCOT | GMS_MAP_DNP.ERCOT_T2_LS_KVCA | ERCOT T2 Low Side Voltage VCA | 365 | kV | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Line MW | ERCOT | GMS_MAP_DNP.ERCOT_LINE_MW | ERCOT Line Megawatts | 366 | MW | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Line MVAR | ERCOT | GMS_MAP_DNP.ERCOT_LINE_MVAR | ERCOT Line Megavars | 367 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Capacitor Bank C11 MVAR | ERCOT | GMS_MAP_DNP.ERCOT_CAP_C11_MVAR | ERCOT Capacitor Bank C11 MVAR | 368 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Capacitor Bank C12 MVAR | ERCOT | GMS_MAP_DNP.ERCOT_CAP_C12_MVAR | ERCOT Capacitor Bank C12 MVAR | 369 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Capacitor Bank C21 MVAR | ERCOT | GMS_MAP_DNP.ERCOT_CAP_C21_MVAR | ERCOT Capacitor Bank C21 MVAR | 370 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Capacitor Bank C22 MVAR | ERCOT | GMS_MAP_DNP.ERCOT_CAP_C22_MVAR | ERCOT Capacitor Bank C22 MVAR | 371 | MVAR | Not Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 1 MW Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_Unit_1_MW_Setpoint_Feedback | GMS MW Setpoint Feedback | 372 | MW | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 2 MW Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_Unit_1_MW_Setpoint_Feedback | GMS MW Setpoint Feedback | 373 | MW | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS POI VAR Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_POI_VAR_Setpoint_Feedback | GMS POI VAR Setpoint Feedback | 374 | MVAR | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS POI PF Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_POI_PF_Setpoint_Feedback | GMS POI PF Setpoint Feedback | 375 | positive is lagging, negative is leading | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS POI Voltage Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_POI_Voltage_Setpoint_Feedback | GMS POI Voltage Setpoint Feedback | 376 | KV | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Up Rate Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Up_Rate_Setpoint_Feedback | GMS Ramp Up Rate Setpoint Feedback | 377 | MW/Min | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Down Rate Setpoint Feedback | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Down_Rate_Setpoint_Feedback | GMS Ramp Down Rate Setpoint Feedback | 378 | MW/Min | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Real Power Setpoint Unit 1 | PPC | GMS_MAP_DNP.PPC_Effective_Real_Power_Setpoint_T1 | PPC Real Power Setpoint | 379 | MW | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Real Power Setpoint Unit 2 | PPC | GMS_MAP_DNP.PPC_Effective_Real_Power_Setpoint_T2 | PPC Real Power Setpoint | 380 | MW | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Reactive Power Setpoint | PPC | GMS_MAP_DNP.PPC_Effective_Reactive_Power_Setpoint | PPC Reactive Power Setpoint | 381 | MVAR | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Power Factor Setpoint | PPC | GMS_MAP_DNP.PPC_Effective_Power_Factor_Setpoint | PPC Power Factor Setpoint | 382 | positive is lagging, negative is leading | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Voltage Setpoint | PPC | GMS_MAP_DNP.PPC_Effective_Voltage_Setpoint | PPC Voltage Setpoint | 383 | KV | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Ramp Rate Up Setpoint | PPC | GMS_MAP_DNP.PPC_Effective_Ramp_Rate_Up_Setpoint | PPC Ramp Rate Up Setpoint | 384 | MW/Min | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Ramp Rate Down Setpoint | PPC | GMS_MAP_DNP.PPC_Effective_Ramp_Rate_Down_Setpoint | PPC Ramp Rate Down Setpoint | 385 | MW/Min | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Effective Reactive Power Control Mode | PPC | GMS_MAP_DNP.PPC_Effective_Reactive_Power_Control_Mode | PPC Control Status | 386 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Real Time Power Potential Unit 1 | PPC | GMS_MAP_DNP.PPC_Real_Time_Power_Potential_Unit_1 | PPC Real Time Power Potential | 387 | MW | Requested-Available | -32767 | 32767
SUB1 | PPC | TSN1_SUB1_PPC_Real Time Power Potential Unit 2 | PPC | GMS_MAP_DNP.PPC_Real_Time_Power_Potential_Unit_2 | PPC Real Time Power Potential | 388 | MW | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Battery Voltage | MET Station | GMS_MAP_DNP.MET101_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Humidity | MET Station | GMS_MAP_DNP.MET101_Humidity | Humidity | 389 | % | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Pressure | MET Station | GMS_MAP_DNP.MET101_Pressure | Pressure | 390 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Temperature | MET Station | GMS_MAP_DNP.MET101_Temperature | Temperature | 391 | °C | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Wind Direction | MET Station | GMS_MAP_DNP.MET101_Wind_Direction | Wind Direction | 392 | ° | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Wind Speed | MET Station | GMS_MAP_DNP.MET101_Wind_Speed | Wind Speed | 393 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET101_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 394 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Wind Direction Average | MET Station | GMS_MAP_DNP.MET101_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Humidity Average | MET Station | GMS_MAP_DNP.MET101_Humidity_Average | Humidity Average | 395 | % | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Pressure Average | MET Station | GMS_MAP_DNP.MET101_Pressure_Average | Pressure Average | 396 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Temperature Average | MET Station | GMS_MAP_DNP.MET101_Temperature_Average | Temperature Average | 397 | °C | Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET101_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Panel Temperature | MET Station | GMS_MAP_DNP.MET101_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Heartbeat | MET Station | GMS_MAP_DNP.MET101_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET101_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 398 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Irradiance | MET Station | GMS_MAP_DNP.MET101_GHI_Irradiance | GHI Irradiance | 399 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Body Temp | MET Station | GMS_MAP_DNP.MET101_GHI_Body_Temp | GHI Body Temp | 400 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Humidity | MET Station | GMS_MAP_DNP.MET101_GHI_Humidity | GHI Humidity | 401 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET101_GHI_Tilt_Angle | GHI Tilt Angle | 402 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET101_GHI_Pressure_Average | GHI Pressure Average | 403 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET101_GHI_Fan_Speed | GHI Fan Speed | 404 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Fan Current | MET Station | GMS_MAP_DNP.MET101_GHI_Fan_Current | GHI Fan Current | 405 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_GHI Heater Current | MET Station | GMS_MAP_DNP.MET101_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 406 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET101_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 407 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Irradiance | MET Station | GMS_MAP_DNP.MET101_POA_Irradiance | POA Irradiance | 408 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Body Temp | MET Station | GMS_MAP_DNP.MET101_POA_Body_Temp | POA Body Temp | 409 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Humidity | MET Station | GMS_MAP_DNP.MET101_POA_Humidity | POA Humidity | 410 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET101_POA_Tilt_Angle | POA Tilt Angle | 411 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Pressure Average | MET Station | GMS_MAP_DNP.MET101_POA_Pressure_Average | POA Pressure Average | 412 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Fan Speed | MET Station | GMS_MAP_DNP.MET101_POA_Fan_Speed | POA Fan Speed | 413 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Fan Current | MET Station | GMS_MAP_DNP.MET101_POA_Fan_Current | POA Fan Current | 414 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_POA Heater Current | MET Station | GMS_MAP_DNP.MET101_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 415 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET101_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 416 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET101_RPOA_Irradiance | RPOA Irradiance | 417 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET101_RPOA_Body_Temp | RPOA Body Temp | 418 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Humidity | MET Station | GMS_MAP_DNP.MET101_RPOA_Humidity | RPOA Humidity | 419 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET101_RPOA_Tilt_Angle | RPOA Tilt Angle | 420 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET101_RPOA_Pressure_Average | RPOA Pressure Average | 421 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET101_RPOA_Fan_Speed | RPOA Fan Speed | 422 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET101_RPOA_Fan_Current | RPOA Fan Current | 423 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET101_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 424 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET101_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 425 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET101_ALB UP_Irradiance | ALB UP Irradiance | 426 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET101_ALB UP_Body_Temp | ALB UP Body Temp | 427 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET101_ALB UP_Humidity | ALB UP Humidity | 428 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET101_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 429 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET101_ALB UP_Pressure_Average | ALB UP Pressure Average | 430 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET101_ALB UP_Fan_Speed | ALB UP Fan Speed | 431 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET101_ALB UP_Fan_Current | ALB UP Fan Current | 432 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET101_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 433 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET101_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 434 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET101_ALB DN_Irradiance | ALB DN Irradiance | 435 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET101_ALB DN_Body_Temp | ALB DN Body Temp | 436 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET101_ALB DN_Humidity | ALB DN Humidity | 437 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET101_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 438 | ° | Not Requested-Available | -32767 | 32767
SUB1 | Station101 | TSN1_SUB1_MET101_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET101_ALB DN_Pressure_Average | ALB DN Pressure Average | 439 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET101_ALB DN_Fan_Speed | ALB DN Fan Speed | 440 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET101_ALB DN_Fan_Current | ALB DN Fan Current | 441 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET101_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 442 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET101_BOM1_Temp | Back Of Module 1 Temp | 443 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET101_BOM2_Temp | Back Of Module 2 Temp | 444 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET101_BOM3_Temp | Back Of Module 3 Temp | 445 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET101 | TSN1_SUB1_MET101_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET101_BOM4_Temp | Back Of Module 4 Temp | 446 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Battery Voltage | MET Station | GMS_MAP_DNP.MET102_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Humidity | MET Station | GMS_MAP_DNP.MET102_Humidity | Humidity | 447 | % | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Pressure | MET Station | GMS_MAP_DNP.MET102_Pressure | Pressure | 448 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Temperature | MET Station | GMS_MAP_DNP.MET102_Temperature | Temperature | 449 | °C | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Wind Direction | MET Station | GMS_MAP_DNP.MET102_Wind_Direction | Wind Direction | 450 | ° | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Wind Speed | MET Station | GMS_MAP_DNP.MET102_Wind_Speed | Wind Speed | 451 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET102_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 452 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Wind Direction Average | MET Station | GMS_MAP_DNP.MET102_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Humidity Average | MET Station | GMS_MAP_DNP.MET102_Humidity_Average | Humidity Average | 453 | % | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Pressure Average | MET Station | GMS_MAP_DNP.MET102_Pressure_Average | Pressure Average | 454 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Temperature Average | MET Station | GMS_MAP_DNP.MET102_Temperature_Average | Temperature Average | 455 | °C | Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET102_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Panel Temperature | MET Station | GMS_MAP_DNP.MET102_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Heartbeat | MET Station | GMS_MAP_DNP.MET102_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET102_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 456 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Irradiance | MET Station | GMS_MAP_DNP.MET102_GHI_Irradiance | GHI Irradiance | 457 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Body Temp | MET Station | GMS_MAP_DNP.MET102_GHI_Body_Temp | GHI Body Temp | 458 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Humidity | MET Station | GMS_MAP_DNP.MET102_GHI_Humidity | GHI Humidity | 459 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET102_GHI_Tilt_Angle | GHI Tilt Angle | 460 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET102_GHI_Pressure_Average | GHI Pressure Average | 461 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET102_GHI_Fan_Speed | GHI Fan Speed | 462 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Fan Current | MET Station | GMS_MAP_DNP.MET102_GHI_Fan_Current | GHI Fan Current | 463 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_GHI Heater Current | MET Station | GMS_MAP_DNP.MET102_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 464 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET102_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 465 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Irradiance | MET Station | GMS_MAP_DNP.MET102_POA_Irradiance | POA Irradiance | 466 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Body Temp | MET Station | GMS_MAP_DNP.MET102_POA_Body_Temp | POA Body Temp | 467 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Humidity | MET Station | GMS_MAP_DNP.MET102_POA_Humidity | POA Humidity | 468 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET102_POA_Tilt_Angle | POA Tilt Angle | 469 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Pressure Average | MET Station | GMS_MAP_DNP.MET102_POA_Pressure_Average | POA Pressure Average | 470 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Fan Speed | MET Station | GMS_MAP_DNP.MET102_POA_Fan_Speed | POA Fan Speed | 471 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Fan Current | MET Station | GMS_MAP_DNP.MET102_POA_Fan_Current | POA Fan Current | 472 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_POA Heater Current | MET Station | GMS_MAP_DNP.MET102_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 473 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET102_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 474 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET102_RPOA_Irradiance | RPOA Irradiance | 475 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET102_RPOA_Body_Temp | RPOA Body Temp | 476 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Humidity | MET Station | GMS_MAP_DNP.MET102_RPOA_Humidity | RPOA Humidity | 477 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET102_RPOA_Tilt_Angle | RPOA Tilt Angle | 478 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET102_RPOA_Pressure_Average | RPOA Pressure Average | 479 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET102_RPOA_Fan_Speed | RPOA Fan Speed | 480 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET102_RPOA_Fan_Current | RPOA Fan Current | 481 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET102_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 482 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET102_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 483 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET102_ALB UP_Irradiance | ALB UP Irradiance | 484 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET102_ALB UP_Body_Temp | ALB UP Body Temp | 485 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET102_ALB UP_Humidity | ALB UP Humidity | 486 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET102_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 487 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET102_ALB UP_Pressure_Average | ALB UP Pressure Average | 488 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET102_ALB UP_Fan_Speed | ALB UP Fan Speed | 489 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET102_ALB UP_Fan_Current | ALB UP Fan Current | 490 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET102_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 491 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET102_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 492 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET102_ALB DN_Irradiance | ALB DN Irradiance | 493 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET102_ALB DN_Body_Temp | ALB DN Body Temp | 494 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET102_ALB DN_Humidity | ALB DN Humidity | 495 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET102_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 496 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET102_ALB DN_Pressure_Average | ALB DN Pressure Average | 497 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET102_ALB DN_Fan_Speed | ALB DN Fan Speed | 498 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET102_ALB DN_Fan_Current | ALB DN Fan Current | 499 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET102_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 500 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET102_BOM1_Temp | Back Of Module 1 Temp | 501 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET102_BOM2_Temp | Back Of Module 2 Temp | 502 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET102_BOM3_Temp | Back Of Module 3 Temp | 503 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET102 | TSN1_SUB1_MET102_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET102_BOM4_Temp | Back Of Module 4 Temp | 504 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Battery Voltage | MET Station | GMS_MAP_DNP.MET103_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Humidity | MET Station | GMS_MAP_DNP.MET103_Humidity | Humidity | 505 | % | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Pressure | MET Station | GMS_MAP_DNP.MET103_Pressure | Pressure | 506 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Temperature | MET Station | GMS_MAP_DNP.MET103_Temperature | Temperature | 507 | °C | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Wind Direction | MET Station | GMS_MAP_DNP.MET103_Wind_Direction | Wind Direction | 508 | ° | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Wind Speed | MET Station | GMS_MAP_DNP.MET103_Wind_Speed | Wind Speed | 509 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET103_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 510 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Wind Direction Average | MET Station | GMS_MAP_DNP.MET103_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Humidity Average | MET Station | GMS_MAP_DNP.MET103_Humidity_Average | Humidity Average | 511 | % | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Pressure Average | MET Station | GMS_MAP_DNP.MET103_Pressure_Average | Pressure Average | 512 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Temperature Average | MET Station | GMS_MAP_DNP.MET103_Temperature_Average | Temperature Average | 513 | °C | Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET103_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Panel Temperature | MET Station | GMS_MAP_DNP.MET103_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Heartbeat | MET Station | GMS_MAP_DNP.MET103_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET103_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 514 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Irradiance | MET Station | GMS_MAP_DNP.MET103_GHI_Irradiance | GHI Irradiance | 515 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Body Temp | MET Station | GMS_MAP_DNP.MET103_GHI_Body_Temp | GHI Body Temp | 516 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Humidity | MET Station | GMS_MAP_DNP.MET103_GHI_Humidity | GHI Humidity | 517 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET103_GHI_Tilt_Angle | GHI Tilt Angle | 518 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET103_GHI_Pressure_Average | GHI Pressure Average | 519 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET103_GHI_Fan_Speed | GHI Fan Speed | 520 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Fan Current | MET Station | GMS_MAP_DNP.MET103_GHI_Fan_Current | GHI Fan Current | 521 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_GHI Heater Current | MET Station | GMS_MAP_DNP.MET103_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 522 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET103_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 523 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Irradiance | MET Station | GMS_MAP_DNP.MET103_POA_Irradiance | POA Irradiance | 524 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Body Temp | MET Station | GMS_MAP_DNP.MET103_POA_Body_Temp | POA Body Temp | 525 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Humidity | MET Station | GMS_MAP_DNP.MET103_POA_Humidity | POA Humidity | 526 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET103_POA_Tilt_Angle | POA Tilt Angle | 527 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Pressure Average | MET Station | GMS_MAP_DNP.MET103_POA_Pressure_Average | POA Pressure Average | 528 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Fan Speed | MET Station | GMS_MAP_DNP.MET103_POA_Fan_Speed | POA Fan Speed | 529 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Fan Current | MET Station | GMS_MAP_DNP.MET103_POA_Fan_Current | POA Fan Current | 530 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_POA Heater Current | MET Station | GMS_MAP_DNP.MET103_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 531 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET103_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 532 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET103_RPOA_Irradiance | RPOA Irradiance | 533 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET103_RPOA_Body_Temp | RPOA Body Temp | 534 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Humidity | MET Station | GMS_MAP_DNP.MET103_RPOA_Humidity | RPOA Humidity | 535 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET103_RPOA_Tilt_Angle | RPOA Tilt Angle | 536 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET103_RPOA_Pressure_Average | RPOA Pressure Average | 537 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET103_RPOA_Fan_Speed | RPOA Fan Speed | 538 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET103_RPOA_Fan_Current | RPOA Fan Current | 539 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET103_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 540 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET103_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 541 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET103_ALB UP_Irradiance | ALB UP Irradiance | 542 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET103_ALB UP_Body_Temp | ALB UP Body Temp | 543 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET103_ALB UP_Humidity | ALB UP Humidity | 544 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET103_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 545 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET103_ALB UP_Pressure_Average | ALB UP Pressure Average | 546 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET103_ALB UP_Fan_Speed | ALB UP Fan Speed | 547 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET103_ALB UP_Fan_Current | ALB UP Fan Current | 548 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET103_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 549 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET103_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 550 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET103_ALB DN_Irradiance | ALB DN Irradiance | 551 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET103_ALB DN_Body_Temp | ALB DN Body Temp | 552 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET103_ALB DN_Humidity | ALB DN Humidity | 553 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET103_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 554 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET103_ALB DN_Pressure_Average | ALB DN Pressure Average | 555 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET103_ALB DN_Fan_Speed | ALB DN Fan Speed | 556 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET103_ALB DN_Fan_Current | ALB DN Fan Current | 557 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET103_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 558 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET103_BOM1_Temp | Back Of Module 1 Temp | 559 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET103_BOM2_Temp | Back Of Module 2 Temp | 560 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET103_BOM3_Temp | Back Of Module 3 Temp | 561 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET103 | TSN1_SUB1_MET103_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET103_BOM4_Temp | Back Of Module 4 Temp | 562 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Battery Voltage | MET Station | GMS_MAP_DNP.MET104_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Humidity | MET Station | GMS_MAP_DNP.MET104_Humidity | Humidity | 563 | % | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Pressure | MET Station | GMS_MAP_DNP.MET104_Pressure | Pressure | 564 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Temperature | MET Station | GMS_MAP_DNP.MET104_Temperature | Temperature | 565 | °C | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Wind Direction | MET Station | GMS_MAP_DNP.MET104_Wind_Direction | Wind Direction | 566 | ° | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Wind Speed | MET Station | GMS_MAP_DNP.MET104_Wind_Speed | Wind Speed | 567 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET104_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 568 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Wind Direction Average | MET Station | GMS_MAP_DNP.MET104_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Humidity Average | MET Station | GMS_MAP_DNP.MET104_Humidity_Average | Humidity Average | 569 | % | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Pressure Average | MET Station | GMS_MAP_DNP.MET104_Pressure_Average | Pressure Average | 570 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Temperature Average | MET Station | GMS_MAP_DNP.MET104_Temperature_Average | Temperature Average | 571 | °C | Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET104_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Panel Temperature | MET Station | GMS_MAP_DNP.MET104_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Heartbeat | MET Station | GMS_MAP_DNP.MET104_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET104_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 572 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Irradiance | MET Station | GMS_MAP_DNP.MET104_GHI_Irradiance | GHI Irradiance | 573 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Body Temp | MET Station | GMS_MAP_DNP.MET104_GHI_Body_Temp | GHI Body Temp | 574 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Humidity | MET Station | GMS_MAP_DNP.MET104_GHI_Humidity | GHI Humidity | 575 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET104_GHI_Tilt_Angle | GHI Tilt Angle | 576 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET104_GHI_Pressure_Average | GHI Pressure Average | 577 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET104_GHI_Fan_Speed | GHI Fan Speed | 578 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Fan Current | MET Station | GMS_MAP_DNP.MET104_GHI_Fan_Current | GHI Fan Current | 579 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_GHI Heater Current | MET Station | GMS_MAP_DNP.MET104_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 580 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET104_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 581 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Irradiance | MET Station | GMS_MAP_DNP.MET104_POA_Irradiance | POA Irradiance | 582 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Body Temp | MET Station | GMS_MAP_DNP.MET104_POA_Body_Temp | POA Body Temp | 583 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Humidity | MET Station | GMS_MAP_DNP.MET104_POA_Humidity | POA Humidity | 584 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET104_POA_Tilt_Angle | POA Tilt Angle | 585 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Pressure Average | MET Station | GMS_MAP_DNP.MET104_POA_Pressure_Average | POA Pressure Average | 586 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Fan Speed | MET Station | GMS_MAP_DNP.MET104_POA_Fan_Speed | POA Fan Speed | 587 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Fan Current | MET Station | GMS_MAP_DNP.MET104_POA_Fan_Current | POA Fan Current | 588 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_POA Heater Current | MET Station | GMS_MAP_DNP.MET104_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 589 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET104_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 590 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET104_RPOA_Irradiance | RPOA Irradiance | 591 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET104_RPOA_Body_Temp | RPOA Body Temp | 592 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Humidity | MET Station | GMS_MAP_DNP.MET104_RPOA_Humidity | RPOA Humidity | 593 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET104_RPOA_Tilt_Angle | RPOA Tilt Angle | 594 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET104_RPOA_Pressure_Average | RPOA Pressure Average | 595 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET104_RPOA_Fan_Speed | RPOA Fan Speed | 596 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET104_RPOA_Fan_Current | RPOA Fan Current | 597 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET104_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 598 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET104_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 599 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET104_ALB UP_Irradiance | ALB UP Irradiance | 600 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET104_ALB UP_Body_Temp | ALB UP Body Temp | 601 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET104_ALB UP_Humidity | ALB UP Humidity | 602 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET104_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 603 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET104_ALB UP_Pressure_Average | ALB UP Pressure Average | 604 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET104_ALB UP_Fan_Speed | ALB UP Fan Speed | 605 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET104_ALB UP_Fan_Current | ALB UP Fan Current | 606 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET104_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 607 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET104_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 608 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET104_ALB DN_Irradiance | ALB DN Irradiance | 609 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET104_ALB DN_Body_Temp | ALB DN Body Temp | 610 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET104_ALB DN_Humidity | ALB DN Humidity | 611 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET104_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 612 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET104_ALB DN_Pressure_Average | ALB DN Pressure Average | 613 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET104_ALB DN_Fan_Speed | ALB DN Fan Speed | 614 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET104_ALB DN_Fan_Current | ALB DN Fan Current | 615 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET104_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 616 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET104_BOM1_Temp | Back Of Module 1 Temp | 617 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET104_BOM2_Temp | Back Of Module 2 Temp | 618 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET104_BOM3_Temp | Back Of Module 3 Temp | 619 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET104 | TSN1_SUB1_MET104_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET104_BOM4_Temp | Back Of Module 4 Temp | 620 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Battery Voltage | MET Station | GMS_MAP_DNP.MET105_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Humidity | MET Station | GMS_MAP_DNP.MET105_Humidity | Humidity | 621 | % | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Pressure | MET Station | GMS_MAP_DNP.MET105_Pressure | Pressure | 622 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Temperature | MET Station | GMS_MAP_DNP.MET105_Temperature | Temperature | 623 | °C | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Wind Direction | MET Station | GMS_MAP_DNP.MET105_Wind_Direction | Wind Direction | 624 | ° | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Wind Speed | MET Station | GMS_MAP_DNP.MET105_Wind_Speed | Wind Speed | 625 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET105_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 626 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Wind Direction Average | MET Station | GMS_MAP_DNP.MET105_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Humidity Average | MET Station | GMS_MAP_DNP.MET105_Humidity_Average | Humidity Average | 627 | % | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Pressure Average | MET Station | GMS_MAP_DNP.MET105_Pressure_Average | Pressure Average | 628 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Temperature Average | MET Station | GMS_MAP_DNP.MET105_Temperature_Average | Temperature Average | 629 | °C | Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET105_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Panel Temperature | MET Station | GMS_MAP_DNP.MET105_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Heartbeat | MET Station | GMS_MAP_DNP.MET105_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET105_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 630 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Irradiance | MET Station | GMS_MAP_DNP.MET105_GHI_Irradiance | GHI Irradiance | 631 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Body Temp | MET Station | GMS_MAP_DNP.MET105_GHI_Body_Temp | GHI Body Temp | 632 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Humidity | MET Station | GMS_MAP_DNP.MET105_GHI_Humidity | GHI Humidity | 633 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET105_GHI_Tilt_Angle | GHI Tilt Angle | 634 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET105_GHI_Pressure_Average | GHI Pressure Average | 635 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET105_GHI_Fan_Speed | GHI Fan Speed | 636 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Fan Current | MET Station | GMS_MAP_DNP.MET105_GHI_Fan_Current | GHI Fan Current | 637 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_GHI Heater Current | MET Station | GMS_MAP_DNP.MET105_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 638 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET105_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 639 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Irradiance | MET Station | GMS_MAP_DNP.MET105_POA_Irradiance | POA Irradiance | 640 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Body Temp | MET Station | GMS_MAP_DNP.MET105_POA_Body_Temp | POA Body Temp | 641 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Humidity | MET Station | GMS_MAP_DNP.MET105_POA_Humidity | POA Humidity | 642 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET105_POA_Tilt_Angle | POA Tilt Angle | 643 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Pressure Average | MET Station | GMS_MAP_DNP.MET105_POA_Pressure_Average | POA Pressure Average | 644 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Fan Speed | MET Station | GMS_MAP_DNP.MET105_POA_Fan_Speed | POA Fan Speed | 645 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Fan Current | MET Station | GMS_MAP_DNP.MET105_POA_Fan_Current | POA Fan Current | 646 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_POA Heater Current | MET Station | GMS_MAP_DNP.MET105_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 647 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET105_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 648 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET105_RPOA_Irradiance | RPOA Irradiance | 649 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET105_RPOA_Body_Temp | RPOA Body Temp | 650 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Humidity | MET Station | GMS_MAP_DNP.MET105_RPOA_Humidity | RPOA Humidity | 651 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET105_RPOA_Tilt_Angle | RPOA Tilt Angle | 652 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET105_RPOA_Pressure_Average | RPOA Pressure Average | 653 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET105_RPOA_Fan_Speed | RPOA Fan Speed | 654 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET105_RPOA_Fan_Current | RPOA Fan Current | 655 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET105_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 656 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET105_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 657 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET105_ALB UP_Irradiance | ALB UP Irradiance | 658 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET105_ALB UP_Body_Temp | ALB UP Body Temp | 659 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET105_ALB UP_Humidity | ALB UP Humidity | 660 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET105_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 661 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET105_ALB UP_Pressure_Average | ALB UP Pressure Average | 662 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET105_ALB UP_Fan_Speed | ALB UP Fan Speed | 663 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET105_ALB UP_Fan_Current | ALB UP Fan Current | 664 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET105_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 665 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET105_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 666 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET105_ALB DN_Irradiance | ALB DN Irradiance | 667 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET105_ALB DN_Body_Temp | ALB DN Body Temp | 668 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET105_ALB DN_Humidity | ALB DN Humidity | 669 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET105_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 670 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET105_ALB DN_Pressure_Average | ALB DN Pressure Average | 671 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET105_ALB DN_Fan_Speed | ALB DN Fan Speed | 672 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET105_ALB DN_Fan_Current | ALB DN Fan Current | 673 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET105_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 674 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET105_BOM1_Temp | Back Of Module 1 Temp | 675 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET105_BOM2_Temp | Back Of Module 2 Temp | 676 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET105_BOM3_Temp | Back Of Module 3 Temp | 677 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET105 | TSN1_SUB1_MET105_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET105_BOM4_Temp | Back Of Module 4 Temp | 678 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Battery Voltage | MET Station | GMS_MAP_DNP.MET106_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Humidity | MET Station | GMS_MAP_DNP.MET106_Humidity | Humidity | 679 | % | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Pressure | MET Station | GMS_MAP_DNP.MET106_Pressure | Pressure | 680 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Temperature | MET Station | GMS_MAP_DNP.MET106_Temperature | Temperature | 681 | °C | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Wind Direction | MET Station | GMS_MAP_DNP.MET106_Wind_Direction | Wind Direction | 682 | ° | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Wind Speed | MET Station | GMS_MAP_DNP.MET106_Wind_Speed | Wind Speed | 683 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET106_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 684 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Wind Direction Average | MET Station | GMS_MAP_DNP.MET106_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Humidity Average | MET Station | GMS_MAP_DNP.MET106_Humidity_Average | Humidity Average | 685 | % | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Pressure Average | MET Station | GMS_MAP_DNP.MET106_Pressure_Average | Pressure Average | 686 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Temperature Average | MET Station | GMS_MAP_DNP.MET106_Temperature_Average | Temperature Average | 687 | °C | Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET106_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Panel Temperature | MET Station | GMS_MAP_DNP.MET106_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Heartbeat | MET Station | GMS_MAP_DNP.MET106_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET106_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 688 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Irradiance | MET Station | GMS_MAP_DNP.MET106_GHI_Irradiance | GHI Irradiance | 689 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Body Temp | MET Station | GMS_MAP_DNP.MET106_GHI_Body_Temp | GHI Body Temp | 690 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Humidity | MET Station | GMS_MAP_DNP.MET106_GHI_Humidity | GHI Humidity | 691 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET106_GHI_Tilt_Angle | GHI Tilt Angle | 692 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET106_GHI_Pressure_Average | GHI Pressure Average | 693 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET106_GHI_Fan_Speed | GHI Fan Speed | 694 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Fan Current | MET Station | GMS_MAP_DNP.MET106_GHI_Fan_Current | GHI Fan Current | 695 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_GHI Heater Current | MET Station | GMS_MAP_DNP.MET106_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 696 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET106_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 697 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Irradiance | MET Station | GMS_MAP_DNP.MET106_POA_Irradiance | POA Irradiance | 698 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Body Temp | MET Station | GMS_MAP_DNP.MET106_POA_Body_Temp | POA Body Temp | 699 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Humidity | MET Station | GMS_MAP_DNP.MET106_POA_Humidity | POA Humidity | 700 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET106_POA_Tilt_Angle | POA Tilt Angle | 701 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Pressure Average | MET Station | GMS_MAP_DNP.MET106_POA_Pressure_Average | POA Pressure Average | 702 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Fan Speed | MET Station | GMS_MAP_DNP.MET106_POA_Fan_Speed | POA Fan Speed | 703 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Fan Current | MET Station | GMS_MAP_DNP.MET106_POA_Fan_Current | POA Fan Current | 704 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_POA Heater Current | MET Station | GMS_MAP_DNP.MET106_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 705 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET106_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 706 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET106_RPOA_Irradiance | RPOA Irradiance | 707 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET106_RPOA_Body_Temp | RPOA Body Temp | 708 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Humidity | MET Station | GMS_MAP_DNP.MET106_RPOA_Humidity | RPOA Humidity | 709 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET106_RPOA_Tilt_Angle | RPOA Tilt Angle | 710 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET106_RPOA_Pressure_Average | RPOA Pressure Average | 711 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET106_RPOA_Fan_Speed | RPOA Fan Speed | 712 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET106_RPOA_Fan_Current | RPOA Fan Current | 713 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET106_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 714 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET106_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 715 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET106_ALB UP_Irradiance | ALB UP Irradiance | 716 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET106_ALB UP_Body_Temp | ALB UP Body Temp | 717 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET106_ALB UP_Humidity | ALB UP Humidity | 718 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET106_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 719 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET106_ALB UP_Pressure_Average | ALB UP Pressure Average | 720 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET106_ALB UP_Fan_Speed | ALB UP Fan Speed | 721 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET106_ALB UP_Fan_Current | ALB UP Fan Current | 722 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET106_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 723 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET106_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 724 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET106_ALB DN_Irradiance | ALB DN Irradiance | 725 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET106_ALB DN_Body_Temp | ALB DN Body Temp | 726 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET106_ALB DN_Humidity | ALB DN Humidity | 727 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET106_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 728 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET106_ALB DN_Pressure_Average | ALB DN Pressure Average | 729 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET106_ALB DN_Fan_Speed | ALB DN Fan Speed | 730 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET106_ALB DN_Fan_Current | ALB DN Fan Current | 731 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET106_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 732 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET106_BOM1_Temp | Back Of Module 1 Temp | 733 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET106_BOM2_Temp | Back Of Module 2 Temp | 734 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET106_BOM3_Temp | Back Of Module 3 Temp | 735 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET106 | TSN1_SUB1_MET106_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET106_BOM4_Temp | Back Of Module 4 Temp | 736 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Battery Voltage | MET Station | GMS_MAP_DNP.MET107_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Humidity | MET Station | GMS_MAP_DNP.MET107_Humidity | Humidity | 737 | % | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Pressure | MET Station | GMS_MAP_DNP.MET107_Pressure | Pressure | 738 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Temperature | MET Station | GMS_MAP_DNP.MET107_Temperature | Temperature | 739 | °C | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Wind Direction | MET Station | GMS_MAP_DNP.MET107_Wind_Direction | Wind Direction | 740 | ° | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Wind Speed | MET Station | GMS_MAP_DNP.MET107_Wind_Speed | Wind Speed | 741 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET107_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 742 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Wind Direction Average | MET Station | GMS_MAP_DNP.MET107_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Humidity Average | MET Station | GMS_MAP_DNP.MET107_Humidity_Average | Humidity Average | 743 | % | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Pressure Average | MET Station | GMS_MAP_DNP.MET107_Pressure_Average | Pressure Average | 744 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Temperature Average | MET Station | GMS_MAP_DNP.MET107_Temperature_Average | Temperature Average | 745 | °C | Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET107_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Panel Temperature | MET Station | GMS_MAP_DNP.MET107_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Heartbeat | MET Station | GMS_MAP_DNP.MET107_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET107_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 746 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Irradiance | MET Station | GMS_MAP_DNP.MET107_GHI_Irradiance | GHI Irradiance | 747 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Body Temp | MET Station | GMS_MAP_DNP.MET107_GHI_Body_Temp | GHI Body Temp | 748 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Humidity | MET Station | GMS_MAP_DNP.MET107_GHI_Humidity | GHI Humidity | 749 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET107_GHI_Tilt_Angle | GHI Tilt Angle | 750 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET107_GHI_Pressure_Average | GHI Pressure Average | 751 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET107_GHI_Fan_Speed | GHI Fan Speed | 752 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Fan Current | MET Station | GMS_MAP_DNP.MET107_GHI_Fan_Current | GHI Fan Current | 753 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_GHI Heater Current | MET Station | GMS_MAP_DNP.MET107_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 754 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET107_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 755 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Irradiance | MET Station | GMS_MAP_DNP.MET107_POA_Irradiance | POA Irradiance | 756 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Body Temp | MET Station | GMS_MAP_DNP.MET107_POA_Body_Temp | POA Body Temp | 757 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Humidity | MET Station | GMS_MAP_DNP.MET107_POA_Humidity | POA Humidity | 758 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET107_POA_Tilt_Angle | POA Tilt Angle | 759 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Pressure Average | MET Station | GMS_MAP_DNP.MET107_POA_Pressure_Average | POA Pressure Average | 760 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Fan Speed | MET Station | GMS_MAP_DNP.MET107_POA_Fan_Speed | POA Fan Speed | 761 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Fan Current | MET Station | GMS_MAP_DNP.MET107_POA_Fan_Current | POA Fan Current | 762 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_POA Heater Current | MET Station | GMS_MAP_DNP.MET107_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 763 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET107_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 764 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET107_RPOA_Irradiance | RPOA Irradiance | 765 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET107_RPOA_Body_Temp | RPOA Body Temp | 766 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Humidity | MET Station | GMS_MAP_DNP.MET107_RPOA_Humidity | RPOA Humidity | 767 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET107_RPOA_Tilt_Angle | RPOA Tilt Angle | 768 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET107_RPOA_Pressure_Average | RPOA Pressure Average | 769 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET107_RPOA_Fan_Speed | RPOA Fan Speed | 770 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET107_RPOA_Fan_Current | RPOA Fan Current | 771 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET107_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 772 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET107_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 773 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET107_ALB UP_Irradiance | ALB UP Irradiance | 774 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET107_ALB UP_Body_Temp | ALB UP Body Temp | 775 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET107_ALB UP_Humidity | ALB UP Humidity | 776 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET107_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 777 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET107_ALB UP_Pressure_Average | ALB UP Pressure Average | 778 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET107_ALB UP_Fan_Speed | ALB UP Fan Speed | 779 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET107_ALB UP_Fan_Current | ALB UP Fan Current | 780 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET107_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 781 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET107_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 782 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET107_ALB DN_Irradiance | ALB DN Irradiance | 783 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET107_ALB DN_Body_Temp | ALB DN Body Temp | 784 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET107_ALB DN_Humidity | ALB DN Humidity | 785 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET107_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 786 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET107_ALB DN_Pressure_Average | ALB DN Pressure Average | 787 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET107_ALB DN_Fan_Speed | ALB DN Fan Speed | 788 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET107_ALB DN_Fan_Current | ALB DN Fan Current | 789 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET107_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 790 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET107_BOM1_Temp | Back Of Module 1 Temp | 791 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET107_BOM2_Temp | Back Of Module 2 Temp | 792 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET107_BOM3_Temp | Back Of Module 3 Temp | 793 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET107 | TSN1_SUB1_MET107_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET107_BOM4_Temp | Back Of Module 4 Temp | 794 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Battery Voltage | MET Station | GMS_MAP_DNP.MET108_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Humidity | MET Station | GMS_MAP_DNP.MET108_Humidity | Humidity | 795 | % | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Pressure | MET Station | GMS_MAP_DNP.MET108_Pressure | Pressure | 796 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Temperature | MET Station | GMS_MAP_DNP.MET108_Temperature | Temperature | 797 | °C | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Wind Direction | MET Station | GMS_MAP_DNP.MET108_Wind_Direction | Wind Direction | 798 | ° | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Wind Speed | MET Station | GMS_MAP_DNP.MET108_Wind_Speed | Wind Speed | 799 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET108_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 800 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Wind Direction Average | MET Station | GMS_MAP_DNP.MET108_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Humidity Average | MET Station | GMS_MAP_DNP.MET108_Humidity_Average | Humidity Average | 801 | % | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Pressure Average | MET Station | GMS_MAP_DNP.MET108_Pressure_Average | Pressure Average | 802 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Temperature Average | MET Station | GMS_MAP_DNP.MET108_Temperature_Average | Temperature Average | 803 | °C | Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET108_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Panel Temperature | MET Station | GMS_MAP_DNP.MET108_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Heartbeat | MET Station | GMS_MAP_DNP.MET108_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET108_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 804 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Irradiance | MET Station | GMS_MAP_DNP.MET108_GHI_Irradiance | GHI Irradiance | 805 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Body Temp | MET Station | GMS_MAP_DNP.MET108_GHI_Body_Temp | GHI Body Temp | 806 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Humidity | MET Station | GMS_MAP_DNP.MET108_GHI_Humidity | GHI Humidity | 807 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET108_GHI_Tilt_Angle | GHI Tilt Angle | 808 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET108_GHI_Pressure_Average | GHI Pressure Average | 809 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET108_GHI_Fan_Speed | GHI Fan Speed | 810 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Fan Current | MET Station | GMS_MAP_DNP.MET108_GHI_Fan_Current | GHI Fan Current | 811 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_GHI Heater Current | MET Station | GMS_MAP_DNP.MET108_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 812 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET108_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 813 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Irradiance | MET Station | GMS_MAP_DNP.MET108_POA_Irradiance | POA Irradiance | 814 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Body Temp | MET Station | GMS_MAP_DNP.MET108_POA_Body_Temp | POA Body Temp | 815 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Humidity | MET Station | GMS_MAP_DNP.MET108_POA_Humidity | POA Humidity | 816 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET108_POA_Tilt_Angle | POA Tilt Angle | 817 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Pressure Average | MET Station | GMS_MAP_DNP.MET108_POA_Pressure_Average | POA Pressure Average | 818 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Fan Speed | MET Station | GMS_MAP_DNP.MET108_POA_Fan_Speed | POA Fan Speed | 819 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Fan Current | MET Station | GMS_MAP_DNP.MET108_POA_Fan_Current | POA Fan Current | 820 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_POA Heater Current | MET Station | GMS_MAP_DNP.MET108_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 821 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET108_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 822 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET108_RPOA_Irradiance | RPOA Irradiance | 823 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET108_RPOA_Body_Temp | RPOA Body Temp | 824 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Humidity | MET Station | GMS_MAP_DNP.MET108_RPOA_Humidity | RPOA Humidity | 825 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET108_RPOA_Tilt_Angle | RPOA Tilt Angle | 826 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET108_RPOA_Pressure_Average | RPOA Pressure Average | 827 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET108_RPOA_Fan_Speed | RPOA Fan Speed | 828 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET108_RPOA_Fan_Current | RPOA Fan Current | 829 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET108_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 830 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET108_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 831 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET108_ALB UP_Irradiance | ALB UP Irradiance | 832 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET108_ALB UP_Body_Temp | ALB UP Body Temp | 833 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET108_ALB UP_Humidity | ALB UP Humidity | 834 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET108_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 835 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET108_ALB UP_Pressure_Average | ALB UP Pressure Average | 836 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET108_ALB UP_Fan_Speed | ALB UP Fan Speed | 837 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET108_ALB UP_Fan_Current | ALB UP Fan Current | 838 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET108_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 839 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET108_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 840 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET108_ALB DN_Irradiance | ALB DN Irradiance | 841 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET108_ALB DN_Body_Temp | ALB DN Body Temp | 842 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET108_ALB DN_Humidity | ALB DN Humidity | 843 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET108_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 844 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET108_ALB DN_Pressure_Average | ALB DN Pressure Average | 845 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET108_ALB DN_Fan_Speed | ALB DN Fan Speed | 846 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET108_ALB DN_Fan_Current | ALB DN Fan Current | 847 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET108_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 848 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET108_BOM1_Temp | Back Of Module 1 Temp | 849 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET108_BOM2_Temp | Back Of Module 2 Temp | 850 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET108_BOM3_Temp | Back Of Module 3 Temp | 851 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET108 | TSN1_SUB1_MET108_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET108_BOM4_Temp | Back Of Module 4 Temp | 852 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Battery Voltage | MET Station | GMS_MAP_DNP.MET109_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Humidity | MET Station | GMS_MAP_DNP.MET109_Humidity | Humidity | 853 | % | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Pressure | MET Station | GMS_MAP_DNP.MET109_Pressure | Pressure | 854 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Temperature | MET Station | GMS_MAP_DNP.MET109_Temperature | Temperature | 855 | °C | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Wind Direction | MET Station | GMS_MAP_DNP.MET109_Wind_Direction | Wind Direction | 856 | ° | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Wind Speed | MET Station | GMS_MAP_DNP.MET109_Wind_Speed | Wind Speed | 857 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET109_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 858 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Wind Direction Average | MET Station | GMS_MAP_DNP.MET109_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Humidity Average | MET Station | GMS_MAP_DNP.MET109_Humidity_Average | Humidity Average | 859 | % | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Pressure Average | MET Station | GMS_MAP_DNP.MET109_Pressure_Average | Pressure Average | 860 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Temperature Average | MET Station | GMS_MAP_DNP.MET109_Temperature_Average | Temperature Average | 861 | °C | Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET109_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Panel Temperature | MET Station | GMS_MAP_DNP.MET109_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Heartbeat | MET Station | GMS_MAP_DNP.MET109_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET109_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 862 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Irradiance | MET Station | GMS_MAP_DNP.MET109_GHI_Irradiance | GHI Irradiance | 863 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Body Temp | MET Station | GMS_MAP_DNP.MET109_GHI_Body_Temp | GHI Body Temp | 864 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Humidity | MET Station | GMS_MAP_DNP.MET109_GHI_Humidity | GHI Humidity | 865 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET109_GHI_Tilt_Angle | GHI Tilt Angle | 866 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET109_GHI_Pressure_Average | GHI Pressure Average | 867 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET109_GHI_Fan_Speed | GHI Fan Speed | 868 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Fan Current | MET Station | GMS_MAP_DNP.MET109_GHI_Fan_Current | GHI Fan Current | 869 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_GHI Heater Current | MET Station | GMS_MAP_DNP.MET109_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 870 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET109_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 871 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Irradiance | MET Station | GMS_MAP_DNP.MET109_POA_Irradiance | POA Irradiance | 872 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Body Temp | MET Station | GMS_MAP_DNP.MET109_POA_Body_Temp | POA Body Temp | 873 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Humidity | MET Station | GMS_MAP_DNP.MET109_POA_Humidity | POA Humidity | 874 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET109_POA_Tilt_Angle | POA Tilt Angle | 875 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Pressure Average | MET Station | GMS_MAP_DNP.MET109_POA_Pressure_Average | POA Pressure Average | 876 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Fan Speed | MET Station | GMS_MAP_DNP.MET109_POA_Fan_Speed | POA Fan Speed | 877 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Fan Current | MET Station | GMS_MAP_DNP.MET109_POA_Fan_Current | POA Fan Current | 878 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_POA Heater Current | MET Station | GMS_MAP_DNP.MET109_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 879 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET109_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 880 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET109_RPOA_Irradiance | RPOA Irradiance | 881 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET109_RPOA_Body_Temp | RPOA Body Temp | 882 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Humidity | MET Station | GMS_MAP_DNP.MET109_RPOA_Humidity | RPOA Humidity | 883 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET109_RPOA_Tilt_Angle | RPOA Tilt Angle | 884 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET109_RPOA_Pressure_Average | RPOA Pressure Average | 885 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET109_RPOA_Fan_Speed | RPOA Fan Speed | 886 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET109_RPOA_Fan_Current | RPOA Fan Current | 887 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET109_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 888 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET109_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 889 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET109_ALB UP_Irradiance | ALB UP Irradiance | 890 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET109_ALB UP_Body_Temp | ALB UP Body Temp | 891 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET109_ALB UP_Humidity | ALB UP Humidity | 892 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET109_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 893 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET109_ALB UP_Pressure_Average | ALB UP Pressure Average | 894 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET109_ALB UP_Fan_Speed | ALB UP Fan Speed | 895 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET109_ALB UP_Fan_Current | ALB UP Fan Current | 896 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET109_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 897 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET109_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 898 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET109_ALB DN_Irradiance | ALB DN Irradiance | 899 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET109_ALB DN_Body_Temp | ALB DN Body Temp | 900 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET109_ALB DN_Humidity | ALB DN Humidity | 901 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET109_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 902 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET109_ALB DN_Pressure_Average | ALB DN Pressure Average | 903 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET109_ALB DN_Fan_Speed | ALB DN Fan Speed | 904 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET109_ALB DN_Fan_Current | ALB DN Fan Current | 905 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET109_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 906 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET109_BOM1_Temp | Back Of Module 1 Temp | 907 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET109_BOM2_Temp | Back Of Module 2 Temp | 908 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET109_BOM3_Temp | Back Of Module 3 Temp | 909 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET109 | TSN1_SUB1_MET109_Back Of Module 4_Temp | MET Station | GMS_MAP_DNP.MET109_BOM4_Temp | Back Of Module 4 Temp | 910 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Battery Voltage | MET Station | GMS_MAP_DNP.MET110_Battery_Voltage | Battery Voltage |  | V | Requested-Not Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Humidity | MET Station | GMS_MAP_DNP.MET110_Humidity | Humidity | 911 | % | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Pressure | MET Station | GMS_MAP_DNP.MET110_Pressure | Pressure | 912 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Temperature | MET Station | GMS_MAP_DNP.MET110_Temperature | Temperature | 913 | °C | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Wind Direction | MET Station | GMS_MAP_DNP.MET110_Wind_Direction | Wind Direction | 914 | ° | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Wind Speed | MET Station | GMS_MAP_DNP.MET110_Wind_Speed | Wind Speed | 915 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Wind Speed-10 minute average | MET Station | GMS_MAP_DNP.MET110_Wind_Speed_10_minute_average | Wind Speed-10 minute average | 916 | m/s | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Wind Direction Average | MET Station | GMS_MAP_DNP.MET110_Wind_Direction_Average | Wind Direction Average |  | m/s | Requested-Not Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Humidity Average | MET Station | GMS_MAP_DNP.MET110_Humidity_Average | Humidity Average | 917 | % | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Pressure Average | MET Station | GMS_MAP_DNP.MET110_Pressure_Average | Pressure Average | 918 | hPa | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Temperature Average | MET Station | GMS_MAP_DNP.MET110_Temperature_Average | Temperature Average | 919 | °C | Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Rain-10 Minute | MET Station | GMS_MAP_DNP.MET110_Rain_10_Minute | Rain-10 Minute |  | in | Requested-Not Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Panel Temperature | MET Station | GMS_MAP_DNP.MET110_Panel_Temperature | Panel Temperature |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Heartbeat | MET Station | GMS_MAP_DNP.MET110_Heartbeat | Heartbeat |  | Counts | Requested-Not Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET110_GHI_Irradiance_Temp_Corrected | GHI Irradiance Temp Corrected | 920 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Irradiance | MET Station | GMS_MAP_DNP.MET110_GHI_Irradiance | GHI Irradiance | 921 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Body Temp | MET Station | GMS_MAP_DNP.MET110_GHI_Body_Temp | GHI Body Temp | 922 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Humidity | MET Station | GMS_MAP_DNP.MET110_GHI_Humidity | GHI Humidity | 923 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Tilt Angle | MET Station | GMS_MAP_DNP.MET110_GHI_Tilt_Angle | GHI Tilt Angle | 924 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Pressure Average | MET Station | GMS_MAP_DNP.MET110_GHI_Pressure_Average | GHI Pressure Average | 925 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Fan Speed | MET Station | GMS_MAP_DNP.MET110_GHI_Fan_Speed | GHI Fan Speed | 926 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Fan Current | MET Station | GMS_MAP_DNP.MET110_GHI_Fan_Current | GHI Fan Current | 927 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_GHI Heater Current | MET Station | GMS_MAP_DNP.MET110_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 928 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET110_POA_Irradiance_Temp_Corrected | POA Irradiance Temp Corrected | 929 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Irradiance | MET Station | GMS_MAP_DNP.MET110_POA_Irradiance | POA Irradiance | 930 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Body Temp | MET Station | GMS_MAP_DNP.MET110_POA_Body_Temp | POA Body Temp | 931 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Humidity | MET Station | GMS_MAP_DNP.MET110_POA_Humidity | POA Humidity | 932 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Tilt Angle | MET Station | GMS_MAP_DNP.MET110_POA_Tilt_Angle | POA Tilt Angle | 933 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Pressure Average | MET Station | GMS_MAP_DNP.MET110_POA_Pressure_Average | POA Pressure Average | 934 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Fan Speed | MET Station | GMS_MAP_DNP.MET110_POA_Fan_Speed | POA Fan Speed | 935 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Fan Current | MET Station | GMS_MAP_DNP.MET110_POA_Fan_Current | POA Fan Current | 936 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_POA Heater Current | MET Station | GMS_MAP_DNP.MET110_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 937 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET110_RPOA_Irradiance_Temp_Corrected | RPOA Irradiance Temp Corrected | 938 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Irradiance | MET Station | GMS_MAP_DNP.MET110_RPOA_Irradiance | RPOA Irradiance | 939 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Body Temp | MET Station | GMS_MAP_DNP.MET110_RPOA_Body_Temp | RPOA Body Temp | 940 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Humidity | MET Station | GMS_MAP_DNP.MET110_RPOA_Humidity | RPOA Humidity | 941 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Tilt Angle | MET Station | GMS_MAP_DNP.MET110_RPOA_Tilt_Angle | RPOA Tilt Angle | 942 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Pressure Average | MET Station | GMS_MAP_DNP.MET110_RPOA_Pressure_Average | RPOA Pressure Average | 943 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Fan Speed | MET Station | GMS_MAP_DNP.MET110_RPOA_Fan_Speed | RPOA Fan Speed | 944 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Fan Current | MET Station | GMS_MAP_DNP.MET110_RPOA_Fan_Current | RPOA Fan Current | 945 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_RPOA Heater Current | MET Station | GMS_MAP_DNP.MET110_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 946 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET110_ALB UP_Irradiance_Temp_Corrected | ALB UP Irradiance Temp Corrected | 947 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Irradiance | MET Station | GMS_MAP_DNP.MET110_ALB UP_Irradiance | ALB UP Irradiance | 948 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Body Temp | MET Station | GMS_MAP_DNP.MET110_ALB UP_Body_Temp | ALB UP Body Temp | 949 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Humidity | MET Station | GMS_MAP_DNP.MET110_ALB UP_Humidity | ALB UP Humidity | 950 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Tilt Angle | MET Station | GMS_MAP_DNP.MET110_ALB UP_Tilt_Angle | ALB UP Tilt Angle | 951 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Pressure Average | MET Station | GMS_MAP_DNP.MET110_ALB UP_Pressure_Average | ALB UP Pressure Average | 952 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Fan Speed | MET Station | GMS_MAP_DNP.MET110_ALB UP_Fan_Speed | ALB UP Fan Speed | 953 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Fan Current | MET Station | GMS_MAP_DNP.MET110_ALB UP_Fan_Current | ALB UP Fan Current | 954 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB UP Heater Current | MET Station | GMS_MAP_DNP.MET110_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 955 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Irradiance Temp Corrected | MET Station | GMS_MAP_DNP.MET110_ALB DN_Irradiance_Temp_Corrected | ALB DN Irradiance Temp Corrected | 956 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Irradiance | MET Station | GMS_MAP_DNP.MET110_ALB DN_Irradiance | ALB DN Irradiance | 957 | W/m² | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Body Temp | MET Station | GMS_MAP_DNP.MET110_ALB DN_Body_Temp | ALB DN Body Temp | 958 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Humidity | MET Station | GMS_MAP_DNP.MET110_ALB DN_Humidity | ALB DN Humidity | 959 | % | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Tilt Angle | MET Station | GMS_MAP_DNP.MET110_ALB DN_Tilt_Angle | ALB DN Tilt Angle | 960 | ° | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Pressure Average | MET Station | GMS_MAP_DNP.MET110_ALB DN_Pressure_Average | ALB DN Pressure Average | 961 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Fan Speed | MET Station | GMS_MAP_DNP.MET110_ALB DN_Fan_Speed | ALB DN Fan Speed | 962 | rpm | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Fan Current | MET Station | GMS_MAP_DNP.MET110_ALB DN_Fan_Current | ALB DN Fan Current | 963 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_ALB DN Heater Current | MET Station | GMS_MAP_DNP.MET110_POA1_Pyranometer_Irradiance | POA1-Pyranometer Irradiance | 964 | mA | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Back Of Module 1 Temp | MET Station | GMS_MAP_DNP.MET110_BOM1_Temp | Back Of Module 1 Temp | 965 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Back Of Module 2 Temp | MET Station | GMS_MAP_DNP.MET110_BOM2_Temp | Back Of Module 2 Temp | 966 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Back Of Module 3 Temp | MET Station | GMS_MAP_DNP.MET110_BOM3_Temp | Back Of Module 3 Temp | 967 | °C | Not Requested-Available | -32767 | 32767
SUB1 | MET110 | TSN1_SUB1_MET110_Back Of Module 4 Temp | MET Station | GMS_MAP_DNP.MET110_BOM4_Temp | Back Of Module 4 Temp | 968 | °C | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_A Phase Current | Inverter | GMS_MAP_DNP.INV001_A_Phase_Current | A Phase Current | 969 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_B Phase Current | Inverter | GMS_MAP_DNP.INV001_B_Phase_Current | B Phase Current | 970 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_C Phase Current | Inverter | GMS_MAP_DNP.INV001_C_Phase_Current | C Phase Current | 971 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Bus Voltage | Inverter | GMS_MAP_DNP.INV001_Bus_Voltage_AB | Bus Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Apparent Power | Inverter | GMS_MAP_DNP.INV001_Apparent_Power | Apparent Power |  | kVA | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Common Mode Voltage | Inverter | GMS_MAP_DNP.INV001_Common_Mode_Voltage | Common Mode Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input1 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input1 | Current DC Input# | 972 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input2 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input2 | Current DC Input# | 973 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input3 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input3 | Current DC Input# | 974 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input4 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input4 | Current DC Input# | 975 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input5 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input5 | Current DC Input# | 976 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current DC Input6 | Inverter | GMS_MAP_DNP.INV001_Current_DC_Input6 | Current DC Input# | 977 | A | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power DC Input # | Inverter | GMS_MAP_DNP.INV001_Real Power_DC_Input# | Real Power DC Input # |  | KW | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage DC Input # | Inverter | GMS_MAP_DNP.INV001_Voltage_DC_Input# | Voltage DC Input # |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage DC Positive To Ground | Inverter | GMS_MAP_DNP.INV001_Voltage_DC_Input | Voltage DC Input | 978 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage DC Negative To Ground | Inverter | GMS_MAP_DNP.INV001_Voltage_DC_Input | Voltage DC Input | 979 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current Ground | Inverter | GMS_MAP_DNP.INV001_Current_Ground | Current Ground |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current-AC | Inverter | GMS_MAP_DNP.INV001_Current_AC | Current-AC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Current-DC | Inverter | GMS_MAP_DNP.INV001_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Daily Energy Delivered | Inverter | GMS_MAP_DNP.INV001_Daily_Energy_Delivered | Daily Energy Delivered | 980 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power Set Point | Inverter | GMS_MAP_DNP.INV001_real_Power_Set_Point | Real Power Set Point | 981 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Reactive Power Set Point | Inverter | GMS_MAP_DNP.INV001_Reactive_Power_Set_Point | Reactive Power Set Point | 982 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Frequency | Inverter | GMS_MAP_DNP.INV001_Frequency | Frequency | 983 | Hz | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_IGBT Current | Inverter | GMS_MAP_DNP.INV001_IGBT_Current | IGBT Current |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Insulation Resistance | Inverter | GMS_MAP_DNP.INV001_Insulation_Resistance | Insulation Resistance | 984 | Ω | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Isolation Measure Timeout | Inverter | GMS_MAP_DNP.INV001_Isolation_Measure_Timeout | Isolation Measure Timeout |  | V | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Maximum DC Voltage | Inverter | GMS_MAP_DNP.INV001_Maximum_DC_Voltage | Maximum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Minimum DC Voltage | Inverter | GMS_MAP_DNP.INV001_Minimum_DC_Voltage | Minimum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Number of DU Channels | Inverter | GMS_MAP_DNP.INV001_Number_Of_DU_Channels | Number of DU Channels |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Number of Running Modules | Inverter | GMS_MAP_DNP.INV001_Number_Of_Running_Modules | Number of Running Modules |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Operating State | Inverter | GMS_MAP_DNP.INV001_Operating_State | Operating State |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Power Factor | Inverter | GMS_MAP_DNP.INV001_Power_Factor | Power Factor | 985 | Unitless | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Ramp Down | Inverter | GMS_MAP_DNP.INV001_Ramp_Down | Ramp Down |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Ramp Rate | Inverter | GMS_MAP_DNP.INV001_Ramp_Rate | Ramp Rate |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Ramp Up | Inverter | GMS_MAP_DNP.INV001_Ramp_Up | Ramp Up |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power Delivered | Inverter | GMS_MAP_DNP.INV001_Real Power_Delivered | Real Power Delivered | 986 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Reactive Power Delivered | Inverter | GMS_MAP_DNP.INV001_Reactive Power_Delivered | Reactive Power Delivered | 987 | kVARh | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power | Inverter | GMS_MAP_DNP.INV001_Real_Power | Real Power | 988 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Reactive Power | Inverter | GMS_MAP_DNP.INV001_Reactive_Power | Reactive Power | 989 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Reactive Power Mode | Inverter | GMS_MAP_DNP.INV001_Reactive_Power_Mode | Reactive Power Mode | 990 | # | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Reactive Power Set Point Percent | Inverter | GMS_MAP_DNP.INV001_Reactive_Power_Set_Point_Percent | Reactive Power Set Point Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power AC Percent | Inverter | GMS_MAP_DNP.INV001_Real_Power_AC_Percent | Real Power AC Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power-AC | Inverter | GMS_MAP_DNP.INV001_Real_Power_AC | Real Power-AC | 991 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power-DC | Inverter | GMS_MAP_DNP.INV001_Real_Power_DC | Real Power-DC | 992 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Air Intake | Inverter | GMS_MAP_DNP.INV001_Temperature_Air_Intake | Temperature-Air Intake |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Ambient | Inverter | GMS_MAP_DNP.INV001_Temperature_Ambient | Temperature-Ambient | 993 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Cabinet | Inverter | GMS_MAP_DNP.INV001_Temperature_Cabinet | Temperature-Cabinet | 994 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Combiner Box | Inverter | GMS_MAP_DNP.INV001_Temperature_Combiner Box | Temperature-Combiner Box |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Coolant | Inverter | GMS_MAP_DNP.INV001_Temperature_Coolant | Temperature-Coolant |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Filter Choke | Inverter | GMS_MAP_DNP.INV001_Temperature_Filter Choke | Temperature-Filter Choke |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-IGBT Heat Sink | Inverter | GMS_MAP_DNP.INV001_Temperature_IGBT Heat Sink | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Temperature-Module | Inverter | GMS_MAP_DNP.INV001_Temperature_Module | Temperature-Module |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Humidity Cabinet | Inverter | GMS_MAP_DNP.INV001_Humidity Cabinet | Humidity Cabinet | 995 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Uptime | Inverter | GMS_MAP_DNP.INV001_Uptime | Uptime |  | seconds | Requested-Not Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage A-B | Inverter | GMS_MAP_DNP.INV001_Voltage_A_B | Voltage A-B | 996 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage A-N | Inverter | GMS_MAP_DNP.INV001_Voltage_A_N | Voltage A-N | 997 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage B-C | Inverter | GMS_MAP_DNP.INV001_Voltage_B_C | Voltage B-C | 998 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage B-N | Inverter | GMS_MAP_DNP.INV001_Voltage_B_N | Voltage B-N | 999 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage C-A | Inverter | GMS_MAP_DNP.INV001_Voltage_C_A | Voltage C-A | 1000 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage C-N | Inverter | GMS_MAP_DNP.INV001_Voltage_C_N | Voltage C-N | 1001 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 1 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_1 | Status Bit Word 1 | 1002 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 2 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_2 | Status Bit Word 2 | 1003 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 3 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_3 | Status Bit Word 3 | 1004 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 4 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_4 | Status Bit Word 4 | 1005 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 5 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_5 | Status Bit Word 5 | 1006 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 6 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_6 | Status Bit Word 6 | 1007 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 7 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_7 | Status Bit Word 7 | 1008 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 8 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_8 | Status Bit Word 8 | 1009 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001_Status Bit Word 9 | Inverter | GMS_MAP_DNP.INV001_Status_Bit_Word_9 | Status Bit Word 9 | 1010 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001 | TSN1_SUB1_INV001 Module 1_Status Bit Word | Inverter | GMS_MAP_DNP.INV001_Module_1_Status_Bit_Word | Status Bit Word | 1011 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_01_Reactive_Power_Mode | Reactive Power Mode | 1012 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_01_A_Phase_Current | A Phase Current | 1013 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_01_B_Phase_Current | B Phase Current | 1014 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_01_C_Phase_Current | C Phase Current | 1015 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_01_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_01_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_01_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_01_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_IO Status | Inverter Module | GMS_MAP_DNP.INV001_01_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Module Status | Inverter Module | GMS_MAP_DNP.INV001_01_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Operating State | Inverter Module | GMS_MAP_DNP.INV001_01_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_01_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_01_Reactive_Power | Reactive Power | 1016 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_01_Real_Power | Real Power-AC | 1017 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_01_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_01_Voltage_DC | Voltage DC Bus | 1018 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_01_Voltage DC N | Voltage DC N | 1019 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_1_Voltage DC P | Voltage DC P | 1020 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001_01_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input1 | Current DC Input1 | 1021 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Inp_ut2_ | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input2 | Current DC Input2 | 1022 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input3 | Current DC Input3 | 1023 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input4 | Current DC Input4 | 1024 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input5 | Current DC Input5 | 1025 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input6 | Current DC Input6 | 1026 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input7 | Current DC Input7 | 1027 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_01_Current_DC_Input8 | Current DC Input8 | 1028 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_01_Power Command FB | Power Command FB | 1029 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_01_Power Setpoint FB | Power Setpoint FB | 1030 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_01_Reactive_Reactive Command FB | React Command FB | 1031 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_01_Reactive Setpoint FB | Reactive Setpoint FB | 1032 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_01_Real_Power_DC | Real Power-DC | 1033 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-01 | TSN1_SUB1_INV001-01_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1034 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV001_02_Status_Bit_Word | Status Bit Word | 1035 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_02_Reactive_Power_Mode | Reactive Power Mode | 1036 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_02_A_Phase_Current | A Phase Current | 1037 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_02_B_Phase_Current | B Phase Current | 1038 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_02_C_Phase_Current | C Phase Current | 1039 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_02_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_02_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_02_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_02_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_IO Status | Inverter Module | GMS_MAP_DNP.INV001_02_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Module Status | Inverter Module | GMS_MAP_DNP.INV001_02_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Operating State | Inverter Module | GMS_MAP_DNP.INV001_02_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_02_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_02_Reactive_Power | Reactive Power | 1040 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_02_Real_Power | Real Power-AC | 1041 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_02_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_02_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_02_Voltage_DC | Voltage DC Bus | 1042 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_02_Voltage DC N | Voltage DC N | 1043 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_2_Voltage DC P | Voltage DC P | 1044 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input1 | Current DC Input1 | 1045 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input2 | Current DC Input2 | 1046 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input3 | Current DC Input3 | 1047 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input4 | Current DC Input4 | 1048 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input5 | Current DC Input5 | 1049 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input6 | Current DC Input6 | 1050 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input7 | Current DC Input7 | 1051 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_02_Current_DC_Input8 | Current DC Input8 | 1052 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_02_Power Command FB | Power Command FB | 1053 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_02_Power Setpoint FB | Power Setpoint FB | 1054 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_02_Reactive_Reactive Command FB | React Command FB | 1055 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_02_Reactive Setpoint FB | Reactive Setpoint FB | 1056 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_02_Real_Power_DC | Real Power-DC | 1057 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-02 | TSN1_SUB1_INV001-02_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1058 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV001_03_Status_Bit_Word | Status Bit Word | 1059 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_03_Reactive_Power_Mode | Reactive Power Mode | 1060 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_03_A_Phase_Current | A Phase Current | 1061 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_03_B_Phase_Current | B Phase Current | 1062 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_03_C_Phase_Current | C Phase Current | 1063 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_03_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_03_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_03_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_03_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_IO Status | Inverter Module | GMS_MAP_DNP.INV001_03_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Module Status | Inverter Module | GMS_MAP_DNP.INV001_03_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Operating State | Inverter Module | GMS_MAP_DNP.INV001_03_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_03_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_03_Reactive_Power | Reactive Power | 1064 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_03_Real_Power | Real Power-AC | 1065 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_03_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_03_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_03Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_03Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_03_Voltage_DC | Voltage DC Bus | 1066 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_03_Voltage DC N | Voltage DC N | 1067 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_3_Voltage DC P | Voltage DC P | 1068 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input1 | Current DC Input1 | 1069 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input2 | Current DC Input2 | 1070 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input3 | Current DC Input3 | 1071 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input4 | Current DC Input4 | 1072 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input5 | Current DC Input5 | 1073 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input6 | Current DC Input6 | 1074 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input7 | Current DC Input7 | 1075 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_03_Current_DC_Input8 | Current DC Input8 | 1076 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_03_Power Command FB | Power Command FB | 1077 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_03_Power Setpoint FB | Power Setpoint FB | 1078 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_03_Reactive_Reactive Command FB | React Command FB | 1079 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_03_Reactive Setpoint FB | Reactive Setpoint FB | 1080 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_03_Real_Power_DC | Real Power-DC | 1081 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-03 | TSN1_SUB1_INV001-03_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1082 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV001_04_Status_Bit_Word | Status Bit Word | 1083 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_04_Reactive_Power_Mode | Reactive Power Mode | 1084 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_04_A_Phase_Current | A Phase Current | 1085 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_04_B_Phase_Current | B Phase Current | 1086 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_04_C_Phase_Current | C Phase Current | 1087 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_04_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_04_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_04_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_04_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_IO Status | Inverter Module | GMS_MAP_DNP.INV001_04_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Module Status | Inverter Module | GMS_MAP_DNP.INV001_04_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Operating State | Inverter Module | GMS_MAP_DNP.INV001_04_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_04_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_04_Reactive_Power | Reactive Power | 1088 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_04_Real_Power | Real Power-AC | 1089 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_04_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_04_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_04_Voltage_DC | Voltage DC Bus | 1090 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_04_Voltage DC N | Voltage DC N | 1091 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_4_Voltage DC P | Voltage DC P | 1092 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input1 | Current DC Input1 | 1093 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input2 | Current DC Input2 | 1094 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input3 | Current DC Input3 | 1095 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input4 | Current DC Input4 | 1096 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input5 | Current DC Input5 | 1097 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input6 | Current DC Input6 | 1098 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input7 | Current DC Input7 | 1099 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_04_Current_DC_Input8 | Current DC Input8 | 1100 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_04_Power Command FB | Power Command FB | 1101 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_04_Power Setpoint FB | Power Setpoint FB | 1102 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_04_Reactive_Reactive Command FB | React Command FB | 1103 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_04_Reactive Setpoint FB | Reactive Setpoint FB | 1104 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_04_Real_Power_DC | Real Power-DC | 1105 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-04 | TSN1_SUB1_INV001-04_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1106 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV001_05_Status_Bit_Word | Status Bit Word | 1107 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_05_Reactive_Power_Mode | Reactive Power Mode | 1108 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_05_A_Phase_Current | A Phase Current | 1109 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_05_B_Phase_Current | B Phase Current | 1110 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_05_C_Phase_Current | C Phase Current | 1111 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_05_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_05_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_05_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_05_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_IO Status | Inverter Module | GMS_MAP_DNP.INV001_05_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Module Status | Inverter Module | GMS_MAP_DNP.INV001_05_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Operating State | Inverter Module | GMS_MAP_DNP.INV001_05_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_05_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_05_Reactive_Power | Reactive Power | 1112 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_05_Real_Power | Real Power-AC | 1113 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_05_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_05_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_05_Voltage_DC | Voltage DC Bus | 1114 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_05_Voltage DC N | Voltage DC N | 1115 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_5_Voltage DC P | Voltage DC P | 1116 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input1 | Current DC Input1 | 1117 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input2 | Current DC Input2 | 1118 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input3 | Current DC Input3 | 1119 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input4 | Current DC Input4 | 1120 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input5 | Current DC Input5 | 1121 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input6 | Current DC Input6 | 1122 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input7 | Current DC Input7 | 1123 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_05_Current_DC_Input8 | Current DC Input8 | 1124 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_05_Power Command FB | Power Command FB | 1125 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_05_Power Setpoint FB | Power Setpoint FB | 1126 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_05_Reactive_Reactive Command FB | React Command FB | 1127 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_05_Reactive Setpoint FB | Reactive Setpoint FB | 1128 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_05_Real_Power_DC | Real Power-DC | 1129 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-05 | TSN1_SUB1_INV001-05_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1130 | °C | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV001_06_Status_Bit_Word | Status Bit Word | 1131 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV001_06_Reactive_Power_Mode | Reactive Power Mode | 1132 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_A Phase Current | Inverter Module | GMS_MAP_DNP.INV001_06_A_Phase_Current | A Phase Current | 1133 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_B Phase Current | Inverter Module | GMS_MAP_DNP.INV001_06_B_Phase_Current | B Phase Current | 1134 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_C Phase Current | Inverter Module | GMS_MAP_DNP.INV001_06_C_Phase_Current | C Phase Current | 1135 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current-DC | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV001_06_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Firmware version | Inverter Module | GMS_MAP_DNP.INV001_06_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Hardware version | Inverter Module | GMS_MAP_DNP.INV001_06_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Inverter Name | Inverter Module | GMS_MAP_DNP.INV001_06_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_IO Status | Inverter Module | GMS_MAP_DNP.INV001_06_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Module Status | Inverter Module | GMS_MAP_DNP.INV001_06_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Operating State | Inverter Module | GMS_MAP_DNP.INV001_06_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV001_06_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Reactive Power | Inverter Module | GMS_MAP_DNP.INV001_06_Reactive_Power | Reactive Power | 1136 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV001_06_Real_Power | Real Power-AC | 1137 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV001_06_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV001_06_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV001_06Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV001_06Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV001_06_Voltage_DC | Voltage DC Bus | 1138 | kV | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV001_06_Voltage DC N | Voltage DC N | 1139 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV001_ Module_6_Voltage DC P | Voltage DC P | 1140 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input1 | Current DC Input1 | 1141 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input2 | Current DC Input2 | 1142 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input3 | Current DC Input3 | 1143 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input4 | Current DC Input4 | 1144 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input5 | Current DC Input5 | 1145 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input6 | Current DC Input6 | 1146 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input7 | Current DC Input7 | 1147 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV001_06_Current_DC_Input8 | Current DC Input8 | 1148 | A | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Power Command FB | Inverter Module | GMS_MAP_DNP.INV001_06_Power Command FB | Power Command FB | 1149 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_06_Power Setpoint FB | Power Setpoint FB | 1150 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_React Command FB | Inverter Module | GMS_MAP_DNP.INV001_06_Reactive_Reactive Command FB | React Command FB | 1151 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV001_06_Reactive Setpoint FB | Reactive Setpoint FB | 1152 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV001_06_Real_Power_DC | Real Power-DC | 1153 | kW | Requested-Available | -32767 | 32767
SUB1 | INV001-06 | TSN1_SUB1_INV001-06_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV001_01_Temperature_Ambient | Temperature-Ambient | 1154 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_A Phase Current | Inverter | GMS_MAP_DNP.INV002_A_Phase_Current | A Phase Current | 1155 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_B Phase Current | Inverter | GMS_MAP_DNP.INV002_B_Phase_Current | B Phase Current | 1156 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_C Phase Current | Inverter | GMS_MAP_DNP.INV002_C_Phase_Current | C Phase Current | 1157 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Bus Voltage | Inverter | GMS_MAP_DNP.INV002_Bus_Voltage_AB | Bus Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Apparent Power | Inverter | GMS_MAP_DNP.INV002_Apparent_Power | Apparent Power |  | kVA | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Common Mode Voltage | Inverter | GMS_MAP_DNP.INV002_Common_Mode_Voltage | Common Mode Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input1 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input1 | Current DC Input# | 1158 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input2 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input2 | Current DC Input# | 1159 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input3 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input3 | Current DC Input# | 1160 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input4 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input4 | Current DC Input# | 1161 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input5 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input5 | Current DC Input# | 1162 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current DC Input6 | Inverter | GMS_MAP_DNP.INV002_Current_DC_Input6 | Current DC Input# | 1163 | A | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power DC Input # | Inverter | GMS_MAP_DNP.INV002_Real Power_DC_Input# | Real Power DC Input # |  | KW | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage DC Input # | Inverter | GMS_MAP_DNP.INV002_Voltage_DC_Input# | Voltage DC Input # |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage DC Positive To Ground | Inverter | GMS_MAP_DNP.INV002_Voltage_DC_Input | Voltage DC Input | 1164 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage DC Negative To Ground | Inverter | GMS_MAP_DNP.INV002_Voltage_DC_Input | Voltage DC Input | 1165 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current Ground | Inverter | GMS_MAP_DNP.INV002_Current_Ground | Current Ground |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current-AC | Inverter | GMS_MAP_DNP.INV002_Current_AC | Current-AC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Current-DC | Inverter | GMS_MAP_DNP.INV002_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Daily Energy Delivered | Inverter | GMS_MAP_DNP.INV002_Daily_Energy_Delivered | Daily Energy Delivered | 1166 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power Set Point | Inverter | GMS_MAP_DNP.INV002_real_Power_Set_Point | Real Power Set Point | 1167 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Reactive Power Set Point | Inverter | GMS_MAP_DNP.INV002_Reactive_Power_Set_Point | Reactive Power Set Point | 1168 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Frequency | Inverter | GMS_MAP_DNP.INV002_Frequency | Frequency | 1169 | Hz | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_IGBT Current | Inverter | GMS_MAP_DNP.INV002_IGBT_Current | IGBT Current |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Insulation Resistance | Inverter | GMS_MAP_DNP.INV002_Insulation_Resistance | Insulation Resistance | 1170 | Ω | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Isolation Measure Timeout | Inverter | GMS_MAP_DNP.INV002_Isolation_Measure_Timeout | Isolation Measure Timeout |  | V | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Maximum DC Voltage | Inverter | GMS_MAP_DNP.INV002_Maximum_DC_Voltage | Maximum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Minimum DC Voltage | Inverter | GMS_MAP_DNP.INV002_Minimum_DC_Voltage | Minimum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Number of DU Channels | Inverter | GMS_MAP_DNP.INV002_Number_Of_DU_Channels | Number of DU Channels |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Number of Running Modules | Inverter | GMS_MAP_DNP.INV002_Number_Of_Running_Modules | Number of Running Modules |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Operating State | Inverter | GMS_MAP_DNP.INV002_Operating_State | Operating State |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Power Factor | Inverter | GMS_MAP_DNP.INV002_Power_Factor | Power Factor | 1171 | Unitless | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Ramp Down | Inverter | GMS_MAP_DNP.INV002_Ramp_Down | Ramp Down |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Ramp Rate | Inverter | GMS_MAP_DNP.INV002_Ramp_Rate | Ramp Rate |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Ramp Up | Inverter | GMS_MAP_DNP.INV002_Ramp_Up | Ramp Up |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power Delivered | Inverter | GMS_MAP_DNP.INV002_Real Power_Delivered | Real Power Delivered | 1172 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Reactive Power Delivered | Inverter | GMS_MAP_DNP.INV002_Reactive Power_Delivered | Reactive Power Delivered | 1173 | kVARh | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power | Inverter | GMS_MAP_DNP.INV002_Real_Power | Real Power | 1174 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Reactive Power | Inverter | GMS_MAP_DNP.INV002_Reactive_Power | Reactive Power | 1175 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Reactive Power Mode | Inverter | GMS_MAP_DNP.INV002_Reactive_Power_Mode | Reactive Power Mode | 1176 | # | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Reactive Power Set Point Percent | Inverter | GMS_MAP_DNP.INV002_Reactive_Power_Set_Point_Percent | Reactive Power Set Point Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power AC Percent | Inverter | GMS_MAP_DNP.INV002_Real_Power_AC_Percent | Real Power AC Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power-AC | Inverter | GMS_MAP_DNP.INV002_Real_Power_AC | Real Power-AC | 1177 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power-DC | Inverter | GMS_MAP_DNP.INV002_Real_Power_DC | Real Power-DC | 1178 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Air Intake | Inverter | GMS_MAP_DNP.INV002_Temperature_Air_Intake | Temperature-Air Intake |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Ambient | Inverter | GMS_MAP_DNP.INV002_Temperature_Ambient | Temperature-Ambient | 1179 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Cabinet | Inverter | GMS_MAP_DNP.INV002_Temperature_Cabinet | Temperature-Cabinet | 1180 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Combiner Box | Inverter | GMS_MAP_DNP.INV002_Temperature_Combiner Box | Temperature-Combiner Box |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Coolant | Inverter | GMS_MAP_DNP.INV002_Temperature_Coolant | Temperature-Coolant |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Filter Choke | Inverter | GMS_MAP_DNP.INV002_Temperature_Filter Choke | Temperature-Filter Choke |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-IGBT Heat Sink | Inverter | GMS_MAP_DNP.INV002_Temperature_IGBT Heat Sink | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Temperature-Module | Inverter | GMS_MAP_DNP.INV002_Temperature_Module | Temperature-Module |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Humidity Cabinet | Inverter | GMS_MAP_DNP.INV002_Humidity Cabinet | Humidity Cabinet | 1181 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Uptime | Inverter | GMS_MAP_DNP.INV002_Uptime | Uptime |  | seconds | Requested-Not Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage A-B | Inverter | GMS_MAP_DNP.INV002_Voltage_A_B | Voltage A-B | 1182 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage A-N | Inverter | GMS_MAP_DNP.INV002_Voltage_A_N | Voltage A-N | 1183 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage B-C | Inverter | GMS_MAP_DNP.INV002_Voltage_B_C | Voltage B-C | 1184 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage B-N | Inverter | GMS_MAP_DNP.INV002_Voltage_B_N | Voltage B-N | 1185 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage C-A | Inverter | GMS_MAP_DNP.INV002_Voltage_C_A | Voltage C-A | 1186 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage C-N | Inverter | GMS_MAP_DNP.INV002_Voltage_C_N | Voltage C-N | 1187 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 1 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_1 | Status Bit Word 1 | 1188 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 2 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_2 | Status Bit Word 2 | 1189 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 3 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_3 | Status Bit Word 3 | 1190 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 4 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_4 | Status Bit Word 4 | 1191 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 5 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_5 | Status Bit Word 5 | 1192 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 6 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_6 | Status Bit Word 6 | 1193 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 7 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_7 | Status Bit Word 7 | 1194 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 8 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_8 | Status Bit Word 8 | 1195 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002_Status Bit Word 9 | Inverter | GMS_MAP_DNP.INV002_Status_Bit_Word_9 | Status Bit Word 9 | 1196 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002 | TSN1_SUB1_INV002 Module 1_Status Bit Word | Inverter | GMS_MAP_DNP.INV002_Module_1_Status_Bit_Word | Status Bit Word | 1197 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_01_Reactive_Power_Mode | Reactive Power Mode | 1198 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_01_A_Phase_Current | A Phase Current | 1199 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_01_B_Phase_Current | B Phase Current | 1200 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_01_C_Phase_Current | C Phase Current | 1201 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_01_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_01_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_01_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_01_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_IO Status | Inverter Module | GMS_MAP_DNP.INV002_01_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Module Status | Inverter Module | GMS_MAP_DNP.INV002_01_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Operating State | Inverter Module | GMS_MAP_DNP.INV002_01_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_01_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_01_Reactive_Power | Reactive Power | 1202 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_01_Real_Power | Real Power-AC | 1203 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_01_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_01_Voltage_DC | Voltage DC Bus | 1204 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_01_Voltage DC N | Voltage DC N | 1205 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_1_Voltage DC P | Voltage DC P | 1206 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input1 | Current DC Input1 | 1207 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input2 | Current DC Input2 | 1208 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input3 | Current DC Input3 | 1209 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input4 | Current DC Input4 | 1210 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input5 | Current DC Input5 | 1211 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input6 | Current DC Input6 | 1212 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input7 | Current DC Input7 | 1213 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_01_Current_DC_Input8 | Current DC Input8 | 1214 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_01_Power Command FB | Power Command FB | 1215 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_01_Power Setpoint FB | Power Setpoint FB | 1216 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_01_Reactive_Reactive Command FB | React Command FB | 1217 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_01_Reactive Setpoint FB | Reactive Setpoint FB | 1218 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_01_Real_Power_DC | Real Power-DC | 1219 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-01 | TSN1_SUB1_INV002-01_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1220 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV002_02_Status_Bit_Word | Status Bit Word | 1221 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_02_Reactive_Power_Mode | Reactive Power Mode | 1222 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_02_A_Phase_Current | A Phase Current | 1223 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_02_B_Phase_Current | B Phase Current | 1224 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_02_C_Phase_Current | C Phase Current | 1225 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_02_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_02_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_02_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_02_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_IO Status | Inverter Module | GMS_MAP_DNP.INV002_02_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Module Status | Inverter Module | GMS_MAP_DNP.INV002_02_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Operating State | Inverter Module | GMS_MAP_DNP.INV002_02_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_02_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_02_Reactive_Power | Reactive Power | 1226 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_02_Real_Power | Real Power-AC | 1227 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_02_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_02_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_02_Voltage_DC | Voltage DC Bus | 1228 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_02_Voltage DC N | Voltage DC N | 1229 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_2_Voltage DC P | Voltage DC P | 1230 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input1 | Current DC Input1 | 1231 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input2 | Current DC Input2 | 1232 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input3 | Current DC Input3 | 1233 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input4 | Current DC Input4 | 1234 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input5 | Current DC Input5 | 1235 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input6 | Current DC Input6 | 1236 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input7 | Current DC Input7 | 1237 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_02_Current_DC_Input8 | Current DC Input8 | 1238 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_02_Power Command FB | Power Command FB | 1239 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_02_Power Setpoint FB | Power Setpoint FB | 1240 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_02_Reactive_Reactive Command FB | React Command FB | 1241 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_02_Reactive Setpoint FB | Reactive Setpoint FB | 1242 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_02_Real_Power_DC | Real Power-DC | 1243 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-02 | TSN1_SUB1_INV002-02_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1244 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV002_03_Status_Bit_Word | Status Bit Word | 1245 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_03_Reactive_Power_Mode | Reactive Power Mode | 1246 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_03_A_Phase_Current | A Phase Current | 1247 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_03_B_Phase_Current | B Phase Current | 1248 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_03_C_Phase_Current | C Phase Current | 1249 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_03_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_03_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_03_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_03_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_IO Status | Inverter Module | GMS_MAP_DNP.INV002_03_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Module Status | Inverter Module | GMS_MAP_DNP.INV002_03_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Operating State | Inverter Module | GMS_MAP_DNP.INV002_03_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_03_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_03_Reactive_Power | Reactive Power | 1250 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_03_Real_Power | Real Power-AC | 1251 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_03_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_03_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_03Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_03Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_03_Voltage_DC | Voltage DC Bus | 1252 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_03_Voltage DC N | Voltage DC N | 1253 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_3_Voltage DC P | Voltage DC P | 1254 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input1 | Current DC Input1 | 1255 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input2 | Current DC Input2 | 1256 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input3 | Current DC Input3 | 1257 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input4 | Current DC Input4 | 1258 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input5 | Current DC Input5 | 1259 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input6 | Current DC Input6 | 1260 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input7 | Current DC Input7 | 1261 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_03_Current_DC_Input8 | Current DC Input8 | 1262 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_03_Power Command FB | Power Command FB | 1263 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_03_Power Setpoint FB | Power Setpoint FB | 1264 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_03_Reactive_Reactive Command FB | React Command FB | 1265 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_03_Reactive Setpoint FB | Reactive Setpoint FB | 1266 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_03_Real_Power_DC | Real Power-DC | 1267 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-03 | TSN1_SUB1_INV002-03_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1268 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV002_04_Status_Bit_Word | Status Bit Word | 1269 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_04_Reactive_Power_Mode | Reactive Power Mode | 1270 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_04_A_Phase_Current | A Phase Current | 1271 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_04_B_Phase_Current | B Phase Current | 1272 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_04_C_Phase_Current | C Phase Current | 1273 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_04_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_04_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_04_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_04_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_IO Status | Inverter Module | GMS_MAP_DNP.INV002_04_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Module Status | Inverter Module | GMS_MAP_DNP.INV002_04_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Operating State | Inverter Module | GMS_MAP_DNP.INV002_04_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_04_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_04_Reactive_Power | Reactive Power | 1274 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_04_Real_Power | Real Power-AC | 1275 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_04_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_04_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_04_Voltage_DC | Voltage DC Bus | 1276 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_04_Voltage DC N | Voltage DC N | 1277 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_4_Voltage DC P | Voltage DC P | 1278 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input1 | Current DC Input1 | 1279 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input2 | Current DC Input2 | 1280 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input3 | Current DC Input3 | 1281 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input4 | Current DC Input4 | 1282 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input5 | Current DC Input5 | 1283 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input6 | Current DC Input6 | 1284 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input7 | Current DC Input7 | 1285 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_04_Current_DC_Input8 | Current DC Input8 | 1286 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_04_Power Command FB | Power Command FB | 1287 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_04_Power Setpoint FB | Power Setpoint FB | 1288 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_04_Reactive_Reactive Command FB | React Command FB | 1289 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_04_Reactive Setpoint FB | Reactive Setpoint FB | 1290 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_04_Real_Power_DC | Real Power-DC | 1291 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-04 | TSN1_SUB1_INV002-04_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1292 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV002_05_Status_Bit_Word | Status Bit Word | 1293 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_05_Reactive_Power_Mode | Reactive Power Mode | 1294 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_05_A_Phase_Current | A Phase Current | 1295 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_05_B_Phase_Current | B Phase Current | 1296 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_05_C_Phase_Current | C Phase Current | 1297 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_05_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_05_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_05_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_05_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_IO Status | Inverter Module | GMS_MAP_DNP.INV002_05_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Module Status | Inverter Module | GMS_MAP_DNP.INV002_05_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Operating State | Inverter Module | GMS_MAP_DNP.INV002_05_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_05_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_05_Reactive_Power | Reactive Power | 1298 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_05_Real_Power | Real Power-AC | 1299 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_05_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_05_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_05_Voltage_DC | Voltage DC Bus | 1300 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_05_Voltage DC N | Voltage DC N | 1301 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_5_Voltage DC P | Voltage DC P | 1302 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input1 | Current DC Input1 | 1303 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input2 | Current DC Input2 | 1304 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input3 | Current DC Input3 | 1305 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input4 | Current DC Input4 | 1306 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input5 | Current DC Input5 | 1307 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input6 | Current DC Input6 | 1308 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input7 | Current DC Input7 | 1309 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_05_Current_DC_Input8 | Current DC Input8 | 1310 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_05_Power Command FB | Power Command FB | 1311 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_05_Power Setpoint FB | Power Setpoint FB | 1312 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_05_Reactive_Reactive Command FB | React Command FB | 1313 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_05_Reactive Setpoint FB | Reactive Setpoint FB | 1314 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_05_Real_Power_DC | Real Power-DC | 1315 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-05 | TSN1_SUB1_INV002-05_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1316 | °C | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV002_06_Status_Bit_Word | Status Bit Word | 1317 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV002_06_Reactive_Power_Mode | Reactive Power Mode | 1318 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_A Phase Current | Inverter Module | GMS_MAP_DNP.INV002_06_A_Phase_Current | A Phase Current | 1319 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_B Phase Current | Inverter Module | GMS_MAP_DNP.INV002_06_B_Phase_Current | B Phase Current | 1320 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_C Phase Current | Inverter Module | GMS_MAP_DNP.INV002_06_C_Phase_Current | C Phase Current | 1321 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current-DC | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV002_06_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Firmware version | Inverter Module | GMS_MAP_DNP.INV002_06_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Hardware version | Inverter Module | GMS_MAP_DNP.INV002_06_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Inverter Name | Inverter Module | GMS_MAP_DNP.INV002_06_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_IO Status | Inverter Module | GMS_MAP_DNP.INV002_06_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Module Status | Inverter Module | GMS_MAP_DNP.INV002_06_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Operating State | Inverter Module | GMS_MAP_DNP.INV002_06_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV002_06_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Reactive Power | Inverter Module | GMS_MAP_DNP.INV002_06_Reactive_Power | Reactive Power | 1322 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV002_06_Real_Power | Real Power-AC | 1323 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV002_06_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV002_06_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV002_06Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV002_06Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV002_06_Voltage_DC | Voltage DC Bus | 1324 | kV | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV002_06_Voltage DC N | Voltage DC N | 1325 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV002_ Module_6_Voltage DC P | Voltage DC P | 1326 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input1 | Current DC Input1 | 1327 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input2 | Current DC Input2 | 1328 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input3 | Current DC Input3 | 1329 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input4 | Current DC Input4 | 1330 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input5 | Current DC Input5 | 1331 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input6 | Current DC Input6 | 1332 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input7 | Current DC Input7 | 1333 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV002_06_Current_DC_Input8 | Current DC Input8 | 1334 | A | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Power Command FB | Inverter Module | GMS_MAP_DNP.INV002_06_Power Command FB | Power Command FB | 1335 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_06_Power Setpoint FB | Power Setpoint FB | 1336 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_React Command FB | Inverter Module | GMS_MAP_DNP.INV002_06_Reactive_Reactive Command FB | React Command FB | 1337 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV002_06_Reactive Setpoint FB | Reactive Setpoint FB | 1338 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV002_06_Real_Power_DC | Real Power-DC | 1339 | kW | Requested-Available | -32767 | 32767
SUB1 | INV002-06 | TSN1_SUB1_INV002-06_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV002_01_Temperature_Ambient | Temperature-Ambient | 1340 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_A Phase Current | Inverter | GMS_MAP_DNP.INV003_A_Phase_Current | A Phase Current | 1341 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_B Phase Current | Inverter | GMS_MAP_DNP.INV003_B_Phase_Current | B Phase Current | 1342 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_C Phase Current | Inverter | GMS_MAP_DNP.INV003_C_Phase_Current | C Phase Current | 1343 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Bus Voltage | Inverter | GMS_MAP_DNP.INV003_Bus_Voltage_AB | Bus Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Apparent Power | Inverter | GMS_MAP_DNP.INV003_Apparent_Power | Apparent Power |  | kVA | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Common Mode Voltage | Inverter | GMS_MAP_DNP.INV003_Common_Mode_Voltage | Common Mode Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input1 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input1 | Current DC Input# | 1344 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input2 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input2 | Current DC Input# | 1345 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input3 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input3 | Current DC Input# | 1346 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input4 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input4 | Current DC Input# | 1347 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input5 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input5 | Current DC Input# | 1348 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current DC Input6 | Inverter | GMS_MAP_DNP.INV003_Current_DC_Input6 | Current DC Input# | 1349 | A | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power DC Input # | Inverter | GMS_MAP_DNP.INV003_Real Power_DC_Input# | Real Power DC Input # |  | KW | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage DC Input # | Inverter | GMS_MAP_DNP.INV003_Voltage_DC_Input# | Voltage DC Input # |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage DC Positive To Ground | Inverter | GMS_MAP_DNP.INV003_Voltage_DC_Input | Voltage DC Input | 1350 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage DC Negative To Ground | Inverter | GMS_MAP_DNP.INV003_Voltage_DC_Input | Voltage DC Input | 1351 | V | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current Ground | Inverter | GMS_MAP_DNP.INV003_Current_Ground | Current Ground |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current-AC | Inverter | GMS_MAP_DNP.INV003_Current_AC | Current-AC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Current-DC | Inverter | GMS_MAP_DNP.INV003_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Daily Energy Delivered | Inverter | GMS_MAP_DNP.INV003_Daily_Energy_Delivered | Daily Energy Delivered | 1352 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power Set Point | Inverter | GMS_MAP_DNP.INV003_real_Power_Set_Point | Real Power Set Point | 1353 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Reactive Power Set Point | Inverter | GMS_MAP_DNP.INV003_Reactive_Power_Set_Point | Reactive Power Set Point | 1354 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Frequency | Inverter | GMS_MAP_DNP.INV003_Frequency | Frequency | 1355 | Hz | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_IGBT Current | Inverter | GMS_MAP_DNP.INV003_IGBT_Current | IGBT Current |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Insulation Resistance | Inverter | GMS_MAP_DNP.INV003_Insulation_Resistance | Insulation Resistance | 1356 | Ω | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Isolation Measure Timeout | Inverter | GMS_MAP_DNP.INV003_Isolation_Measure_Timeout | Isolation Measure Timeout |  | V | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Maximum DC Voltage | Inverter | GMS_MAP_DNP.INV003_Maximum_DC_Voltage | Maximum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Minimum DC Voltage | Inverter | GMS_MAP_DNP.INV003_Minimum_DC_Voltage | Minimum DC Voltage |  | kV | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Number of DU Channels | Inverter | GMS_MAP_DNP.INV003_Number_Of_DU_Channels | Number of DU Channels |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Number of Running Modules | Inverter | GMS_MAP_DNP.INV003_Number_Of_Running_Modules | Number of Running Modules |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Operating State | Inverter | GMS_MAP_DNP.INV003_Operating_State | Operating State |  | # | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Power Factor | Inverter | GMS_MAP_DNP.INV003_Power_Factor | Power Factor | 1357 | Unitless | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Ramp Down | Inverter | GMS_MAP_DNP.INV003_Ramp_Down | Ramp Down |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Ramp Rate | Inverter | GMS_MAP_DNP.INV003_Ramp_Rate | Ramp Rate |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Ramp Up | Inverter | GMS_MAP_DNP.INV003_Ramp_Up | Ramp Up |  | MW/sec | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power Delivered | Inverter | GMS_MAP_DNP.INV003_Real Power_Delivered | Real Power Delivered | 1358 | kWh | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Reactive Power Delivered | Inverter | GMS_MAP_DNP.INV003_Reactive Power_Delivered | Reactive Power Delivered | 1359 | kVARh | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power | Inverter | GMS_MAP_DNP.INV003_Real_Power | Real Power | 1360 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Reactive Power | Inverter | GMS_MAP_DNP.INV003_Reactive_Power | Reactive Power | 1361 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Reactive Power Mode | Inverter | GMS_MAP_DNP.INV003_Reactive_Power_Mode | Reactive Power Mode | 1362 | # | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Reactive Power Set Point Percent | Inverter | GMS_MAP_DNP.INV003_Reactive_Power_Set_Point_Percent | Reactive Power Set Point Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power AC Percent | Inverter | GMS_MAP_DNP.INV003_Real_Power_AC_Percent | Real Power AC Percent |  | % | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power-AC | Inverter | GMS_MAP_DNP.INV003_Real_Power_AC | Real Power-AC | 1363 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power-DC | Inverter | GMS_MAP_DNP.INV003_Real_Power_DC | Real Power-DC | 1364 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Air Intake | Inverter | GMS_MAP_DNP.INV003_Temperature_Air_Intake | Temperature-Air Intake |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Ambient | Inverter | GMS_MAP_DNP.INV003_Temperature_Ambient | Temperature-Ambient | 1365 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Cabinet | Inverter | GMS_MAP_DNP.INV003_Temperature_Cabinet | Temperature-Cabinet | 1366 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Combiner Box | Inverter | GMS_MAP_DNP.INV003_Temperature_Combiner Box | Temperature-Combiner Box |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Coolant | Inverter | GMS_MAP_DNP.INV003_Temperature_Coolant | Temperature-Coolant |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Filter Choke | Inverter | GMS_MAP_DNP.INV003_Temperature_Filter Choke | Temperature-Filter Choke |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-IGBT Heat Sink | Inverter | GMS_MAP_DNP.INV003_Temperature_IGBT Heat Sink | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Temperature-Module | Inverter | GMS_MAP_DNP.INV003_Temperature_Module | Temperature-Module |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Humidity Cabinet | Inverter | GMS_MAP_DNP.INV003_Humidity Cabinet | Humidity Cabinet | 1367 | hPa | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Uptime | Inverter | GMS_MAP_DNP.INV003_Uptime | Uptime |  | seconds | Requested-Not Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage A-B | Inverter | GMS_MAP_DNP.INV003_Voltage_A_B | Voltage A-B | 1368 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage A-N | Inverter | GMS_MAP_DNP.INV003_Voltage_A_N | Voltage A-N | 1369 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage B-C | Inverter | GMS_MAP_DNP.INV003_Voltage_B_C | Voltage B-C | 1370 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage B-N | Inverter | GMS_MAP_DNP.INV003_Voltage_B_N | Voltage B-N | 1371 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage C-A | Inverter | GMS_MAP_DNP.INV003_Voltage_C_A | Voltage C-A | 1372 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage C-N | Inverter | GMS_MAP_DNP.INV003_Voltage_C_N | Voltage C-N | 1373 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 1 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_1 | Status Bit Word 1 | 1374 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 2 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_2 | Status Bit Word 2 | 1375 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 3 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_3 | Status Bit Word 3 | 1376 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 4 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_4 | Status Bit Word 4 | 1377 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 5 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_5 | Status Bit Word 5 | 1378 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 6 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_6 | Status Bit Word 6 | 1379 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 7 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_7 | Status Bit Word 7 | 1380 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 8 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_8 | Status Bit Word 8 | 1381 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003_Status Bit Word 9 | Inverter | GMS_MAP_DNP.INV003_Status_Bit_Word_9 | Status Bit Word 9 | 1382 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003 | TSN1_SUB1_INV003 Module 1_Status Bit Word | Inverter | GMS_MAP_DNP.INV003_Module_1_Status_Bit_Word | Status Bit Word | 1383 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_01_Reactive_Power_Mode | Reactive Power Mode | 1384 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_01_A_Phase_Current | A Phase Current | 1385 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_01_B_Phase_Current | B Phase Current | 1386 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_01_C_Phase_Current | C Phase Current | 1387 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_01_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_01_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_01_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_01_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_IO Status | Inverter Module | GMS_MAP_DNP.INV003_01_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Module Status | Inverter Module | GMS_MAP_DNP.INV003_01_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Operating State | Inverter Module | GMS_MAP_DNP.INV003_01_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_01_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Reactive Power | Inverter Module | GMS_MAP_DNP.INV003_01_Reactive_Power | Reactive Power | 1388 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_01_Real_Power | Real Power-AC | 1389 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_01_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_01_Voltage_DC | Voltage DC Bus | 1390 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_01_Voltage DC N | Voltage DC N | 1391 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_1_Voltage DC P | Voltage DC P | 1392 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input1 | Current DC Input1 | 1393 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input2 | Current DC Input2 | 1394 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input3 | Current DC Input3 | 1395 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input4 | Current DC Input4 | 1396 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input5 | Current DC Input5 | 1397 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input6 | Current DC Input6 | 1398 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input7 | Current DC Input7 | 1399 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_01_Current_DC_Input8 | Current DC Input8 | 1400 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_01_Power Command FB | Power Command FB | 1401 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_01_Power Setpoint FB | Power Setpoint FB | 1402 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_01_Reactive_Reactive Command FB | React Command FB | 1403 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_01_Reactive Setpoint FB | Reactive Setpoint FB | 1404 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_01_Real_Power_DC | Real Power-DC | 1405 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-01 | TSN1_SUB1_INV003-01_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1406 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV003_02_Status_Bit_Word | Status Bit Word | 1407 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_02_Reactive_Power_Mode | Reactive Power Mode | 1408 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_02_A_Phase_Current | A Phase Current | 1409 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_02_B_Phase_Current | B Phase Current | 1410 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_02_C_Phase_Current | C Phase Current | 1411 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_02_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_02_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_02_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_02_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_IO Status | Inverter Module | GMS_MAP_DNP.INV003_02_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Module Status | Inverter Module | GMS_MAP_DNP.INV003_02_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Operating State | Inverter Module | GMS_MAP_DNP.INV003_02_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_02_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Reactive Power | Inverter Module | GMS_MAP_DNP.INV003_02_Reactive_Power | Reactive Power | 1412 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_02_Real_Power | Real Power-AC | 1413 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_02_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_02_Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_02_Voltage_DC | Voltage DC Bus | 1414 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_02_Voltage DC N | Voltage DC N | 1415 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_2_Voltage DC P | Voltage DC P | 1416 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input1 | Current DC Input1 | 1417 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input2 | Current DC Input2 | 1418 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input3 | Current DC Input3 | 1419 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input4 | Current DC Input4 | 1420 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input5 | Current DC Input5 | 1421 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input6 | Current DC Input6 | 1422 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input7 | Current DC Input7 | 1423 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_02_Current_DC_Input8 | Current DC Input8 | 1424 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_02_Power Command FB | Power Command FB | 1425 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_02_Power Setpoint FB | Power Setpoint FB | 1426 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_02_Reactive_Reactive Command FB | React Command FB | 1427 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_02_Reactive Setpoint FB | Reactive Setpoint FB | 1428 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_02_Real_Power_DC | Real Power-DC | 1429 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-02 | TSN1_SUB1_INV003-02_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1430 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV003_03_Status_Bit_Word | Status Bit Word | 1431 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_03_Reactive_Power_Mode | Reactive Power Mode | 1432 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_03_A_Phase_Current | A Phase Current | 1433 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_03_B_Phase_Current | B Phase Current | 1434 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_03_C_Phase_Current | C Phase Current | 1435 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_03_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_03_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_03_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_03_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_IO Status | Inverter Module | GMS_MAP_DNP.INV003_03_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Module Status | Inverter Module | GMS_MAP_DNP.INV003_03_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Operating State | Inverter Module | GMS_MAP_DNP.INV003_03_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_03_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Reactive Power | Inverter Module | GMS_MAP_DNP.INV003_03_Reactive_Power | Reactive Power | 1436 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_03_Real_Power | Real Power-AC | 1437 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_03_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_03_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_03Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_03Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_03_Voltage_DC | Voltage DC Bus | 1438 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_03_Voltage DC N | Voltage DC N | 1439 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_3_Voltage DC P | Voltage DC P | 1440 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input1 | Current DC Input1 | 1441 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input2 | Current DC Input2 | 1442 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input3 | Current DC Input3 | 1443 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input4 | Current DC Input4 | 1444 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input5 | Current DC Input5 | 1445 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input6 | Current DC Input6 | 1446 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input7 | Current DC Input7 | 1447 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_03_Current_DC_Input8 | Current DC Input8 | 1448 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_03_Power Command FB | Power Command FB | 1449 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_03_Power Setpoint FB | Power Setpoint FB | 1450 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_03_Reactive_Reactive Command FB | React Command FB | 1451 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_03_Reactive Setpoint FB | Reactive Setpoint FB | 1452 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_03_Real_Power_DC | Real Power-DC | 1453 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-03 | TSN1_SUB1_INV003-03_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1454 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV003_04_Status_Bit_Word | Status Bit Word | 1455 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_04_Reactive_Power_Mode | Reactive Power Mode | 1456 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_04_A_Phase_Current | A Phase Current | 1457 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_04_B_Phase_Current | B Phase Current | 1458 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_04_C_Phase_Current | C Phase Current | 1459 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_04_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_04_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_04_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_04_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_IO Status | Inverter Module | GMS_MAP_DNP.INV003_04_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Module Status | Inverter Module | GMS_MAP_DNP.INV003_04_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Operating State | Inverter Module | GMS_MAP_DNP.INV003_04_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_04_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Reactive Power | Inverter Module | GMS_MAP_DNP.INV003_04_Reactive_Power | Reactive Power | 1460 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_04_Real_Power | Real Power-AC | 1461 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_04_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_04_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_04_Voltage_DC | Voltage DC Bus | 1462 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_04_Voltage DC N | Voltage DC N | 1463 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_4_Voltage DC P | Voltage DC P | 1464 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input1 | Current DC Input1 | 1465 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input2 | Current DC Input2 | 1466 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input3 | Current DC Input3 | 1467 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input4 | Current DC Input4 | 1468 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input5 | Current DC Input5 | 1469 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input6 | Current DC Input6 | 1470 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input7 | Current DC Input7 | 1471 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_04_Current_DC_Input8 | Current DC Input8 | 1472 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_04_Power Command FB | Power Command FB | 1473 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_04_Power Setpoint FB | Power Setpoint FB | 1474 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_04_Reactive_Reactive Command FB | React Command FB | 1475 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_04_Reactive Setpoint FB | Reactive Setpoint FB | 1476 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_04_Real_Power_DC | Real Power-DC | 1477 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-04 | TSN1_SUB1_INV003-04_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1478 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Status Bit Word | Inverter Module | GMS_MAP_DNP.INV003_05_Status_Bit_Word | Status Bit Word | 1479 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_05_Reactive_Power_Mode | Reactive Power Mode | 1480 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_05_A_Phase_Current | A Phase Current | 1481 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_05_B_Phase_Current | B Phase Current | 1482 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_05_C_Phase_Current | C Phase Current | 1483 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_05_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_05_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_05_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_05_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_IO Status | Inverter Module | GMS_MAP_DNP.INV003_05_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Module Status | Inverter Module | GMS_MAP_DNP.INV003_05_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Operating State | Inverter Module | GMS_MAP_DNP.INV003_05_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_05_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Reactive_Power | Inverter Module | GMS_MAP_DNP.INV003_05_Reactive_Power | Reactive Power | 1484 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_05_Real_Power | Real Power-AC | 1485 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_05_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_05_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_04Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_04Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_05_Voltage_DC | Voltage DC Bus | 1486 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_05_Voltage DC N | Voltage DC N | 1487 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_5_Voltage DC P | Voltage DC P | 1488 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input1 | Current DC Input1 | 1489 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input2 | Current DC Input2 | 1490 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input3 | Current DC Input3 | 1491 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input4 | Current DC Input4 | 1492 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input5 | Current DC Input5 | 1493 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input6 | Current DC Input6 | 1494 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input7 | Current DC Input7 | 1495 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_05_Current_DC_Input8 | Current DC Input8 | 1496 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_05_Power Command FB | Power Command FB | 1497 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_05_Power Setpoint FB | Power Setpoint FB | 1498 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_05_Reactive_Reactive Command FB | React Command FB | 1499 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_05_Reactive Setpoint FB | Reactive Setpoint FB | 1500 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_05_Real_Power_DC | Real Power-DC | 1501 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-05 | TSN1_SUB1_INV003-05_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1502 | °C | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Status Bit Word Tooooooooooooooooooo Looooooooooooooooooong | Inverter Module | GMS_MAP_DNP.INV003_06_Status_Bit_Word | Status Bit Word | 1503 | Bitwise, see Table & Binary Points | Not Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Reactive Power Mode | Inverter Module | GMS_MAP_DNP.INV003_06_Reactive_Power_Mode | Reactive Power Mode | 1504 | # | Not Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_A Phase Current | Inverter Module | GMS_MAP_DNP.INV003_06_A_Phase_Current | A Phase Current | 1505 | A | Not Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_B Phase Current | Inverter Module | GMS_MAP_DNP.INV003_06_B_Phase_Current | B Phase Current | 1506 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_C Phase Current | Inverter Module | GMS_MAP_DNP.INV003_06_C_Phase_Current | C Phase Current | 1507 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current-DC | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC | Current-DC |  | A | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Energy Delivered | Inverter Module | GMS_MAP_DNP.INV003_06_Energy_Delivered | Energy Delivered |  | kWh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Firmware version | Inverter Module | GMS_MAP_DNP.INV003_06_Firmware_Version | Firmware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Hardware version | Inverter Module | GMS_MAP_DNP.INV003_06_Hardware_Version | Hardware version |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Inverter Name | Inverter Module | GMS_MAP_DNP.INV003_06_Inverter_Name | Inverter Name |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_IO Status | Inverter Module | GMS_MAP_DNP.INV003_06_IO_Status | IO Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Module Status | Inverter Module | GMS_MAP_DNP.INV003_06_Module_Status | Module Status |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Operating State | Inverter Module | GMS_MAP_DNP.INV003_06_Operating_State | Operating State |  | n/a | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Reactive Energy | Inverter Module | GMS_MAP_DNP.INV003_06_Reactive_Energy | Reactive Energy |  | kVARh | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Reactive Power | Inverter Module | GMS_MAP_DNP.INV003_06_Reactive_Power | Reactive Power | 1508 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Real Power-AC | Inverter Module | GMS_MAP_DNP.INV003_06_Real_Power | Real Power-AC | 1509 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-Cabinet | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_Cabinet | Temperature-Cabinet |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-R1 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_R1 | Temperature-IGBT-R1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-R2 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_R2 | Temperature-IGBT-R2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-R3 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_R3 | Temperature-IGBT-R3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-S1 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_S1 | Temperature-IGBT-S1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-S2 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_S2 | Temperature-IGBT-S2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-S3 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_S3 | Temperature-IGBT-S3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-T1 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_T1 | Temperature-IGBT-T1 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-T2 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_T2 | Temperature-IGBT-T2 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-IGBT-T3 | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_IGBT_T3 | Temperature-IGBT-T3 |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-Max | Inverter Module | GMS_MAP_DNP.INV003_06_Temperature_Max | Temperature-Max |  | °C | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleA | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleA | Tracker-Commanded Tilt AngleA |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleB | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleB | Tracker-Commanded Tilt AngleB |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleC | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleC | Tracker-Commanded Tilt AngleC |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleD | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleD | Tracker-Commanded Tilt AngleD |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleE | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleE | Tracker-Commanded Tilt AngleE |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleF | Inverter Module | GMS_MAP_DNP.INV003_06_Commanded Tilt AngleF | Tracker-Commanded Tilt AngleF |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleG | Inverter Module | GMS_MAP_DNP.INV003_06Commanded Tilt AngleG | Tracker-Commanded Tilt AngleG |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Tracker-Commanded Tilt AngleH | Inverter Module | GMS_MAP_DNP.INV003_06Commanded Tilt AngleH | Tracker-Commanded Tilt AngleH |  | ° | Requested-Not Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Voltage DC Bus | Inverter Module | GMS_MAP_DNP.INV003_06_Voltage_DC | Voltage DC Bus | 1510 | kV | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Voltage DC N | Inverter Module | GMS_MAP_DNP.INV003_06_Voltage DC N | Voltage DC N | 1511 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Voltage DC P | Inverter Module | GMS_MAP_DNP.INV003_ Module_6_Voltage DC P | Voltage DC P | 1512 | kV | Not Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input1 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input1 | Current DC Input1 | 1513 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input2 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input2 | Current DC Input2 | 1514 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input3 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input3 | Current DC Input3 | 1515 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input4 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input4 | Current DC Input4 | 1516 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input5 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input5 | Current DC Input5 | 1517 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input6 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input6 | Current DC Input6 | 1518 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input7 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input7 | Current DC Input7 | 1519 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Current DC Input8 | Inverter Module | GMS_MAP_DNP.INV003_06_Current_DC_Input8 | Current DC Input8 | 1520 | A | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Power Command FB | Inverter Module | GMS_MAP_DNP.INV003_06_Power Command FB | Power Command FB | 1521 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Power Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_06_Power Setpoint FB | Power Setpoint FB | 1522 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_React Command FB | Inverter Module | GMS_MAP_DNP.INV003_06_Reactive_Reactive Command FB | React Command FB | 1523 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Reactive Setpoint FB | Inverter Module | GMS_MAP_DNP.INV003_06_Reactive Setpoint FB | Reactive Setpoint FB | 1524 | kVAR | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Real Power-DC | Inverter Module | GMS_MAP_DNP.INV003_06_Real_Power_DC | Real Power-DC | 1525 | kW | Requested-Available | -32767 | 32767
SUB1 | INV003-06 | TSN1_SUB1_INV003-06_Temperature-Ambient | Inverter Module | GMS_MAP_DNP.INV003_01_Temperature_Ambient | Temperature-Ambient | 1526 | °C | Requested-Available | -32767 | 32767
Digital Inputs | [6 empty] | n/a
Substation | DeviceID | Point Name | Device Type | Native_RTAC_Point_Name | Description | DNP Index | 0/1 State | Availability
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Communication Status | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Communication_Status | Communication Status | 0 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Relay Enabled | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Relay_Enabled | Relay Online | 1 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Software Alarm | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Software_Alarm | Software Alarm | 2 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Hardware Alarm | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Hardware_Alarm | Hardware Alarm | 3 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Communication Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Communication_Status | Communication Status | 4 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Relay Enabled | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Relay_Enabled | Relay Online | 5 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Software Alarm | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Software_Alarm | Software Alarm | 6 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Hardware Alarm | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Hardware_Alarm | Hardware Alarm | 7 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Breaker Fail Initiate 52T1 | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_OUT203_Breaker_Fail_Initiate_T1 | Breaker Fail Initiate | 8 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Breaker Fail Initiate 52T2 | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_OUT204_Breaker_Fail_Initiate_T2 | Breaker Fail Initiate | 9 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Line Comm Cutout | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Line_Comm_Cutout | Line Relaying Comm Cutout | 10 | 0 = Normal, 1 = Cutout | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Line Comm Failure | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Line_Comm_Failure | Line Relaying Comm Failure | 11 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_Direct Transfer Trip | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_Direct_Transfer_Trip | Direct Transfer Trip | 12 | 0 = Normal, 1 = Trip | Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_51 Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_51_TARGET_LED_STATE | 51 Target LED State | 13 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | WRONG | TSN1_SUB1_SEL-411L-87L1P_50 Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_50_TARGET_LED_STATE | 50 Target LED State | 14 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_TRIP Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_TRIP_TARGET_LED_STATE | TRIP Target LED State | 15 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_87 Channel 1 Alarm | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_87CH1AL | Diff Channel 1 Alarm | 16 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_87 Channel 2 Alarm | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_87CH1AL | Diff Channel 2 Alarm | 17 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_A Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_A_TARGET_LED_STATE | A Target LED State | 18 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_B Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_B_TARGET_LED_STATE | B Target LED State | 19 | 0=Normal, 1=Wrong | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_C Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_C_TARGET_LED_STATE | C Target LED State | 20 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_G Target LED State | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_G_TARGET_LED_STATE | G Target LED State | 21 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_PCB T1 Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN203_PCB_T1_Status | PCB T1 Status | 22 | 0=Open, 1=Closed | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1SUB1SEL-411L-87L1P_PCB T2 Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN204_PCB_T2_Status | PCB T2 Status | 23 | 0=Open, 1=Closed | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_86BFT1 Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN205_86BFT1_Status | 86BFT1 Status | 24 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_86BFT2 Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN206_86BFT2_Status | 86BFT2 Status | 25 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_89L 89a Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN301_89L_89a_Status | 89L 89a Status | 26 | 0=Open, 1=Closed | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_89L 43LR Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN302_89L_43LR_Status | 89L 43LR Status | 27 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-411L-87L1P | TSN1_SUB1_SEL-411L-87L1P_89L 89b Status | Line Relay | GMS_MAP_DNP.SEL_411L_87L1P_IN303_89L_89b_Status | 89L 89b Status | 28 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1s | TSN1_SUB1_GE-L90-87L1S_Communication Status | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Communication_Status | Communication Status | 29 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Relay Enabled | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Relay_Enabled | Relay Online | 30 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Software Alarm | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Software_Alarm | Software Alarm | 66 | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Hardware Alarm | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Hardware_Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Breaker Fail Initiate 52T1 | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Breaker_Fail_Initiate | Breaker Fail Initiate | 32 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Breaker Fail Initiate 52T2 | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Breaker_Fail_Initiate | Breaker Fail Initiate | 33 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Line Comm Cutout | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Line_Comm_Cutout | Line Relaying Comm Cutout | 34 | 0 = Normal, 1 = ope | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Line Comm Failure CH1 | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Line_Comm_CH1 Failure | Line Relaying Comm Failure | 35 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Line Comm Failure CH2 | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Line_Comm_CH2_Failure | Line Relaying Comm Failure | 36 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Direct Transfer Trip | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Direct_Transfer_Trip | Direct Transfer Trip | 37 | 0 = Normal, 1 = Trip | Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Minor Error | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Minor_Error | Minor Error | 56 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_Major Error | Line Relay | GMS_MAP_DNP.GE_L90_L1S_Major_Error | Major Error | 39 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_TRIP Target LED State | Line Relay | GMS_MAP_DNP.GE_L90_L1S_TRIP_TARGET_LED_STATE | TRIP Target LED State | 40 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_PCB T1 Status | Line Relay | GMS_MAP_DNP.GE_L90_L1S_PCB_T1_Status | PCB T1 Status | 41 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_PCB T2 Status | Line Relay | GMS_MAP_DNP.GE_L90_L1S_PCB_T2_Status | PCB T2 Status | 42 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_86BFT1 Status | Line Relay | GMS_MAP_DNP.GE_L90_L1S_86BFT1_Status | 86BFT1 Status | 43 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | GE-L90-87L1S | TSN1_SUB1_GE-L90-87L1S_86BFT2 Status | Line Relay | GMS_MAP_DNP.GE_L90_L1S_86BFT2_Status | 86BFT2 Status | 44 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Communication_Status | Communication Status | 45 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Relay_Enabled | Relay Online | 46 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Software_Alarm | Software Alarm | 47 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Hardware_Alarm | Hardware Alarm | 48 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Breaker_Status | Breaker Status | 49 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_43LR_BKR | Remote Local Status (At Breaker) | 50 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_43LR_Ctl_House | Remote Local Status (In Control House) | 51 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Loss_Of_AC_Alarm | Loss of AC Alarm | 52 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Loss_Of_DC_Alarm | Loss of DC Alarm | 53 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Spring_Charge_Alarm | Spring Charge Alarm | 54 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Low_SF6_Alarm | Low SF6 Alarm | 55 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Low SF6 Lockout | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_Low_SF6_Alarm | Low SF6 Lockout | 56 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 57 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 58 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 59 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 60 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_TCM_TC1 | 52T1 Trip Coil Monitor Alarm TC1 | 61 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_52T1 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_TCM_TC2 | 52T1 Trip Coil Monitor Alarm TC2 | 40 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_86BFT1 Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_86BFT1_Status | 86BFT1 Status | 63 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Breaker Fail Initiate | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_52T1_BFI | 52T1 BFI | 64 | poo | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_89T1 89a Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_89T1_89a | 89T1 89a Status | 65 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_89T1 43LR Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_89T1_43LR_Ctl_House | 89T1 Remote Local Status (In Control House) | 66 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_89T1 89b Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_89T1_89b | 89T1 89b Status | 67 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Communication Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Communication_Status | Communication Status | 68 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Relay Enabled | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Relay_Enabled | Relay Online | 69 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Software Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Software_Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Hardware Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Hardware_Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Breaker Fail Initiate | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Breaker_Fail_Initiate | Breaker Fail Initiate | 70 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Relay Trip LED | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_RELAY_TRIP_LED | RELAY TRIP LED | 71 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_86T1P Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Status | 86T1P Status | 72 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Cross Trip From T2 LOR | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Cross_Trip | 87T1P Cross Trip Received | 73 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_HV Winding Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_HV_Winding_Trip | T1 HV Winding Trip | 74 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Oil Temp Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Oil_Temp_Trip | T1 Oil Temp Trip | 75 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Bucholz Relay Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Bucholz_Trip | T1 Bucholz Relay Trip | 76 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Loss Of AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Loss_AC | T1 Loss of AC | 77 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Loss Of DC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_86T1P_Loss_DC | T1 Loss of DC | 78 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Communication Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Communication_Status | Communication Status | 79 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Relay Enabled | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Relay_Enabled | Relay Online | 80 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Software Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Software_Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hardware Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hardware_Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Breaker Fail Initiate | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Breaker_Fail_Initiate | Breaker Fail Initiate | 81 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Relay Trip LED | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1SR_RELAY_TRIP_LED | RELAY TRIP LED | 82 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_86T1S Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_86T1S_Status | 86T1S Status | 83 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Cross Trip From T2 LOR | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Cross_Trip_From_T2_LOR | 87T1S Cross Trip Received | 84 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_T1 Sudden Pressure Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_T1_Sudden_Pressure_Alarm | T1 Sudden Pressure Alarm | 85 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_High Oil Temp Alarm 95C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_High_Oil_Temp_Alarm | High Oil Temp Alarm 95C | 86 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_High Oil Temp Alarm 105C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_High_Oil_Temp_Alarm_105 | High Oil Temp Alarm 105C | 87 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_High Winding Temp Alarm 113C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_High_Winding_Temp_Alarm_113C | High Winding Temp Alarm 113C | 88 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_High Winding Temp Alarm 135C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_High_Winding_Temp_Alarm_135C | High Winding Temp Alarm 135C | 89 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hydran Gas HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hydran_Gas_HI_Alarm | Hydran Gas HI Alarm | 90 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hydran Gas HI HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hydran_Gas_HI_HI_Alarm | Hydran Gas HI HI Alarm | 91 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hydran Moisture HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hydran_Moisture_HI_Alarm | Hydran Moisture HI Alarm | 92 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hydran Moisture HI HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hydran_Moisture_HI_HI_Alarm | Hydran Moisture HI HI Alarm | 93 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Hydran Gas System Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Hydran_Gas_System_Alarm | Hydran Gas System Alarm | 94 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_2414 RLY Fail | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_2414_RLY_Fail | 2414 RLY Fail | 95 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Communication Status_Communication Status | Communication Status | 96 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Low Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Oil Level Low Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Sudden Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-HYDRAN | TSN1_SUB1_XFMR001-HYDRAN_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_HYDRAN_Loss Of Cooling Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Communication_Status | Communication Status | 97 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Low Pressure Alarm | Transformer Alarms | 98 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Oil Level Low Alarm | Transformer Alarms | 99 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Sudden Pressure Alarm | Transformer Alarms | 100 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL-2414_Loss Of Cooling Alarm | Transformer Alarms | 101 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Cooling Group 1 Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_COOLING_GROUP_1_Status | Stage fan status | 102 | 0=Off, 1=Cooling | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Cooling Group 2 Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_COOLING_GROUP_2_Status | Stage fan status | 103 | 0=Off, 1=Cooling | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Pressure Relief | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Pressure Relief | Transformer Alarms | 104 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Loss Of AC | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Loss Of AC | Transformer Alarms | 105 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Loss Of DC | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Loss Of DC | Transformer Alarms | 106 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ Bucholz Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_Bucholz Alarm | Transformer Alarms | 107 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR001-SEL-2414 | TSN1_SUB1_XFMR001-SEL-2414_ OLTC Protection Relay | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_SEL_2414_OLTC Protection Relay | Transformer Alarms | 108 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC Communication Status | Communication Status | 109 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Low Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Oil Level Low Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Sudden Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC_Loss Of Cooling Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Raise Active | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC Raise Active | T1 Tap Changer Raising | 110 | 0 =Normal, 1 = Raising | Not Requested-Available
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Lower Active | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC Lower Active | T1 Tap Changer Lowering | 111 | 0 =Normal, 1 = Lowering | Not Requested-Available
SUB1 | XFMR001-OLTC | TSN1_SUB1_XFMR001-OLTC_Auto Manual Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR001_OLTC _AUTO MAN | T1 Tap Changer Auto Manual Status | 112 | 0 =Auto, 1 = Manual | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Communication_Status | Communication Status | 113 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Relay_Enabled | Relay Online | 114 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Software_Alarm | Software Alarm | 115 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Hardware_Alarm | Hardware Alarm | 116 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Breaker Status | Breaker Relay |  | Breaker Status |  | 0 = Open, 1 = Closed | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Remote/Local At Breaker | Breaker Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Remote/Local Ctl House | Breaker Relay |  | Remote Local Status (In Control House) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Loss of AC Alarm | Breaker Relay |  | Loss of AC Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Loss of DC Alarm | Breaker Relay |  | Loss of DC Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Spring Charge Alarm | Breaker Relay |  | Spring Charge Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_52T1 Low SF6 Alarm | Breaker Relay |  | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 117 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 118 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 119 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 120 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89B1 89a Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89B1_89a | 89B1 89a Status | 121 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89B1 43LR Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89B1_43LR_Ctl_House | 89B1 Remote Local Status (In Control House) | 122 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89B1 89b Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89B1_89b | 89B1 89b Status | 123 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89TS 89a Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89TS_89a | 89TS 89a Status | 124 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89TS 43LR Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89TS_43LR_Ctl_House | 89TS Remote Local Status (In Control House) | 125 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_89TS 89b Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_89TS_89b | 89TS 89b Status | 126 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_Communication Status | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_Communication Status | Communication Status | 127 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_Relay Enabled | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_Relay Enabled | Relay Online | 128 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_Software Alarm | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_Software Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_Hardware Alarm | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_Hardware Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-B1 | TSN1_SUB1_SEL-587Z-B1_87 Target | Bus Relay | GMS_MAP_DNP.SEL_587Z_B1_87 Target | 87 Target | 129 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Communication_Status | Communication Status | 130 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Relay_Enabled | Relay Online | 131 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Software_Alarm | Software Alarm | 132 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Hardware_Alarm | Hardware Alarm | 133 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_Breaker_Status | Breaker Status | 134 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_43LR_BKR | Remote Local Status (At Breaker) | 135 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_43LR_Ctl_House | Remote Local Status (In Control House) | 136 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_Loss_Of_AC_Alarm | Loss of AC Alarm | 137 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_Loss_Of_DC_Alarm | Loss of DC Alarm | 138 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_Spring_Charge_Alarm | Spring Charge Alarm | 139 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 140 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 141 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 142 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 143 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_TCM_TC1 | PCB 35-11 Trip Coil Monitor Alarm TC1 | 144 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_52F11 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_52F11_TCM_TC2 | PCB 35-11 Trip Coil Monitor Alarm TC2 | 145 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Communication_Status | Communication Status | 146 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Relay_Enabled | Relay Online | 147 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Software_Alarm | Software Alarm | 148 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Hardware_Alarm | Hardware Alarm | 149 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_Breaker_Status | Breaker Status | 150 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_43LR_BKR | Remote Local Status (At Breaker) | 151 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_43LR_Ctl_House | Remote Local Status (In Control House) | 152 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_Loss_Of_AC_Alarm | Loss of AC Alarm | 153 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_Loss_Of_DC_Alarm | Loss of DC Alarm | 154 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_Spring_Charge_Alarm | Spring Charge Alarm | 155 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 156 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 157 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 158 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 159 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_TCM_TC1 | PCB 35-12 Trip Coil Monitor Alarm TC1 | 160 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_52F12 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_52F12_TCM_TC2 | PCB 35-12 Trip Coil Monitor Alarm TC2 | 161 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Communication_Status | Communication Status | 162 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Relay_Enabled | Relay Online | 163 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Software_Alarm | Software Alarm | 164 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Hardware_Alarm | Hardware Alarm | 165 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_Breaker_Status | Breaker Status | 166 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_43LR_BKR | Remote Local Status (At Breaker) | 167 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_43LR_Ctl_House | Remote Local Status (In Control House) | 168 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_Loss_Of_AC_Alarm | Loss of AC Alarm | 169 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_Loss_Of_DC_Alarm | Loss of DC Alarm | 170 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_Spring_Charge_Alarm | Spring Charge Alarm | 171 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 172 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 173 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 174 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 175 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_TCM_TC1 | PCB 35-13 Trip Coil Monitor Alarm TC1 | 176 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_52F13 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_52F13_TCM_TC2 | PCB 35-13 Trip Coil Monitor Alarm TC2 | 177 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Communication Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Communication_Status | Communication Status | 178 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Relay Enabled | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Relay_Enabled | Relay Online | 179 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Software Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Software_Alarm | Software Alarm | 180 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Hardware Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Hardware_Alarm | Hardware Alarm | 181 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Breaker Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Breaker_Status | Breaker Status | 182 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Remote/Local At Breaker | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Remote_Local_At_Breaker | Remote Local Status (At Breaker) | 183 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Remote_Local_Ctl_House | Remote Local Status (In Control House) | 184 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Loss_Of_AC_Alarm | Loss of AC Alarm | 185 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Loss_Of_DC_Alarm | Loss of DC Alarm | 186 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Spring Charge Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1_Spring_Charge_Alarm | Spring Charge Alarm | 187 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 Low SF6 Alarm | Reactive Power Relay |  | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_RELAY TRIP Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_RELAY TRIP Target | RELAY TRIP Target | 188 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_27 59 Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_27 59 Target | Under / Over Voltage Target | 189 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_50 51 Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_50 51 Target | Overcurrent Target | 190 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 TCM 1 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1 TCM 1 Alarm | 52V1 TCM 1 Alarm | 191 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_52V1 TCM 2 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_52V1 TCM 2 Alarm | 52V1 TCM 2 Alarm | 192 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89V1 89a Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11_Remote_Local_Ctl_House | 89V1 89a Status | 193 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Switch Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 89a Status | Switch Status | 194 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Remote/Local At Breaker | Reactive Power Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Remote/Local Ctl House | Remote Local Status (In Control House) | 195 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Loss Of AC Alarm | Loss of AC Alarm | 196 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Loss Of DC Alarm | Loss of DC Alarm | 197 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_MVAR Contribution | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Spring Charge Alarm | Spring Charge Alarm |  | 0=Normal, 1=Alarm | Requested-Not Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Low SF6 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Low SF6 Alarm | Low SF6 Alarm | 198 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 Low SF6 Lockout | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 Low SF6 Lockout | 89C11 Low SF6 Lockout | 199 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Switch Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 89a Status | Switch Status | 200 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Remote/Local At Breaker | Reactive Power Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Remote/Local Ctl House | Remote Local Status (In Control House) | 201 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Loss Of AC Alarm | Loss of AC Alarm | 202 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Loss Of DC Alarm | Loss of DC Alarm | 203 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Spring Charge Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Spring Charge Alarm | Spring Charge Alarm | 204 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Low SF6 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Low SF6 Alarm | Low SF6 Alarm | 205 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 Low SF6 Lockout | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 Low SF6 Lockout | 89C12 Low SF6 Lockout | 206 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C12 TCM Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C12 TCM Alarm | 89C12 TCM Alarm | 207 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_89C11 TCM Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V1_89C11 TCM Alarm | 89C11 TCM Alarm | 208 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_CAP11 Avail CLOSE | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP11_AVAIL_CLOSE | CAP11 Avail CLOSE | 209 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_CAP11 Avail OPEN | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP11_AVAIL_OPEN | CAP11 Avail OPEN | 210 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_CAP12 Avail CLOSE | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP12_AVAIL_CLOSE | CAP12 Avail CLOSE | 211 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_CAP12 Avail OPEN | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP12_AVAIL_OPEN | CAP12 Avail OPEN | 212 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Communication_Status | Communication Status | 213 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Relay_Enabled | Relay Online | 214 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Software_Alarm | Software Alarm | 215 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Hardware_Alarm | Hardware Alarm | 216 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Breaker_Status | Breaker Status | 217 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_43LR_BKR | Remote Local Status (At Breaker) | 218 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_43LR_Ctl_House | Remote Local Status (In Control House) | 219 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Loss_Of_AC_Alarm | Loss of AC Alarm | 220 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Loss_Of_DC_Alarm | Loss of DC Alarm | 221 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Spring_Charge_Alarm | Spring Charge Alarm | 222 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Low_SF6_Alarm | Low SF6 Alarm | 223 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Low SF6 Lockout | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_Low_SF6_Alarm | Low SF6 Lockout | 224 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 225 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 226 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 227 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 228 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_TCM_TC1 | 52T2 Trip Coil Monitor Alarm TC1 | 229 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_52T2 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_TCM_TC2 | 52T2 Trip Coil Monitor Alarm TC2 | 230 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_86BFT2 Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_86BFT2_Status | 86BFT2 Status | 231 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Breaker Fail Initiate | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_52T2_BFI | Breaker Fail Initiate | 232 | 0=Normal, 1=BFI | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_89T2 89a Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_89T2_89a | 89T2 89a Status | 233 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_89T2 43LR Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_89T2_43LR_Ctl_House | 89T2 Remote Local Status (In Control House) | 234 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_89T2 89b Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_89T2_89b | 89T2 89b Status | 235 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Communication Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Communication_Status | Communication Status | 236 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Relay Enabled | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Relay_Enabled | Relay Online | 237 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Software Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Software_Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Hardware Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Hardware_Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Breaker Fail Initiate | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Breaker_Fail_Initiate | Breaker Fail Initiate | 238 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Relay Trip LED | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_RELAY_TRIP_LED | RELAY TRIP LED | 239 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_86T2P Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Status | 86T2P Status | 240 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Cross Trip From T1 LOR | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Cross_Trip | 87T2P Cross Trip Received | 241 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_HV Winding Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_HV_Winding_Trip | T2 HV Winding Trip | 242 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Oil Temp Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Oil_Temp_Trip | T2 Oil Temp Trip | 243 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Bucholz Relay Trip | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Bucholz_Trip | T2 Bucholz Relay Trip | 244 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Loss Of AC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Loss_AC | T2 Loss of AC | 245 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Loss Of DC | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_86T2P_Loss_DC | T2 Loss of DC | 246 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Communication Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Communication_Status | Communication Status | 247 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Relay Enabled | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Relay_Enabled | Relay Online | 248 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Software Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Software_Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hardware Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hardware_Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Breaker Fail Initiate | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Breaker_Fail_Initiate | Breaker Fail Initiate | 249 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Relay Trip LED | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2SR_RELAY_TRIP_LED | Relay Trip LED | 250 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_86T2S Status | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_86T2S_Status | 86T2S Status | 251 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Cross Trip From T1 LOR | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Cross_Trip_From_T2_LOR | 87T2S Cross Trip Received | 252 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_T2 Sudden Pressure Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_T2_Sudden_Pressure_Alarm | T2 Sudden Pressure Alarm | 253 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_High Oil Temp Alarm 95C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_High_Oil_Temp_Alarm | High Oil Temp Alarm 95C | 254 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_High Oil Temp Alarm 105C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_High_Oil_Temp_Alarm_105 | High Oil Temp Alarm 105C | 255 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_High Winding Temp Alarm 113C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_High_Winding_Temp_Alarm_113C | High Winding Temp Alarm 113C | 256 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_High Winding Temp Alarm 135C | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_High_Winding_Temp_Alarm_135C | High Winding Temp Alarm 135C | 257 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hydran Gas HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hydran_Gas_HI_Alarm | Hydran Gas HI Alarm | 258 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hydran Gas HI HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hydran_Gas_HI_HI_Alarm | Hydran Gas HI HI Alarm | 259 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hydran Moisture HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hydran_Moisture_HI_Alarm | Hydran Moisture HI Alarm | 260 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hydran Moisture HI HI Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hydran_Moisture_HI_HI_Alarm | Hydran Moisture HI HI Alarm | 261 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Hydran Gas System Alarm | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Hydran_Gas_System_Alarm | Hydran Gas System Alarm | 262 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_2414 RLY Fail | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_2414_RLY_Fail | 2414 RLY Fail | 263 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Communication Status_Communication Status | Communication Status | 264 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Low Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Oil Level Low Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Sudden Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-HYDRAN | TSN1_SUB1_XFMR002-HYDRAN_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_HYDRAN_Loss Of Cooling Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Communication_Status | Communication Status | 265 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Low Pressure Alarm | Transformer Alarms | 266 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Oil Level Low Alarm | Transformer Alarms | 267 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Sudden Pressure Alarm | Transformer Alarms | 268 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL-2414_Loss Of Cooling Alarm | Transformer Alarms | 269 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Cooling Group 1 Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_COOLING_GROUP_1_Status | Stage fan status | 270 | 0=Off, 1=Cooling | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Cooling Group 2 Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_COOLING_GROUP_2_Status | Stage fan status | 271 | 0=Off, 1=Cooling | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Pressure Relief | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Pressure Relief | Transformer Alarms | 272 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Loss Of AC | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Loss Of AC | Transformer Alarms | 273 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Loss Of DC | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Loss Of DC | Transformer Alarms | 274 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ Bucholz Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_Bucholz Alarm | Transformer Alarms | 275 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR002-SEL-2414 | TSN1_SUB1_XFMR002-SEL-2414_ OLTC Protection Relay | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_SEL_2414_OLTC Protection Relay | Transformer Alarms | 276 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Communication Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC Communication Status | Communication Status | 277 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Oil Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Oil Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Winding Temperature High Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Winding Temperature High Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_High Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_High Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Low Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Low Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Low Vacuum Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Low Vacuum Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Oil Level Low Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Oil Level Low Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Sudden Pressure Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Sudden Pressure Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Loss Of Cooling Alarm | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC_Loss Of Cooling Alarm | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Applicable
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Raise Active | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC Raise Active | T1 Tap Changer Raising | 278 | 0 =Normal, 1 = Raising | Not Requested-Available
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Lower Active | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC Lower Active | T1 Tap Changer Lowering | 279 | 0 =Normal, 1 = Lowering | Not Requested-Available
SUB1 | XFMR002-OLTC | TSN1_SUB1_XFMR002-OLTC_Auto Manual Status | Medium-High Voltage Transformer | GMS_MAP_DNP.XFMR002_OLTC _AUTO MAN | T1 Tap Changer Auto Manual Status | 280 | 0 =Auto, 1 = Manual | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Communication_Status | Communication Status | 281 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Relay_Enabled | Relay Online | 282 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Software_Alarm | Software Alarm | 283 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Hardware_Alarm | Hardware Alarm | 284 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Breaker Status | Breaker Relay |  | Breaker Status |  | 0 = Open, 1 = Closed | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Remote/Local At Breaker | Breaker Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Remote/Local Ctl House | Breaker Relay |  | Remote Local Status (In Control House) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Loss of AC Alarm | Breaker Relay |  | Loss of AC Alarm |  | 0=Normal, 1=Alarm | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Loss of DC Alarm | Breaker Relay |  | Loss of DC Alarm |  | 0=Normal, 1=Alarm | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Spring Charge Alarm | Breaker Relay |  | Spring Charge Alarm |  | 0=Normal, 1=Alarm | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_52T2 Low SF6 Alarm | Breaker Relay |  | Low SF6 Alarm |  | 0=Normal, 1=Alarm | Requested-Not Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 285 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 286 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 287 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 288 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_89B1 89a Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_89B1_89a | 89B1 89a Status | 289 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_89B1 43LR Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_89B1_43LR_Ctl_House | 89B1 Remote Local Status (In Control House) | 290 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_89B1 89b Status | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_89B1_89b | 89B1 89b Status | 291 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_Communication Status | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_Communication Status | Communication Status | 292 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_Relay Enabled | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_Relay Enabled | Relay Online | 293 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_Software Alarm | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_Software Alarm | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_Hardware Alarm | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_Hardware Alarm | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-B2 | TSN1_SUB1_SEL-587Z-B2_87 Target | Bus Relay | GMS_MAP_DNP.SEL_587Z_B2_87 Target | 87 Target | 294 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Communication_Status | Communication Status | 295 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Relay_Enabled | Relay Online | 296 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Software_Alarm | Software Alarm | 297 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Hardware_Alarm | Hardware Alarm | 298 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_Breaker_Status | Breaker Status | 299 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_43LR_BKR | Remote Local Status (At Breaker) | 300 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_43LR_Ctl_House | Remote Local Status (In Control House) | 301 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_Loss_Of_AC_Alarm | Loss of AC Alarm | 302 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_Loss_Of_DC_Alarm | Loss of DC Alarm | 303 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_Spring_Charge_Alarm | Spring Charge Alarm | 304 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 305 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 306 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 307 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 308 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_TCM_TC1 | 52F21 Trip Coil Monitor Alarm TC1 | 309 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_52F21 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_52F21_TCM_TC2 | 52F21 Trip Coil Monitor Alarm TC2 | 310 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Communication_Status | Communication Status | 311 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Relay_Enabled | Relay Online | 312 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Software_Alarm | Software Alarm | 313 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Hardware_Alarm | Hardware Alarm | 314 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_Breaker_Status | Breaker Status | 315 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_43LR_BKR | Remote Local Status (At Breaker) | 316 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_43LR_Ctl_House | Remote Local Status (In Control House) | 317 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_Loss_Of_AC_Alarm | Loss of AC Alarm | 318 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_Loss_Of_DC_Alarm | Loss of DC Alarm | 319 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_Spring_Charge_Alarm | Spring Charge Alarm | 320 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 321 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 322 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 323 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 324 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_TCM_TC1 | 52F22 Trip Coil Monitor Alarm TC1 | 325 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_52F22 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_52F22_TCM_TC2 | 52F22 Trip Coil Monitor Alarm TC2 | 326 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Communication Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Communication_Status | Communication Status | 327 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Relay Enabled | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Relay_Enabled | Relay Online | 328 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Software Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Software_Alarm | Software Alarm | 329 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Hardware Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Hardware_Alarm | Hardware Alarm | 330 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Breaker Status | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_Breaker_Status | Breaker Status | 331 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Remote/Local At Breaker | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_43LR_BKR | Remote Local Status (At Breaker) | 332 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Remote/Local Ctl House | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_43LR_Ctl_House | Remote Local Status (In Control House) | 333 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Loss of AC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_Loss_Of_AC_Alarm | Loss of AC Alarm | 334 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Loss of DC Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_Loss_Of_DC_Alarm | Loss of DC Alarm | 335 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Spring Charge Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_Spring_Charge_Alarm | Spring Charge Alarm | 336 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Low SF6 Alarm | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_Low_SF6_Alarm | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_LED-12 TRIP Relay Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_LED_2_TRIP_RELAY_TRIP | LED-2 TRIP RELAY TRIP | 337 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_LED-16 50 Instantaneous OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_LED_16_50_Instantaneous_OC_trip | LED-16 50 Instantaneous OC trip | 338 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_LED-17 51 Time Delay OC Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_LED_17_51_Time_Delay_OC_trip | LED-17 51 Time Delay OC trip | 339 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_LED-18 81 Frequency Trip | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_LED_18_81_Freq_Trip | LED-18 81 Frequency Trip | 340 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Trip Coil Monitor Alarm TC1 | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_TCM_TC1 | 52F23 Trip Coil Monitor Alarm TC1 | 341 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_52F23 Trip Coil Monitor Alarm TC2 | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_52F23_TCM_TC2 | 52F23 Trip Coil Monitor Alarm TC2 | 342 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Communication Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Communication_Status | Communication Status | 343 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Relay Enabled | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Relay_Enabled | Relay Online | 344 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Software Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Software_Alarm | Software Alarm | 345 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Hardware Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_RB187_Hardware_Alarm | Hardware Alarm | 346 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Breaker Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Breaker_Status | Breaker Status | 347 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Remote/Local At Breaker | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Remote_Local_At_Breaker | Remote Local Status (At Breaker) | 348 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Remote_Local_Ctl_House | Remote Local Status (In Control House) | 349 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Loss_Of_AC_Alarm | Loss of AC Alarm | 350 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Loss_Of_DC_Alarm | Loss of DC Alarm | 351 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Spring Charge Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2_Spring_Charge_Alarm | Spring Charge Alarm | 352 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 Low SF6 Alarm | Reactive Power Relay |  | Low SF6 Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_RELAY TRIP Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_RELAY TRIP Target | RELAY TRIP Target | 353 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_27 59 Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_27 59 Target | Under / Over Voltage Target | 354 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_50 51 Target | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_50 51 Target | Overcurrent Target | 355 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 TCM 1 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2 TCM 1 Alarm | 52V2 TCM 1 Alarm | 356 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_52V2 TCM 2 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_52V2 TCM 2 Alarm | 52V2 TCM 2 Alarm | 357 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89V2 89a Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C11_Remote_Local_Ctl_House | 89V2 89a Status | 358 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Switch Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21 Switch Status | Switch Status | 359 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Remote/Local At Breaker | Reactive Power Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Remote/Local_Ctl_House | Remote Local Status (In Control House) | 360 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Loss_Of_AC_Alarm | Loss of AC Alarm | 361 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Loss_Of_DC_Alarm | Loss of DC Alarm | 362 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Spring Charge Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Spring_Charge_Alarm | Spring Charge Alarm | 363 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Low SF6 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Low_SF6_Alarm | Low SF6 Alarm | 364 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 Low SF6 Lockout | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_Low_SF6_Lockout | 89C21 Low SF6 Lockout | 365 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Switch Status | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_89a_Status | Switch Status | 366 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Remote/Local At Breaker | Reactive Power Relay |  | Remote Local Status (At Breaker) |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Remote/Local Ctl House | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Remote/Local_Ctl_House | Remote Local Status (In Control House) | 367 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Loss of AC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Loss_Of_AC_Alarm | Loss of AC Alarm | 368 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Loss of DC Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Loss_Of_DC_Alarm | Loss of DC Alarm | 369 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Spring Charge Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Spring_Charge_Alarm | Spring Charge Alarm | 370 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Low SF6 Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Low_SF6_Alarm | Low SF6 Alarm | 371 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 Low SF6 Lockout | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_Low_SF6_Lockout | 89C22 Low SF6 Lockout | 372 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C22 TCM Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C22_TCM_Alarm | 89C22 TCM Alarm | 373 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_89C21 TCM Alarm | Reactive Power Relay | GMS_MAP_DNP.SEL_487V_11V2_89C21_TCM_Alarm | 89C21 TCM Alarm | 374 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_CAP21 Avail CLOSE | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP21_AVAIL_CLOSE | CAP21 Avail CLOSE | 375 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_CAP21 Avail OPEN | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP21_AVAIL_OPEN | CAP21 Avail OPEN | 376 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_CAP22 Avail CLOSE | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP22_AVAIL_CLOSE | CAP22 Avail CLOSE | 377 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_CAP22 Avail OPEN | Reactive Power Relay | GMS_MAP_DNP.SEL-3530-RTAC-1_CAP22_AVAIL_OPEN | CAP22 Avail OPEN | 378 | 0=Unavalable, 1=Available | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Communication Satus | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Communication_Satus | RELAY ENABLED | 379 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_RTU1 Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_RTU1_Fail | RTU1 Fail | 380 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87LP Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87LP_Relay_Alarm | 87LP Relay Alarm | 381 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87LS Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87LS_Relay_Alarm | 87LS Relay Alarm | 382 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11T1H Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11T1H_Relay_Alarm | 11T1H Relay Alarm | 383 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T1P Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T1P_Relay_Alarm | 87T1P Relay Alarm | 384 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T1S Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T1S_Relay_Alarm | 87T1S Relay Alarm | 385 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11T2H Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11T2H_Relay_Alarm | 11T2H Relay Alarm | 386 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T2P Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T2P_Relay_Alarm | 87T2P Relay Alarm | 387 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T2S Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T2S_Relay_Alarm | 87T2S Relay Alarm | 388 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F11 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F11_Relay_Alarm | 11F11 Relay Alarm | 389 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F12 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F12_Relay_Alarm | 11F12 Relay Alarm | 390 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F13 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F13_Relay_Alarm | 11F13 Relay Alarm | 391 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F21 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F21_Relay_Alarm | 11F21 Relay Alarm | 392 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F22 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F22_Relay_Alarm | 11F22 Relay Alarm | 393 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11F23 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11F23_Relay_Alarm | 11F23 Relay Alarm | 394 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87B1 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87B1_Relay_Alarm | 87B1 Relay Alarm | 395 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T1L Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T1L_Relay_Alarm | 87T1L Relay Alarm | 396 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87T2L Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87T2L_Relay_Alarm | 87T2L Relay Alarm | 397 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_87B2 Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_87B2_Relay_Alarm | 87B2 Relay Alarm | 398 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11V1L Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11V1L_Relay_Alarm | 11V1L Relay Alarm | 399 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_11V2L Relay Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_11V2L_Relay_Alarm | 11V2L Relay Alarm | 400 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House Access Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_Access_Alarm | Ctl House Access Alarm | 401 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House Smoke Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House__Smoke_Alarm | Ctl House Smoke Alarm | 402 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House HI Temp Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_HI_Temp_Alarm | Ctl House HI Temp Alarm | 403 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House LO Temp Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_LO_Temp_Alarm | Ctl House Lo Temp Alarm | 404 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House Hydrogen Gas Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_Hydrogen_Gas_Alarm | Ctl House Hydrogen Gas Alarm | 405 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_ATS Loss Of Alternate Power | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_ATS_Loss_Of_Alternate | ATS Loss of Alternate Power | 406 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House ATS On Alternate Power | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_ATS_On_Alternate | Ctl House ATS On Alternate Power | 407 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House HVAC 1 Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_HVAC_1_Alarm | Ctl House HVAC 1 Alarm | 408 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Ctl House HVAC 2 Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Ctl_House_HVAC_2_Alarm | Ctl House HVAC 2 Alarm | 409 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Battery Charger 1 Summary Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Battery_Charger_2_Summary_Alarm | Battery Charger 1 Summary Alarm | 410 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Battery Charger 1 Ground Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Battery_Charger_2_Ground_Alarm | Battery Charger 1 Ground Alarm | 411 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Battery Charger 2 Summary Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Battery_Charger_2_Summary_Alarm | Battery Charger 2 Summary Alarm | 412 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Battery Charger 2 Ground Alarm | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Battery_Charger_2_Ground_Alarm | Battery Charger 2 Ground Alarm | 413 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_Clock Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_Clock_Fail | Clock Fail | 414 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_INV1 Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_INV1_Fail | INV1 Fail | 415 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_HMI Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_HMI_Fail | HMI Fail | 416 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_DFR1 Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_DFR1_Fail | DFR1 Fail | 417 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_DFR1 Triggered | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_DFR1_Triggered | DFR1 Triggered | 418 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | TSN1_SUB1_SEL-2440-DPAC1_MTR1 Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL_2440_DPAC1_MTR1_Fail | MTR1 Fail | 419 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_Any Relay Failure | Discrete IO (DPAC) | GMS_MAP_DNP.SEL-3530-RTAC-1_Any_Relay_Failure | Any Relay Failure | 420 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_Any Relay Comm Fail | Discrete IO (DPAC) | GMS_MAP_DNP.SEL-3530-RTAC-1_Any_Relay_Comm_Fail | Any Relay Comm_Fail | 421 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_Any Relay Loss Of DC | Discrete IO (DPAC) | GMS_MAP_DNP.SEL-3530-RTAC-1_Any_Relay_Loss_Of_DC | Any Relay Loss of DC | 422 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Generator Breaker - Group 1 | ERCOT | GMS_MAP_DNP.SEL-3530-RTAC-1_ERCOT Generator Breaker - Group 1 | ERCOT Generator Breaker - Group 1 | 423 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Auto Voltage Reg (AVR) Group 1 | ERCOT | GMS_MAP_DNP.SEL-3530-RTAC-1_ERCOT Auto Voltage Reg (AVR) Group 1 | ERCOT Auto Voltage Reg (AVR) Group 1 | 424 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Generator Breaker - Group 2 | ERCOT | GMS_MAP_DNP.SEL-3530-RTAC-1_ERCOT Generator Breaker - Group 2 | ERCOT Generator Breaker - Group 2 | 425 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-3555-RTU1 | TSN1_SUB1_SEL-3555-RTU1_ERCOT Auto Voltage Reg (AVR) Group 2 | ERCOT | GMS_MAP_DNP.SEL-3530-RTAC-1_ERCOT Auto Voltage Reg (AVR) Group 2 | ERCOT Auto Voltage Reg (AVR) Group 2 | 426 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 1 Curtailment Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Unit_1_Curtailment_Disabled_Enabled | GMS Curtailment Disabled/Enabled | 427 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Reactive Power Control Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Reactive_Power_Control_Disabled_Enabled | GMS Reactive Power Control Disabled/Enabled | 428 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Power Factor Control Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Power_Factor_Control_Disabled_Enabled | GMS Power Factor Control Disabled/Enabled | 429 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Voltage Control Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Voltage_Control_Disabled_Enabled | GMS Voltage Control Disabled/Enabled | 430 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Up Rate Control Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Up_Rate_Control_Disabled_Enabled | GMS Ramp Up Rate Control Disabled/Enabled | 431 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Down Rate Control Disabled/Enabled | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Down_Rate_Control_Disabled_Enabled | GMS Ramp Down Rate Control Disabled/Enabled | 432 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_AVR Active | PPC | GMS_MAP_DNP.PPC_AVR_Active | AVR Active | 433 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Unit 1 Active Curtailment | PPC | GMS_MAP_DNP.PPC_Unit_1_Active_Curtailment | Active Curtailment | 434 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Invalid GMS Unit 1 Curtailment Setpoint Alarm | PPC | GMS_MAP_DNP.PPC_Invalid_GMS_Unit_1_Curtailment_Setpoint_Alarm | Invalid GMS Curtailment Setpoint Alarm | 435 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Invalid GMS Voltage Setpoint Alarm | PPC | GMS_MAP_DNP.PPC_Invalid_GMS_Voltage_Setpoint_Alarm_ | Invalid GMS Voltage Setpoint Alarm | 436 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Invalid GMS VAR Setpoint Alarm | PPC | GMS_MAP_DNP.PPC_Invalid_GMS_VAR_Setpoint_Alarm | Invalid GMS VAR Setpoint Alarm | 437 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Invalid GMS PF Setpoint Alarm | PPC | GMS_MAP_DNP.PPC_Invalid_GMS_PF_Setpoint_Alarm | Invalid GMS PF Setpoint Alarm | 438 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Invalid GMS Ramp Rate Setpoint Alarm | PPC | GMS_MAP_DNP.PPC_Invalid_GMS_Ramp_Rate_Setpoint_Alarm | Invalid GMS Ramp Rate Setpoint Alarm | 439 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV001 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV001_Control_Status | Inverter Control Status | 440 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV002 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV002_Control_Status | Inverter Control Status | 441 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV003 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV003_Control_Status | Inverter Control Status | 442 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV004 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV004_Control_Status | Inverter Control Status | 443 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV005 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV005_Control_Status | Inverter Control Status | 444 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV006 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV006_Control_Status | Inverter Control Status | 445 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV201 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV201_Control_Status | Inverter Control Status | 446 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV202 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV202_Control_Status | Inverter Control Status | 447 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV203 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV203_Control_Status | Inverter Control Status | 448 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV204 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV204_Control_Status | Inverter Control Status | 449 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV205 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV205_Control_Status | Inverter Control Status | 450 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_INV INV206 Control Status | PPC | GMS_MAP_DNP.PPC_INV_INV206_Control_Status | Inverter Control Status | 451 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_High Frequency Event Flag | PPC | GMS_MAP_DNP.PPC_High_Frequency_Event_Flag | High Frequency Event Flag | 452 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_Low Frequency Event Flag | PPC | GMS_MAP_DNP.PPC_Low_Frequency_Event_Flag | Low Frequency Event Flag | 453 | 0=Off, 1=On | Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_AutoStart On | Inverter | GMS_MAP_DNP.INV001_AutoStart On | AutoStart On |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Comm Fail | Inverter | GMS_MAP_DNP.INV001_Comm Fail | Comm Fail | 454 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Monitor Offline | Inverter | GMS_MAP_DNP.INV001_DC Monitor Offline | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Faulted | Inverter | GMS_MAP_DNP.INV001_Faulted | Faulted |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Locked Out | Inverter | GMS_MAP_DNP.INV001_Locked Out | Locked Out |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Master Control Enabled | Inverter | GMS_MAP_DNP.INV001_Master Control Enabled | Master Control Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Offline | Inverter | GMS_MAP_DNP.INV001_Offline | Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ramp Up Enabled | Inverter | GMS_MAP_DNP.INV001_Ramp Up Enabled | Ramp Up Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ramp Down Enabled | Inverter | GMS_MAP_DNP.INV001_Ramp Down Enabled | Ramp Down Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Real Power Curtailment Flag | Inverter | GMS_MAP_DNP.INV001_Real Power Curtailment Flag | Real Power Curtailment Flag |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Surge MOV Failed | Inverter | GMS_MAP_DNP.INV001_Surge MOV Failed | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Following Setpoint | Inverter | GMS_MAP_DNP.INV001_Following_Setpoint | Following Setpoint |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | TSN1_SUB1_INV001_Major Fault | Inverter | GMS_MAP_DNP.INV001_Major_Fault | Major Fault | 455 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Grid Fault | Inverter | GMS_MAP_DNP.INV001_Grid_Fault_ | Grid Fault | 456 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Alarm | Inverter | GMS_MAP_DNP.INV001_Alarm | Alarm | 457 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Minor Fault | Inverter | GMS_MAP_DNP.INV001_Minor_Fault | Minor Fault | 458 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Module 1 Faulted | Inverter | GMS_MAP_DNP.INV001_Module_1_Faulted | Module 1 Faulted | 459 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Module 2 Faulted | Inverter | GMS_MAP_DNP.INV001_Module_2_Faulted | Module 2 Faulted | 460 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Module 3 Faulted | Inverter | GMS_MAP_DNP.INV001_Module_3_Faulted | Module 3 Faulted | 461 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Module 4 Faulted | Inverter | GMS_MAP_DNP.INV001_Module_4_Faulted | Module 4 Faulted | 462 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Module 5 Faulted | Inverter | GMS_MAP_DNP.INV001_Module_5_Faulted | Module 5 Faulted | 463 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Remote Operation | Inverter | GMS_MAP_DNP.INV001_Remote_Operation | Remote Operation | 464 | 0=Disabled, 1=Enabled | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_72C Status | Inverter | GMS_MAP_DNP.INV001_72C_Status | 72C Status | 465 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Run Command Status | Inverter | GMS_MAP_DNP.INV001_Run_Command_Status | Run Command Status | 466 | 0=Stop, 1=Start | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_MPPT Mode | Inverter | GMS_MAP_DNP.INV001_MPPT_Mode | MPPT Mode | 467 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC-AVR Mode | Inverter | GMS_MAP_DNP.INV001_DC-AVR_Mode | DC-AVR Mode | 468 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_52RC Status | Inverter | GMS_MAP_DNP.INV001_52RC_Status | 52RC Status | 469 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Inverter Status | Inverter | GMS_MAP_DNP.INV001_Inverter_Status | Inverter Status | 470 | 0=GB, 1=DEB | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Circuit Error UF303 | Inverter | GMS_MAP_DNP.INV001_Control_Circuit_Error_UF303 | Control Circuit Error UF303 | 471 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Circuit Error UF305 | Inverter | GMS_MAP_DNP.INV001_Control_Circuit_Error_UF305 | Control Circuit Error UF305 | 472 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Circuit Error UF306 | Inverter | GMS_MAP_DNP.INV001_Control_Circuit_Error_UF306 | Control Circuit Error UF306 | 473 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Circuit Abnormal | Inverter | GMS_MAP_DNP.INV001_DC_Circuit_Abnormal | DC Circuit Abnormal | 474 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Power Supply Abnormal | Inverter | GMS_MAP_DNP.INV001_Control_Power_Supply_Abnormal | Control Power Supply Abnormal | 475 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Curcuit Error UF301 | Inverter | GMS_MAP_DNP.INV001_Control_Curcuit_Error_UF301 | Control Curcuit Error UF301 | 476 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Zero Phase Overcurrent | Inverter | GMS_MAP_DNP.INV001_Zero_Phase_Overcurrent | Zero Phase Overcurrent | 477 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 1 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_1 | DC Overcurrent 1 | 478 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 2 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_2 | DC Overcurrent 2 | 479 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 3 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_3 | DC Overcurrent 3 | 480 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 4 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_4 | DC Overcurrent 4 | 481 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 5 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_5 | DC Overcurrent 5 | 482 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 6 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_6 | DC Overcurrent 6 | 483 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 7 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_7 | DC Overcurrent 7 | 484 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overcurrent 8 | Inverter | GMS_MAP_DNP.INV001_DC_Overcurrent_8 | DC Overcurrent 8 | 485 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Unbalance 2 | Inverter | GMS_MAP_DNP.INV001_DC_Unbalance_2 | DC Unbalance 2 | 486 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Inverter Overcurrent H | Inverter | GMS_MAP_DNP.INV001_Inverter_Overcurrent_H | Inverter Overcurrent H | 487 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Reverse Current 2 | Inverter | GMS_MAP_DNP.INV001_DC_Reverse_Current_2 | DC Reverse Current 2 | 488 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Emergency Stop Active | Inverter | GMS_MAP_DNP.INV001_Emergency_Stop_Active | Emergency Stop Active | 489 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_External Trip | Inverter | GMS_MAP_DNP.INV001_External_Trip | External Trip | 490 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Inverter Abnormal | Inverter | GMS_MAP_DNP.INV001_Inverter_Abnormal | Inverter Abnormal | 491 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Repeated Fault | Inverter | GMS_MAP_DNP.INV001_Repeated_Fault | Repeated Fault | 492 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Inv. OCL. Repeated | Inverter | GMS_MAP_DNP.INV001_Inv._OCL._Repeated | Inv. OCL. Repeated | 493 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Cooling Fan Abnormal | Inverter | GMS_MAP_DNP.INV001_Cooling_Fan_Abnormal | Cooling Fan Abnormal | 494 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Short Circuit | Inverter | GMS_MAP_DNP.INV001_DC_Short_Circuit | DC Short Circuit | 495 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Flash Memory Data Error | Inverter | GMS_MAP_DNP.INV001_Flash_Memory_Data_Error | Flash Memory Data Error | 496 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Curcuit Error UF302 | Inverter | GMS_MAP_DNP.INV001_Control_Curcuit_Error_UF302 | Control Curcuit Error UF302 | 497 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_52RC Off Faulire | Inverter | GMS_MAP_DNP.INV001_52RC_Off_Faulire | 52RC Off Faulire | 498 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ground Fault UF160 | Inverter | GMS_MAP_DNP.INV001_Ground_Fault_UF160 | Ground Fault UF160 | 499 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ground Fault UF161 | Inverter | GMS_MAP_DNP.INV001_Ground_Fault_UF161 | Ground Fault UF161 | 500 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Major Fault A | Inverter | GMS_MAP_DNP.INV001_Major_Fault_A | Major Fault A | 501 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Undervoltage | Inverter | GMS_MAP_DNP.INV001_DC_Undervoltage | DC Undervoltage | 502 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Power Faulure AC Undervoltage | Inverter | GMS_MAP_DNP.INV001_Control_Power_Faulure_AC_Undervoltage | Control Power Faulure AC Undervoltage | 503 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Power Faulure AC Overvoltage | Inverter | GMS_MAP_DNP.INV001_Control_Power_Faulure_AC_Overvoltage | Control Power Faulure AC Overvoltage | 504 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Unbalance 1 | Inverter | GMS_MAP_DNP.INV001_DC_Unbalance_1 | DC Unbalance 1 | 505 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Power Failure DC | Inverter | GMS_MAP_DNP.INV001_Control_Power_Failure_DC | Control Power Failure DC | 506 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Minor Fault A | Inverter | GMS_MAP_DNP.INV001_Minor_Fault_A | Minor Fault A | 507 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Control Circuit Error UF206 | Inverter | GMS_MAP_DNP.INV001_Control_Circuit_Error_UF206 | Control Circuit Error UF206 | 508 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Inverter Overcurrent L | Inverter | GMS_MAP_DNP.INV001_Inverter_Overcurrent_L | Inverter Overcurrent L | 509 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_AC Circuit Error | Inverter | GMS_MAP_DNP.INV001_AC_Circuit_Error | AC Circuit Error | 510 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_52RC On Failure | Inverter | GMS_MAP_DNP.INV001_52RC_On_Failure | 52RC On Failure | 511 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Checking Ground | Inverter | GMS_MAP_DNP.INV001_Checking_Ground | Checking Ground | 512 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_IGBT Overtemp | Inverter | GMS_MAP_DNP.INV001_IGBT_Overtemp | IGBT Overtemp | 513 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_External Minor Fault | Inverter | GMS_MAP_DNP.INV001_External_Minor_Fault | External Minor Fault | 514 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_72C On Failure | Inverter | GMS_MAP_DNP.INV001_72C_On_Failure | 72C On Failure | 515 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_72C Off Faulure | Inverter | GMS_MAP_DNP.INV001_72C_Off_Faulure | 72C Off Faulure | 516 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Grid Overvoltage | Inverter | GMS_MAP_DNP.INV001_Grid_Overvoltage | Grid Overvoltage | 517 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_INST AC Overvoltage | Inverter | GMS_MAP_DNP.INV001_INST_AC_Overvoltage | INST AC Overvoltage | 518 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Grid Undervolage | Inverter | GMS_MAP_DNP.INV001_Grid_Undervolage | Grid Undervolage | 519 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Short Time AC Unervoltage | Inverter | GMS_MAP_DNP.INV001_Short_Time_AC_Unervoltage | Short Time AC Unervoltage | 520 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Over Freequency | Inverter | GMS_MAP_DNP.INV001_Over_Freequency | Over Freequency | 521 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Under Frequency | Inverter | GMS_MAP_DNP.INV001_Under_Frequency | Under Frequency | 522 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Phase Rotation Erro | Inverter | GMS_MAP_DNP.INV001_Phase_Rotation_Error | Phase Rotation Erro | 523 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Open Phase | Inverter | GMS_MAP_DNP.INV001_Open_Phase | Open Phase | 524 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Voltage Phase Jump | Inverter | GMS_MAP_DNP.INV001_Voltage_Phase_Jump | Voltage Phase Jump | 525 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Synchro Loss | Inverter | GMS_MAP_DNP.INV001_Synchro_Loss | Synchro Loss | 526 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_External Grid Fault | Inverter | GMS_MAP_DNP.INV001_External_Grid_Fault | External Grid Fault | 527 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Zero Phase Overcurrent 2 | Inverter | GMS_MAP_DNP.INV001_Zero_Phase_Overcurrent_2 | Zero Phase Overcurrent 2 | 528 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ope Prohibition | Inverter | GMS_MAP_DNP.INV001_Ope_Prohibition | Ope Prohibition | 529 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Overvoltage | Inverter | GMS_MAP_DNP.INV001_DC_Overvoltage | DC Overvoltage | 530 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ground Fault UA 159 | Inverter | GMS_MAP_DNP.INV001_Ground_Fault_UA_159 | Ground Fault UA 159 | 531 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_SPD Error | Inverter | GMS_MAP_DNP.INV001_SPD_Error | SPD Error | 532 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Grid Voltage Rise | Inverter | GMS_MAP_DNP.INV001_Grid_Voltage_Rise | Grid Voltage Rise | 533 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ambient Over Temp | Inverter | GMS_MAP_DNP.INV001_Ambient_Over_Temp | Ambient Over Temp | 534 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Low Temp | Inverter | GMS_MAP_DNP.INV001_Low_Temp | Low Temp | 535 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Ground Fault UA162 | Inverter | GMS_MAP_DNP.INV001_Ground_Fault_UA162 | Ground Fault UA162 | 536 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Vent Fan Error | Inverter | GMS_MAP_DNP.INV001_Vent_Fan_Error | Vent Fan Error | 537 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Alarm A | Inverter | GMS_MAP_DNP.INV001_Alarm_A | Alarm A | 538 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_DC Current Unbalance | Inverter | GMS_MAP_DNP.INV001_DC_Current_Unbalance | DC Current Unbalance | 539 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_AutoStart On | Inverter | GMS_MAP_DNP.INV002_AutoStart On | AutoStart On |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Comm Fail | Inverter | GMS_MAP_DNP.INV002_Comm Fail | Comm Fail | 540 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Monitor Offline | Inverter | GMS_MAP_DNP.INV002_DC Monitor Offline | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Faulted | Inverter | GMS_MAP_DNP.INV002_Faulted | Faulted |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Locked Out | Inverter | GMS_MAP_DNP.INV002_Locked Out | Locked Out |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Master Control Enabled | Inverter | GMS_MAP_DNP.INV002_Master Control Enabled | Master Control Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Offline | Inverter | GMS_MAP_DNP.INV002_Offline | Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ramp Up Enabled | Inverter | GMS_MAP_DNP.INV002_Ramp Up Enabled | Ramp Up Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ramp Down Enabled | Inverter | GMS_MAP_DNP.INV002_Ramp Down Enabled | Ramp Down Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Real Power Curtailment Flag | Inverter | GMS_MAP_DNP.INV002_Real Power Curtailment Flag | Real Power Curtailment Flag |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Surge MOV Failed | Inverter | GMS_MAP_DNP.INV002_Surge MOV Failed | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Following Setpoint | Inverter | GMS_MAP_DNP.INV002_Following_Setpoint | Following Setpoint |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | TSN1_SUB1_INV002_Major Fault | Inverter | GMS_MAP_DNP.INV002_Major_Fault | Major Fault | 541 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Grid Fault | Inverter | GMS_MAP_DNP.INV002_Grid_Fault_ | Grid Fault | 542 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Alarm | Inverter | GMS_MAP_DNP.INV002_Alarm | Alarm | 543 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Minor Fault | Inverter | GMS_MAP_DNP.INV002_Minor_Fault | Minor Fault | 544 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Module 1 Faulted | Inverter | GMS_MAP_DNP.INV002_Module_1_Faulted | Module 1 Faulted | 545 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Module 2 Faulted | Inverter | GMS_MAP_DNP.INV002_Module_2_Faulted | Module 2 Faulted | 546 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Module 3 Faulted | Inverter | GMS_MAP_DNP.INV002_Module_3_Faulted | Module 3 Faulted | 547 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Module 4 Faulted | Inverter | GMS_MAP_DNP.INV002_Module_4_Faulted | Module 4 Faulted | 548 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Module 5 Faulted | Inverter | GMS_MAP_DNP.INV002_Module_5_Faulted | Module 5 Faulted | 549 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Remote Operation | Inverter | GMS_MAP_DNP.INV002_Remote_Operation | Remote Operation | 550 | 0=Disabled, 1=Enabled | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_72C Status | Inverter | GMS_MAP_DNP.INV002_72C_Status | 72C Status | 551 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Run Command Status | Inverter | GMS_MAP_DNP.INV002_Run_Command_Status | Run Command Status | 552 | 0=Stop, 1=Start | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_MPPT Mode | Inverter | GMS_MAP_DNP.INV002_MPPT_Mode | MPPT Mode | 553 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC-AVR Mode | Inverter | GMS_MAP_DNP.INV002_DC-AVR_Mode | DC-AVR Mode | 554 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_52RC Status | Inverter | GMS_MAP_DNP.INV002_52RC_Status | 52RC Status | 555 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Inverter Status | Inverter | GMS_MAP_DNP.INV002_Inverter_Status | Inverter Status | 556 | 0=GB, 1=DEB | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Circuit Error UF303 | Inverter | GMS_MAP_DNP.INV002_Control_Circuit_Error_UF303 | Control Circuit Error UF303 | 557 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Circuit Error UF305 | Inverter | GMS_MAP_DNP.INV002_Control_Circuit_Error_UF305 | Control Circuit Error UF305 | 558 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Circuit Error UF306 | Inverter | GMS_MAP_DNP.INV002_Control_Circuit_Error_UF306 | Control Circuit Error UF306 | 559 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Circuit Abnormal | Inverter | GMS_MAP_DNP.INV002_DC_Circuit_Abnormal | DC Circuit Abnormal | 560 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Power Supply Abnormal | Inverter | GMS_MAP_DNP.INV002_Control_Power_Supply_Abnormal | Control Power Supply Abnormal | 561 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Curcuit Error UF301 | Inverter | GMS_MAP_DNP.INV002_Control_Curcuit_Error_UF301 | Control Curcuit Error UF301 | 562 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Zero Phase Overcurrent | Inverter | GMS_MAP_DNP.INV002_Zero_Phase_Overcurrent | Zero Phase Overcurrent | 563 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 1 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_1 | DC Overcurrent 1 | 564 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 2 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_2 | DC Overcurrent 2 | 565 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 3 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_3 | DC Overcurrent 3 | 566 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 4 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_4 | DC Overcurrent 4 | 567 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 5 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_5 | DC Overcurrent 5 | 568 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 6 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_6 | DC Overcurrent 6 | 569 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 7 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_7 | DC Overcurrent 7 | 570 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overcurrent 8 | Inverter | GMS_MAP_DNP.INV002_DC_Overcurrent_8 | DC Overcurrent 8 | 571 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Unbalance 2 | Inverter | GMS_MAP_DNP.INV002_DC_Unbalance_2 | DC Unbalance 2 | 572 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Inverter Overcurrent H | Inverter | GMS_MAP_DNP.INV002_Inverter_Overcurrent_H | Inverter Overcurrent H | 573 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Reverse Current 2 | Inverter | GMS_MAP_DNP.INV002_DC_Reverse_Current_2 | DC Reverse Current 2 | 574 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Emergency Stop Active | Inverter | GMS_MAP_DNP.INV002_Emergency_Stop_Active | Emergency Stop Active | 575 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_External Trip | Inverter | GMS_MAP_DNP.INV002_External_Trip | External Trip | 576 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Inverter Abnormal | Inverter | GMS_MAP_DNP.INV002_Inverter_Abnormal | Inverter Abnormal | 577 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Repeated Fault | Inverter | GMS_MAP_DNP.INV002_Repeated_Fault | Repeated Fault | 578 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Inv. OCL. Repeated | Inverter | GMS_MAP_DNP.INV002_Inv._OCL._Repeated | Inv. OCL. Repeated | 579 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Cooling Fan Abnormal | Inverter | GMS_MAP_DNP.INV002_Cooling_Fan_Abnormal | Cooling Fan Abnormal | 580 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Short Circuit | Inverter | GMS_MAP_DNP.INV002_DC_Short_Circuit | DC Short Circuit | 581 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Flash Memory Data Error | Inverter | GMS_MAP_DNP.INV002_Flash_Memory_Data_Error | Flash Memory Data Error | 582 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Curcuit Error UF302 | Inverter | GMS_MAP_DNP.INV002_Control_Curcuit_Error_UF302 | Control Curcuit Error UF302 | 583 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_52RC Off Faulire | Inverter | GMS_MAP_DNP.INV002_52RC_Off_Faulire | 52RC Off Faulire | 584 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ground Fault UF160 | Inverter | GMS_MAP_DNP.INV002_Ground_Fault_UF160 | Ground Fault UF160 | 585 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ground Fault UF161 | Inverter | GMS_MAP_DNP.INV002_Ground_Fault_UF161 | Ground Fault UF161 | 586 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Major Fault A | Inverter | GMS_MAP_DNP.INV002_Major_Fault_A | Major Fault A | 587 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Undervoltage | Inverter | GMS_MAP_DNP.INV002_DC_Undervoltage | DC Undervoltage | 588 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Power Faulure AC Undervoltage | Inverter | GMS_MAP_DNP.INV002_Control_Power_Faulure_AC_Undervoltage | Control Power Faulure AC Undervoltage | 589 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Power Faulure AC Overvoltage | Inverter | GMS_MAP_DNP.INV002_Control_Power_Faulure_AC_Overvoltage | Control Power Faulure AC Overvoltage | 590 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Unbalance 1 | Inverter | GMS_MAP_DNP.INV002_DC_Unbalance_1 | DC Unbalance 1 | 591 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Power Failure DC | Inverter | GMS_MAP_DNP.INV002_Control_Power_Failure_DC | Control Power Failure DC | 592 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Minor Fault A | Inverter | GMS_MAP_DNP.INV002_Minor_Fault_A | Minor Fault A | 593 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Control Circuit Error UF206 | Inverter | GMS_MAP_DNP.INV002_Control_Circuit_Error_UF206 | Control Circuit Error UF206 | 594 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Inverter Overcurrent L | Inverter | GMS_MAP_DNP.INV002_Inverter_Overcurrent_L | Inverter Overcurrent L | 595 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_AC Circuit Error | Inverter | GMS_MAP_DNP.INV002_AC_Circuit_Error | AC Circuit Error | 596 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_52RC On Failure | Inverter | GMS_MAP_DNP.INV002_52RC_On_Failure | 52RC On Failure | 597 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Checking Ground | Inverter | GMS_MAP_DNP.INV002_Checking_Ground | Checking Ground | 598 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_IGBT Overtemp | Inverter | GMS_MAP_DNP.INV002_IGBT_Overtemp | IGBT Overtemp | 599 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_External Minor Fault | Inverter | GMS_MAP_DNP.INV002_External_Minor_Fault | External Minor Fault | 600 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_72C On Failure | Inverter | GMS_MAP_DNP.INV002_72C_On_Failure | 72C On Failure | 601 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_72C Off Faulure | Inverter | GMS_MAP_DNP.INV002_72C_Off_Faulure | 72C Off Faulure | 602 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Grid Overvoltage | Inverter | GMS_MAP_DNP.INV002_Grid_Overvoltage | Grid Overvoltage | 603 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_INST AC Overvoltage | Inverter | GMS_MAP_DNP.INV002_INST_AC_Overvoltage | INST AC Overvoltage | 604 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Grid Undervolage | Inverter | GMS_MAP_DNP.INV002_Grid_Undervolage | Grid Undervolage | 605 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Short Time AC Unervoltage | Inverter | GMS_MAP_DNP.INV002_Short_Time_AC_Unervoltage | Short Time AC Unervoltage | 606 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Over Freequency | Inverter | GMS_MAP_DNP.INV002_Over_Freequency | Over Freequency | 607 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Under Frequency | Inverter | GMS_MAP_DNP.INV002_Under_Frequency | Under Frequency | 608 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Phase Rotation Erro | Inverter | GMS_MAP_DNP.INV002_Phase_Rotation_Error | Phase Rotation Erro | 609 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Open Phase | Inverter | GMS_MAP_DNP.INV002_Open_Phase | Open Phase | 610 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Voltage Phase Jump | Inverter | GMS_MAP_DNP.INV002_Voltage_Phase_Jump | Voltage Phase Jump | 611 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Synchro Loss | Inverter | GMS_MAP_DNP.INV002_Synchro_Loss | Synchro Loss | 612 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_External Grid Fault | Inverter | GMS_MAP_DNP.INV002_External_Grid_Fault | External Grid Fault | 613 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Zero Phase Overcurrent 2 | Inverter | GMS_MAP_DNP.INV002_Zero_Phase_Overcurrent_2 | Zero Phase Overcurrent 2 | 614 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ope Prohibition | Inverter | GMS_MAP_DNP.INV002_Ope_Prohibition | Ope Prohibition | 615 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Overvoltage | Inverter | GMS_MAP_DNP.INV002_DC_Overvoltage | DC Overvoltage | 616 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ground Fault UA 159 | Inverter | GMS_MAP_DNP.INV002_Ground_Fault_UA_159 | Ground Fault UA 159 | 617 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_SPD Error | Inverter | GMS_MAP_DNP.INV002_SPD_Error | SPD Error | 618 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Grid Voltage Rise | Inverter | GMS_MAP_DNP.INV002_Grid_Voltage_Rise | Grid Voltage Rise | 619 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ambient Over Temp | Inverter | GMS_MAP_DNP.INV002_Ambient_Over_Temp | Ambient Over Temp | 620 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Low Temp | Inverter | GMS_MAP_DNP.INV002_Low_Temp | Low Temp | 621 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Ground Fault UA162 | Inverter | GMS_MAP_DNP.INV002_Ground_Fault_UA162 | Ground Fault UA162 | 622 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Vent Fan Error | Inverter | GMS_MAP_DNP.INV002_Vent_Fan_Error | Vent Fan Error | 623 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Alarm A | Inverter | GMS_MAP_DNP.INV002_Alarm_A | Alarm A | 624 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_DC Current Unbalance | Inverter | GMS_MAP_DNP.INV002_DC_Current_Unbalance | DC Current Unbalance | 625 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_AutoStart On | Inverter | GMS_MAP_DNP.INV003_AutoStart On | AutoStart On |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Comm Fail | Inverter | GMS_MAP_DNP.INV003_Comm Fail | Comm Fail | 626 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Monitor Offline | Inverter | GMS_MAP_DNP.INV003_DC Monitor Offline | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Faulted | Inverter | GMS_MAP_DNP.INV003_Faulted | Faulted |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Locked Out | Inverter | GMS_MAP_DNP.INV003_Locked Out | Locked Out |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Master Control Enabled | Inverter | GMS_MAP_DNP.INV003_Master Control Enabled | Master Control Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Offline | Inverter | GMS_MAP_DNP.INV003_Offline | Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ramp Up Enabled | Inverter | GMS_MAP_DNP.INV003_Ramp Up Enabled | Ramp Up Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ramp Down Enabled | Inverter | GMS_MAP_DNP.INV003_Ramp Down Enabled | Ramp Down Enabled |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Real Power Curtailment Flag | Inverter | GMS_MAP_DNP.INV003_Real Power Curtailment Flag | Real Power Curtailment Flag |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Surge MOV Failed | Inverter | GMS_MAP_DNP.INV003_Surge MOV Failed | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Following Setpoint | Inverter | GMS_MAP_DNP.INV003_Following_Setpoint | Following Setpoint |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | TSN1_SUB1_INV003_Major Fault | Inverter | GMS_MAP_DNP.INV003_Major_Fault | Major Fault | 627 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Grid Fault | Inverter | GMS_MAP_DNP.INV003_Grid_Fault_ | Grid Fault | 628 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Alarm | Inverter | GMS_MAP_DNP.INV003_Alarm | Alarm | 629 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Minor Fault | Inverter | GMS_MAP_DNP.INV003_Minor_Fault | Minor Fault | 630 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Module 1 Faulted | Inverter | GMS_MAP_DNP.INV003_Module_1_Faulted | Module 1 Faulted | 631 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Module 2 Faulted | Inverter | GMS_MAP_DNP.INV003_Module_2_Faulted | Module 2 Faulted | 632 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Module 3 Faulted | Inverter | GMS_MAP_DNP.INV003_Module_3_Faulted | Module 3 Faulted | 633 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Module 4 Faulted | Inverter | GMS_MAP_DNP.INV003_Module_4_Faulted | Module 4 Faulted | 634 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Module 5 Faulted | Inverter | GMS_MAP_DNP.INV003_Module_5_Faulted | Module 5 Faulted | 635 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Remote Operation | Inverter | GMS_MAP_DNP.INV003_Remote_Operation | Remote Operation | 636 | 0=Disabled, 1=Enabled | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_72C Status | Inverter | GMS_MAP_DNP.INV003_72C_Status | 72C Status | 637 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Run Command Status | Inverter | GMS_MAP_DNP.INV003_Run_Command_Status | Run Command Status | 638 | 0=Stop, 1=Start | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_MPPT Mode | Inverter | GMS_MAP_DNP.INV003_MPPT_Mode | MPPT Mode | 639 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC-AVR Mode | Inverter | GMS_MAP_DNP.INV003_DC-AVR_Mode | DC-AVR Mode | 640 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_52RC Status | Inverter | GMS_MAP_DNP.INV003_52RC_Status | 52RC Status | 641 | 0=Off, 1=On | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Inverter Status | Inverter | GMS_MAP_DNP.INV003_Inverter_Status | Inverter Status | 642 | 0=GB, 1=DEB | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Circuit Error UF303 | Inverter | GMS_MAP_DNP.INV003_Control_Circuit_Error_UF303 | Control Circuit Error UF303 | 643 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Circuit Error UF305 | Inverter | GMS_MAP_DNP.INV003_Control_Circuit_Error_UF305 | Control Circuit Error UF305 | 644 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Circuit Error UF306 | Inverter | GMS_MAP_DNP.INV003_Control_Circuit_Error_UF306 | Control Circuit Error UF306 | 645 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Circuit Abnormal | Inverter | GMS_MAP_DNP.INV003_DC_Circuit_Abnormal | DC Circuit Abnormal | 646 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Power Supply Abnormal | Inverter | GMS_MAP_DNP.INV003_Control_Power_Supply_Abnormal | Control Power Supply Abnormal | 647 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Curcuit Error UF301 | Inverter | GMS_MAP_DNP.INV003_Control_Curcuit_Error_UF301 | Control Curcuit Error UF301 | 648 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Zero Phase Overcurrent | Inverter | GMS_MAP_DNP.INV003_Zero_Phase_Overcurrent | Zero Phase Overcurrent | 649 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 1 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_1 | DC Overcurrent 1 | 650 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 2 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_2 | DC Overcurrent 2 | 651 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 3 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_3 | DC Overcurrent 3 | 652 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 4 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_4 | DC Overcurrent 4 | 653 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 5 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_5 | DC Overcurrent 5 | 654 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 6 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_6 | DC Overcurrent 6 | 655 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 7 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_7 | DC Overcurrent 7 | 656 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overcurrent 8 | Inverter | GMS_MAP_DNP.INV003_DC_Overcurrent_8 | DC Overcurrent 8 | 657 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Unbalance 2 | Inverter | GMS_MAP_DNP.INV003_DC_Unbalance_2 | DC Unbalance 2 | 658 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Inverter Overcurrent H | Inverter | GMS_MAP_DNP.INV003_Inverter_Overcurrent_H | Inverter Overcurrent H | 659 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Reverse Current 2 | Inverter | GMS_MAP_DNP.INV003_DC_Reverse_Current_2 | DC Reverse Current 2 | 660 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Emergency Stop Active | Inverter | GMS_MAP_DNP.INV003_Emergency_Stop_Active | Emergency Stop Active | 661 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_External Trip | Inverter | GMS_MAP_DNP.INV003_External_Trip | External Trip | 662 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Inverter Abnormal | Inverter | GMS_MAP_DNP.INV003_Inverter_Abnormal | Inverter Abnormal | 663 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Repeated Fault | Inverter | GMS_MAP_DNP.INV003_Repeated_Fault | Repeated Fault | 664 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Inv. OCL. Repeated | Inverter | GMS_MAP_DNP.INV003_Inv._OCL._Repeated | Inv. OCL. Repeated | 665 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Cooling Fan Abnormal | Inverter | GMS_MAP_DNP.INV003_Cooling_Fan_Abnormal | Cooling Fan Abnormal | 666 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Short Circuit | Inverter | GMS_MAP_DNP.INV003_DC_Short_Circuit | DC Short Circuit | 667 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Flash Memory Data Error | Inverter | GMS_MAP_DNP.INV003_Flash_Memory_Data_Error | Flash Memory Data Error | 668 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Curcuit Error UF302 | Inverter | GMS_MAP_DNP.INV003_Control_Curcuit_Error_UF302 | Control Curcuit Error UF302 | 669 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_52RC Off Faulire | Inverter | GMS_MAP_DNP.INV003_52RC_Off_Faulire | 52RC Off Faulire | 670 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ground Fault UF160 | Inverter | GMS_MAP_DNP.INV003_Ground_Fault_UF160 | Ground Fault UF160 | 671 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ground Fault UF161 | Inverter | GMS_MAP_DNP.INV003_Ground_Fault_UF161 | Ground Fault UF161 | 672 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Major Fault A | Inverter | GMS_MAP_DNP.INV003_Major_Fault_A | Major Fault A | 673 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Undervoltage | Inverter | GMS_MAP_DNP.INV003_DC_Undervoltage | DC Undervoltage | 674 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Power Faulure AC Undervoltage | Inverter | GMS_MAP_DNP.INV003_Control_Power_Faulure_AC_Undervoltage | Control Power Faulure AC Undervoltage | 675 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Power Faulure AC Overvoltage | Inverter | GMS_MAP_DNP.INV003_Control_Power_Faulure_AC_Overvoltage | Control Power Faulure AC Overvoltage | 676 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Unbalance 1 | Inverter | GMS_MAP_DNP.INV003_DC_Unbalance_1 | DC Unbalance 1 | 677 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Power Failure DC | Inverter | GMS_MAP_DNP.INV003_Control_Power_Failure_DC | Control Power Failure DC | 678 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Minor Fault A | Inverter | GMS_MAP_DNP.INV003_Minor_Fault_A | Minor Fault A | 679 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Control Circuit Error UF206 | Inverter | GMS_MAP_DNP.INV003_Control_Circuit_Error_UF206 | Control Circuit Error UF206 | 680 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Inverter Overcurrent L | Inverter | GMS_MAP_DNP.INV003_Inverter_Overcurrent_L | Inverter Overcurrent L | 681 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_AC Circuit Error | Inverter | GMS_MAP_DNP.INV003_AC_Circuit_Error | AC Circuit Error | 682 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_52RC On Failure | Inverter | GMS_MAP_DNP.INV003_52RC_On_Failure | 52RC On Failure | 683 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Checking Ground | Inverter | GMS_MAP_DNP.INV003_Checking_Ground | Checking Ground | 684 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_IGBT Overtemp | Inverter | GMS_MAP_DNP.INV003_IGBT_Overtemp | IGBT Overtemp | 685 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_External Minor Fault | Inverter | GMS_MAP_DNP.INV003_External_Minor_Fault | External Minor Fault | 686 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_72C On Failure | Inverter | GMS_MAP_DNP.INV003_72C_On_Failure | 72C On Failure | 687 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_72C Off Faulure | Inverter | GMS_MAP_DNP.INV003_72C_Off_Faulure | 72C Off Faulure | 688 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Grid Overvoltage | Inverter | GMS_MAP_DNP.INV003_Grid_Overvoltage | Grid Overvoltage | 689 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_INST AC Overvoltage | Inverter | GMS_MAP_DNP.INV003_INST_AC_Overvoltage | INST AC Overvoltage | 690 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Grid Undervolage | Inverter | GMS_MAP_DNP.INV003_Grid_Undervolage | Grid Undervolage | 691 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Short Time AC Unervoltage | Inverter | GMS_MAP_DNP.INV003_Short_Time_AC_Unervoltage | Short Time AC Unervoltage | 692 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Over Freequency | Inverter | GMS_MAP_DNP.INV003_Over_Freequency | Over Freequency | 693 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Under Frequency | Inverter | GMS_MAP_DNP.INV003_Under_Frequency | Under Frequency | 694 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Phase Rotation Erro | Inverter | GMS_MAP_DNP.INV003_Phase_Rotation_Error | Phase Rotation Erro | 695 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Open Phase | Inverter | GMS_MAP_DNP.INV003_Open_Phase | Open Phase | 696 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Voltage Phase Jump | Inverter | GMS_MAP_DNP.INV003_Voltage_Phase_Jump | Voltage Phase Jump | 697 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Synchro Loss | Inverter | GMS_MAP_DNP.INV003_Synchro_Loss | Synchro Loss | 698 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUBC_INV003_External Grid Fault | Inverter | GMS_MAP_DNP.INV003_External_Grid_Fault | External Grid Fault | 699 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Zero Phase Overcurrent 2 | Inverter | GMS_MAP_DNP.INV003_Zero_Phase_Overcurrent_2 | Zero Phase Overcurrent 2 | 700 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ope Prohibition | Inverter | GMS_MAP_DNP.INV003_Ope_Prohibition | Ope Prohibition | 701 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Overvoltage | Inverter | GMS_MAP_DNP.INV003_DC_Overvoltage | DC Overvoltage | 702 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ground Fault UA 159 | Inverter | GMS_MAP_DNP.INV003_Ground_Fault_UA_159 | Ground Fault UA 159 | 703 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_SPD Error | Inverter | GMS_MAP_DNP.INV003_SPD_Error | SPD Error | 704 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Grid Voltage Rise | Inverter | GMS_MAP_DNP.INV003_Grid_Voltage_Rise | Grid Voltage Rise | 705 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ambient Over Temp | Inverter | GMS_MAP_DNP.INV003_Ambient_Over_Temp | Ambient Over Temp | 706 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Low Temp | Inverter | GMS_MAP_DNP.INV003_Low_Temp | Low Temp | 707 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Ground Fault UA162 | Inverter | GMS_MAP_DNP.INV003_Ground_Fault_UA162 | Ground Fault UA162 | 708 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Vent Fan Error | Inverter | GMS_MAP_DNP.INV003_Vent_Fan_Error | Vent Fan Error | 709 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Alarm A | Inverter | GMS_MAP_DNP.INV003_Alarm_A | Alarm A | 710 | 0=Normal, 1=Alarm | Not Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_DC Current Unbalance | Inverter | GMS_MAP_DNP.INV003_DC_Current_Unbalance | DC Current Unbalance | 711 | 0=Normal, 1=Alarm | Not Requested-Available
Counters | [6 empty] | n/a
Substation | DeviceID | Point Name | Device Type | Native_RTAC_Point_Name | Description | DNP Index | Units | Availability | Rollover
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_A_Phase_Energy_Received | Phase Energy Received | 4 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_B_Phase_Energy_Received | Phase Energy Received | 1 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_C_Phase_Energy_Received | Phase Energy Received | 2 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_A_Phase_Energy_Delivered | Phase Energy Delivered | 3 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_B_Phase_Energy_Delivered | Phase Energy Delivered | 4 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_C_Phase_Energy_Delivered | Phase Energy Delivered | 5 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Reactive Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 6 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Reactive Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 7 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Reactive Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 8 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_A Phase Reactive Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 9 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_B Phase Reactive Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 10 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_C Phase Reactive Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 11 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Energy_Received | Energy Received | 12 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Energy_Delivered | Energy Delivered | 13 | MWh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Reactive Energy Received | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Reactive_Energy_Received | Reactive Energy Received | 14 | MVARh | Requested-Available
SUB1 | SEL-735-MTRL1 HS | TSN1_SUB1_SEL-735-MTRL1 HS_Reactive Energy Delivered | Meter | GMS_MAP_DNP.SEL_735_MTRL1_Reactive_Energy_Delivered | Reactive Energy Delivered | 15 | MVARh | Requested-Available
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Energy_Received | Energy Received | 16 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Energy_Delivered | Energy Delivered | 17 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Reactive_Energy_Received | Reactive Energy Received | 18 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_Reactive_Energy_Delivered | Reactive Energy Delivered | 19 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A_Phase_Energy_Received | Phase Energy Received | 20 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B_Phase_Energy_Received | Phase Energy Received | 21 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C_Phase_Energy_Received | Phase Energy Received | 22 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A_Phase_Energy_Delivered | Phase Energy Delivered | 23 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B_Phase_Energy_Delivered | Phase Energy Delivered | 24 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C_Phase_Energy_Delivered | Phase Energy Delivered | 25 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 26 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 27 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 28 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 29 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 30 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1H | TSN1_SUB1_SEL-351-11T1H_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1H_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 31 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Energy_Received | Energy Received | 32 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Energy_Delivered | Energy Delivered | 33 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Reactive_Energy_Received | Reactive Energy Received | 34 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_Reactive_Energy_Delivered | Reactive Energy Delivered | 35 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A_Phase_Energy_Received | Phase Energy Received | 36 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B_Phase_Energy_Received | Phase Energy Received | 37 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C_Phase_Energy_Received | Phase Energy Received | 38 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A_Phase_Energy_Delivered | Phase Energy Delivered | 39 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B_Phase_Energy_Delivered | Phase Energy Delivered | 40 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C_Phase_Energy_Delivered | Phase Energy Delivered | 41 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 42 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 43 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 44 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 45 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 46 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T1L | TSN1_SUB1_SEL-351-11T1L_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T1L_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 47 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Energy_Received | Energy Received | 48 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Energy_Delivered | Energy Delivered | 49 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Reactive_Energy_Received | Reactive Energy Received | 50 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_Reactive_Energy_Delivered | Reactive Energy Delivered | 51 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A_Phase_Energy_Received | Phase Energy Received | 52 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B_Phase_Energy_Received | Phase Energy Received | 53 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C_Phase_Energy_Received | Phase Energy Received | 54 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A_Phase_Energy_Delivered | Phase Energy Delivered | 55 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B_Phase_Energy_Delivered | Phase Energy Delivered | 56 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C_Phase_Energy_Delivered | Phase Energy Delivered | 57 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 58 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 59 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 60 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 61 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 62 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F11 | TSN1_SUB1_SEL-351-F11_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F11_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 63 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Energy_Received | Energy Received | 64 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Energy_Delivered | Energy Delivered | 65 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Reactive_Energy_Received | Reactive Energy Received | 66 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_Reactive_Energy_Delivered | Reactive Energy Delivered | 67 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A_Phase_Energy_Received | Phase Energy Received | 68 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B_Phase_Energy_Received | Phase Energy Received | 69 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C_Phase_Energy_Received | Phase Energy Received | 70 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A_Phase_Energy_Delivered | Phase Energy Delivered | 71 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B_Phase_Energy_Delivered | Phase Energy Delivered | 72 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C_Phase_Energy_Delivered | Phase Energy Delivered | 73 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 74 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 75 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 76 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 77 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 78 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F12 | TSN1_SUB1_SEL-351-F12_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F12_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 79 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Energy_Received | Energy Received | 80 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Energy_Delivered | Energy Delivered | 81 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Reactive_Energy_Received | Reactive Energy Received | 82 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_Reactive_Energy_Delivered | Reactive Energy Delivered | 83 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A_Phase_Energy_Received | Phase Energy Received | 84 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B_Phase_Energy_Received | Phase Energy Received | 85 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C_Phase_Energy_Received | Phase Energy Received | 86 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A_Phase_Energy_Delivered | Phase Energy Delivered | 87 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B_Phase_Energy_Delivered | Phase Energy Delivered | 88 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C_Phase_Energy_Delivered | Phase Energy Delivered | 89 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 90 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 91 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 92 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 93 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 94 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F13 | TSN1_SUB1_SEL-351-F13_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F13_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 95 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Energy_Received | Energy Received | 96 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Energy_Delivered | Energy Delivered | 97 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Reactive_Energy_Received | Reactive Energy Received | 98 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_Reactive_Energy_Delivered | Reactive Energy Delivered | 99 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A_Phase_Energy_Received | Phase Energy Received | 100 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B_Phase_Energy_Received | Phase Energy Received | 101 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C_Phase_Energy_Received | Phase Energy Received | 102 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A_Phase_Energy_Delivered | Phase Energy Delivered | 103 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B_Phase_Energy_Delivered | Phase Energy Delivered | 104 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C_Phase_Energy_Delivered | Phase Energy Delivered | 105 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 106 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 107 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 108 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 109 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 110 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2H | TSN1_SUB1_SEL-351-11T2H_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2H_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 111 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Energy_Received | Energy Received | 112 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Energy_Delivered | Energy Delivered | 113 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Reactive_Energy_Received | Reactive Energy Received | 114 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_Reactive_Energy_Delivered | Reactive Energy Delivered | 115 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A_Phase_Energy_Received | Phase Energy Received | 116 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B_Phase_Energy_Received | Phase Energy Received | 117 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C_Phase_Energy_Received | Phase Energy Received | 118 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A_Phase_Energy_Delivered | Phase Energy Delivered | 119 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B_Phase_Energy_Delivered | Phase Energy Delivered | 120 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C_Phase_Energy_Delivered | Phase Energy Delivered | 121 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 122 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 123 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 124 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 125 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 126 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-11T2L | TSN1_SUB1_SEL-351-11T2L_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11T2L_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 127 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Energy_Received | Energy Received | 128 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Energy_Delivered | Energy Delivered | 129 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Reactive_Energy_Received | Reactive Energy Received | 130 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_Reactive_Energy_Delivered | Reactive Energy Delivered | 131 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A_Phase_Energy_Received | Phase Energy Received | 132 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B_Phase_Energy_Received | Phase Energy Received | 133 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C_Phase_Energy_Received | Phase Energy Received | 134 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A_Phase_Energy_Delivered | Phase Energy Delivered | 135 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B_Phase_Energy_Delivered | Phase Energy Delivered | 136 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C_Phase_Energy_Delivered | Phase Energy Delivered | 137 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 138 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 139 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 140 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 141 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 142 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F21 | TSN1_SUB1_SEL-351-F21_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F21_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 143 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Energy_Received | Energy Received | 144 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Energy_Delivered | Energy Delivered | 145 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Reactive_Energy_Received | Reactive Energy Received | 146 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_Reactive_Energy_Delivered | Reactive Energy Delivered | 147 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A_Phase_Energy_Received | Phase Energy Received | 148 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B_Phase_Energy_Received | Phase Energy Received | 149 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C_Phase_Energy_Received | Phase Energy Received | 150 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A_Phase_Energy_Delivered | Phase Energy Delivered | 151 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B_Phase_Energy_Delivered | Phase Energy Delivered | 152 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C_Phase_Energy_Delivered | Phase Energy Delivered | 153 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 154 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 155 | oodles | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 156 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 157 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 158 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F22 | TSN1_SUB1_SEL-351-F22_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F22_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 159 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Energy_Received | Energy Received | 160 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Energy_Delivered | Energy Delivered | 161 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Reactive_Energy_Received | Reactive Energy Received | 162 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_Reactive_Energy_Delivered | Reactive Energy Delivered | 163 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A_Phase_Energy_Received | Phase Energy Received | 164 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B_Phase_Energy_Received | Phase Energy Received | 165 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C_Phase_Energy_Received | Phase Energy Received | 166 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A_Phase_Energy_Delivered | Phase Energy Delivered | 167 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B_Phase_Energy_Delivered | Phase Energy Delivered | 168 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C_Phase_Energy_Delivered | Phase Energy Delivered | 169 | MWh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 170 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 171 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received | 172 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 173 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 174 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-351-F23 | TSN1_SUB1_SEL-351-F23_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_F23_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered | 175 | MVARh | Requested-Available | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Energy_Received | Energy Received |  | MWh | Requested-Available | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_A Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_B Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1P | TSN1_SUB1_SEL-387A-T1P_C Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1P_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Energy_Received | Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_A Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_B Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T1S | TSN1_SUB1_SEL-387A-T1S_C Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T1S_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Energy_Received | Energy Received |  | MWh | Requested-Available | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_A Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_B Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2P | TSN1_SUB1_SEL-387A-T2P_C Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2P_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Energy_Received | Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Reactive Energy Received | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_A Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_B Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-387A-T2S | TSN1_SUB1_SEL-387A-T2S_C Phase Reactive Energy Delivered | Transformer Relay | GMS_MAP_DNP.SEL_387A_T2S_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Applicable | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_Energy_Received | Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_C_Phase_Energy_Received | Phase Energy Received |  | tons | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V1 | TSN1_SUB1_SEL-487V-11V1_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V1_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_Energy_Received | Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_Energy_Delivered | Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_Reactive_Energy_Received | Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_Reactive_Energy_Delivered | Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_A_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_B_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_C_Phase_Energy_Received | Phase Energy Received |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_A_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_B_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_C_Phase_Energy_Delivered | Phase Energy Delivered |  | MWh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_A_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_B_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_C Phase Reactive Energy Received | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_C_Phase_Reactive_Energy_Received | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_A Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_A_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_SUB1_SEL-487V-11V2_B Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_B_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
SUB1 | SEL-487V-11V2 | TSN1_TEST_SEL-487V-11V2_C Phase Reactive Energy Delivered | Breaker Relay | GMS_MAP_DNP.SEL_351_11V2_C_Phase_Reactive_Energy_Delivered | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 4294967295
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native_RTAC_Point_Name | Description | DNP Index | Units | Availability
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 1 MW Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_Unit_1_MW_Setpoint | MW Setpoint | 0 | MW*100 | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 2 MW Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_Unit_2_MW_Setpoint | MW Setpoint | 1 | MW*100 | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS POI PF Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_POI_PF_Setpoint | GMS POI PF Setpoint | 2 | MVAR*100 | Requested-Available
SUB1 | PPC | TSN1_SUB71_PPC_GMS POI Voltage Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_POI_Voltage_Setpoint | GMS POI Voltage Setpoint | 3 | PF*100 | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS POI VAR Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_POI_VAR_Setpoint | GMS POI VAR Setpoint | 3 |  | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Up Rate Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Up_Rate_Setpoint | GMS Ramp Up Rate Setpoint | 5 | (MW/min)*100 | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Down Rate Setpoint | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Down_Rate_Setpoint | GMS Ramp Down Rate Setpoint | 6 | (MW/min)*100 | Requested-Available
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native_RTAC_Point_Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV001 | TSN1_SUB1_INV001_Start | Inverter | GMS_MAP_DNP.INV001_Start | Start | 0 | Latch On | Requested-Available
SUB1 | INV001 | TSN1_SUB1_INV001_Stop | Inverter | GMS_MAP_DNP.INV001_Stop | Stop | 1 | Latch On | Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Start | Inverter | GMS_MAP_DNP.INV002_Start | Start | 2 | Latch On | Requested-Available
SUB1 | INV002 | TSN1_SUB1_INV002_Stop | Inverter | GMS_MAP_DNP.INV002_Stop | Stop | 3 | Latch On | Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Start | Inverter | GMS_MAP_DNP.INV003_Start | Start | 4 | Latch On | Requested-Available
SUB1 | INV003 | TSN1_SUB1_INV003_Stop | Inverter | GMS_MAP_DNP.INV003_Stop | Stop | 5 | Latch On | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 1 Curtailment Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_Unit_1_Curtailment_Disable_Enable | Curtailment Disable/Enable | 137 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Unit 2 Curtailment Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_Unit_2_Curtailment_Disable_Enable | Curtailment Disable/Enable | 138 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Voltage Mode Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_Voltage_Mode_Disable_Enable | GMS Voltage Mode Disable/Enable | 139 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS PF Mode Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_PF_Mode_Disable_Enable | GMS PF Mode Disable/Enable | 140 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS MVAR Mode Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_MVAR_Mode_Disable_Enable | GMS MVAR Mode Disable/Enable | 141 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Up Rate Setpoint Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Up_Rate_Setpoint_Disable_Enable | GMS Ramp Up Rate Setpoint Disable/Enable | 142 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Ramp Down Rate Setpoint Disable/Enable | PPC | GMS_MAP_DNP.PPC_GMS_Ramp_Down_Rate_Setpoint_Disable_Enable | GMS Ramp Down Rate Setpoint Disable/Enable | 143 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52T1 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52T1_Breaker_Control | Breaker Controls | 144 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52T2 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52T2_Breaker_Control | Breaker Controls | 145 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F11 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F11_Breaker_Control | Breaker Controls | 146 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F12 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F12_Breaker_Control | Breaker Controls | 147 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F13 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F13_Breaker_Control | Breaker Controls | 148 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52V1 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52V1_Breaker_Control | Breaker Controls | 149 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89C11 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_89C11_Breaker_Control | Breaker Controls | 150 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89C12 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_89C12_Breaker_Control | Breaker Controls | 151 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F21 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F21_Breaker_Control | Breaker Controls | 152 | Latch Off = Trip, Latch On = Close | Tada
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F22 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F22_Breaker_Control | Breaker Controls | 153 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52F23 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52F23_Breaker_Control | Breaker Controls | 154 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 52V2 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_52V2_Breaker_Control | Breaker Controls | 155 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89C21 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_89C21_Breaker_Control | Breaker Controls | 156 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89C22 Breaker Control | PPC | GMS_MAP_DNP.PPC_GMS_89C22_Breaker_Control | Breaker Controls | 157 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89L1 MOD Control | PPC | GMS_MAP_DNP.PPC_GMS_89L1_MOD_Control | Breaker Controls | 158 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89T1 MOD Control | PPC | GMS_MAP_DNP.PPC_GMS_89T1_MOD_Control | Breaker Controls | 159 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS 89T2 MOD Control | PPC | GMS_MAP_DNP.PPC_GMS_89T2_MOD_Control | Breaker Controls | 160 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 001 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 001_Control | Inverter Controls | 161 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 002 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 002_Control | Inverter Controls | 162 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 003 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 003_Control | Inverter Controls | 163 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 004 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 004_Control | Inverter Controls | 164 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 005 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 005_Control | Inverter Controls | 165 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 006 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 006_Control | Inverter Controls | 166 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 007 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 007_Control | Inverter Controls | 167 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 008 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 008_Control | Inverter Controls | 168 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 009 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 009_Control | Inverter Controls | 169 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 010 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 010_Control | Inverter Controls | 170 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 011 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 011_Control | Inverter Controls | 171 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 012 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 012_Control | Inverter Controls | 172 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 013 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 013_Control | Inverter Controls | 173 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 014 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 014_Control | Inverter Controls | 174 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 015 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 015_Control | Inverter Controls | 175 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 016 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 016_Control | Inverter Controls | 176 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 017 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 017_Control | Inverter Controls | 177 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 018 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 018_Control | Inverter Controls | 178 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 019 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 019_Control | Inverter Controls | 179 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 020 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 020_Control | Inverter Controls | 180 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 021 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 021_Control | Inverter Controls | 181 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 022 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 022_Control | Inverter Controls | 182 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 023 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 023_Control | Inverter Controls | 183 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 024 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 024_Control | Inverter Controls | 184 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 025 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 025_Control | Inverter Controls | 185 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 026 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 026_Control | Inverter Controls | 186 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 027 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 027_Control | Inverter Controls | 187 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 028 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 028_Control | Inverter Controls | 188 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 029 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 029_Control | Inverter Controls | 189 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 030 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 030_Control | Inverter Controls | 190 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 031 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 031_Control | Inverter Controls | 191 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 032 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 032_Control | Inverter Controls | 192 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 033 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 033_Control | Inverter Controls | 193 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 034 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 034_Control | Inverter Controls | 194 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 035 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 035_Control | Inverter Controls | 195 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 036 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 036_Control | Inverter Controls | 196 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 037 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 037_Control | Inverter Controls | 197 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 038 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 038_Control | Inverter Controls | 198 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 039 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 039_Control | Inverter Controls | 199 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 040 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 040_Control | Inverter Controls | 200 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 041 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 041_Control | Inverter Controls | 201 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 042 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 042_Control | Inverter Controls | 202 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 043 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 043_Control | Inverter Controls | 203 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 044 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 044_Control | Inverter Controls | 204 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 045 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 045_Control | Inverter Controls | 205 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 046 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 046_Control | Inverter Controls | 206 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 047 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 047_Control | Inverter Controls | 207 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 048 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 048_Control | Inverter Controls | 208 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 049 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 049_Control | Inverter Controls | 209 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 050 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 050_Control | Inverter Controls | 210 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 051 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 051_Control | Inverter Controls | 211 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 052 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 052_Control | Inverter Controls | 212 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 053 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 053_Control | Inverter Controls | 213 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 054 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 054_Control | Inverter Controls | 214 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 055 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 055_Control | Inverter Controls | 215 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 056 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 056_Control | Inverter Controls | 216 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 057 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 057_Control | Inverter Controls | 217 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 058 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 058_Control | Inverter Controls | 218 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 059 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 059_Control | Inverter Controls | 219 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 060 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 060_Control | Inverter Controls | 220 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 061 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 061_Control | Inverter Controls | 221 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 062 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 062_Control | Inverter Controls | 222 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 063 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 063_Control | Inverter Controls | 223 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 064 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 064_Control | Inverter Controls | 224 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 065 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 065_Control | Inverter Controls | 225 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 066 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 066_Control | Inverter Controls | 226 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 067 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 067_Control | Inverter Controls | 227 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Inverter 068 Control | PPC | GMS_MAP_DNP.PPC_GMS_INV 068_Control | Inverter Controls | 228 | Latch On = Reset | Requested-Available
SUB1 | PPC | TSN1_SUB1_PPC_GMS Turbine # Control | PPC | GMS_MAP_DNP.PPC_GMS_Turbine_#_Control | Turbine Controls |  | Latch On = Reset | Requested-Not Available