SUB1 | INV072 | Daggett 3_SUB1_INV072_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Number of DU Channels | Inverter | inverter072_MODBUS.HR0653_duChannels | Number of DU Channels | 4204 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Number of Running Modules | Inverter | inverter072_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4205 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Operating State | Inverter | inverter072_MODBUS.HR1123_currentStatus | Operating State | 4206 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Power Factor | Inverter | inverter072_MODBUS.HR1011_pf3 | Power Factor | 4207 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV072 | Daggett 3_SUB1_INV072_Ramp Down | Inverter | inverter072_MODBUS.HR0286_dropGradient_p | Ramp Down | 4208 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Ramp Up | Inverter | inverter072_MODBUS.HR0282_riseGradient_p | Ramp Up | 4209 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power Delivered | Inverter | inverter072_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4210 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Reactive Power Delivered | Inverter | inverter072_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4211 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power | 4212 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Reactive Power | Inverter | inverter072_MODBUS.HR1009_q3_kvar | Reactive Power | 4213 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Reactive Power Mode | Inverter | inverter072_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4214 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Reactive Power Set Point Percent | Inverter | inverter072_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4215 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power AC Percent | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4216 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power-AC | Inverter | inverter072_MODBUS.HR1008_p3_kW | Real Power-AC | 4217 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power-DC | Inverter | inverter072_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4218 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Air Intake | Inverter | inverter072_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4219 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Cabinet | Inverter | inverter072_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4220 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-IGBT | Inverter | inverter072_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4221 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Temperature-Module | Inverter | inverter072_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4222 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage A-B | Inverter | inverter072_MODBUS.HR1002_vRS_V | Voltage A-B | 4223 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage B-C | Inverter | inverter072_MODBUS.HR1002_vST_V | Voltage B-C | 4224 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage C-A | Inverter | inverter072_MODBUS.HR1003_vTR_V | Voltage C-A | 4225 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC | Inverter | inverter072_MODBUS.HR1051_vdcBus_V | Voltage DC | 4226 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV072 | Daggett 3_SUB1_INV072_Fault Code 1 | Inverter | Inverter072_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Warning | Inverter | Inverter072_MODBUS.HRxxxx_currentWarning | Warning | 4228 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Internal Input Status | Inverter | Inverter072_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4229 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Internal Output Status | Inverter | Inverter072_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4230 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Module Fault Code | Inverter | Inverter072_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4231 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Internal Humidity | Inverter | Inverter072_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4232 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Humidity | Inverter | Inverter072_MODBUS.HRxxxx_humidity | Humidity | 4233 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Comms Fault Time | Inverter | Inverter072_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Status | Inverter | Inverter072_MODBUS.HRxxxx_M1_status | Module Status | 4235 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 IR | Inverter | Inverter072_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 IS | Inverter | Inverter072_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 IT | Inverter | Inverter072_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4240 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4242 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 P | Inverter | Inverter072_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4243 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Q | Inverter | Inverter072_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4244 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4245 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4246 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4247 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M1 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Status | Inverter | Inverter072_MODBUS.HRxxxx_M2_status | Module Status | 4250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 IR | Inverter | Inverter072_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4251 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 IS | Inverter | Inverter072_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 IT | Inverter | Inverter072_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4255 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4256 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4257 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 P | Inverter | Inverter072_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4258 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Q | Inverter | Inverter072_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4259 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4260 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4261 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4262 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4263 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M2 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4264 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Status | Inverter | Inverter072_MODBUS.HRxxxx_M3_status | Module Status | 4265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 IR | Inverter | Inverter072_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4266 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 IS | Inverter | Inverter072_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4267 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 IT | Inverter | Inverter072_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4268 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4269 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4270 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4271 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4272 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 P | Inverter | Inverter072_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4273 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Q | Inverter | Inverter072_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4274 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4275 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4276 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4277 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4278 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M3 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4279 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Status | Inverter | Inverter072_MODBUS.HRxxxx_M4_status | Module Status | 4280 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 IR | Inverter | Inverter072_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4281 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 IS | Inverter | Inverter072_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4282 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 IT | Inverter | Inverter072_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4283 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4284 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4285 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4286 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4287 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 P | Inverter | Inverter072_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4288 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Q | Inverter | Inverter072_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4289 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4290 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4291 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4292 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4293 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M4 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4294 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Status | Inverter | Inverter072_MODBUS.HRxxxx_M5_status | Module Status | 4295 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 IR | Inverter | Inverter072_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 IS | Inverter | Inverter072_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 IT | Inverter | Inverter072_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4299 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4300 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4301 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4302 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 P | Inverter | Inverter072_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4303 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Q | Inverter | Inverter072_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4304 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4305 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4306 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4308 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M5 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4309 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Status | Inverter | Inverter072_MODBUS.HRxxxx_M6_status | Module Status | 4310 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 IR | Inverter | Inverter072_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4311 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 IS | Inverter | Inverter072_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 IT | Inverter | Inverter072_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 IDC | Inverter | Inverter072_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 VDCP | Inverter | Inverter072_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4315 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 VDCN | Inverter | Inverter072_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 VDC | Inverter | Inverter072_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4317 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 P | Inverter | Inverter072_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4318 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Q | Inverter | Inverter072_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4319 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Ambient Temp | Inverter | Inverter072_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4320 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Max IGBT Temp | Inverter | Inverter072_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4321 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 IO Status | Inverter | Inverter072_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4322 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Hardware Version | Inverter | Inverter072_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_M6 Software Version | Inverter | Inverter072_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_A Phase Current | Inverter | inverter073_MODBUS.HR1004_i1_A | A Phase Current | 4325 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_B Phase Current | Inverter | inverter073_MODBUS.HR1005_i2_A | B Phase Current | 4326 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_C Phase Current | Inverter | inverter073_MODBUS.HR1006_i3_A | C Phase Current | 4327 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Bus Voltage | Inverter | inverter073_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4328 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV073 | Daggett 3_SUB1_INV073_Apparent Power | Inverter | inverter073_MODBUS.HR1010_s3_VA | Apparent Power | 4329 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 1 | Inverter | Inverter073_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC Input 1 | Inverter | Inverter073_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4331 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 2 | Inverter | Inverter073_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4332 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 2 | Inverter | Inverter073_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4333 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 3 | Inverter | Inverter073_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 3 | Inverter | Inverter073_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4335 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 4 | Inverter | Inverter073_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 4 | Inverter | Inverter073_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4337 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 5 | Inverter | Inverter073_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4338 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 5 | Inverter | Inverter073_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4339 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 6 | Inverter | Inverter073_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4340 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 6 | Inverter | Inverter073_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4341 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 7 | Inverter | Inverter073_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 7 | Inverter | Inverter073_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4343 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 8 | Inverter | Inverter073_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4344 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 8 | Inverter | Inverter073_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4345 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 9 | Inverter | Inverter073_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4346 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 9 | Inverter | Inverter073_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4347 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 10 | Inverter | Inverter073_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4348 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 10 | Inverter | Inverter073_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4349 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 11 | Inverter | Inverter073_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 11 | Inverter | Inverter073_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4351 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 12 | Inverter | Inverter073_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 12 | Inverter | Inverter073_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4353 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 13 | Inverter | Inverter073_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4354 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 13 | Inverter | Inverter073_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4355 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 14 | Inverter | Inverter073_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4356 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 14 | Inverter | Inverter073_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4357 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 15 | Inverter | Inverter073_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 15 | Inverter | Inverter073_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4359 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 16 | Inverter | Inverter073_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4360 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 16 | Inverter | Inverter073_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4361 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 17 | Inverter | Inverter073_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4362 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 17 | Inverter | Inverter073_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4363 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 18 | Inverter | Inverter073_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4364 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 18 | Inverter | Inverter073_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4365 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 19 | Inverter | Inverter073_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 19 | Inverter | Inverter073_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4367 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current DC Input 20 | Inverter | Inverter073_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC input 20 | Inverter | Inverter073_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4369 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current-AC | Inverter | inverter073_MODBUS.HR1007_i3Avg_A | Current-AC | 4370 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Current-DC | Inverter | inverter073_MODBUS.HR1062_idcInput_A | Current-DC | 4371 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Daily Energy Delivered | Inverter | inverter073_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4372 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power Set Point | Inverter | inverter073_MODBUS.HR0553_pRef | Real Power Set Point | 4373 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Reactive Power Set Point | Inverter | inverter073_MODBUS.HR0558_qRef | Reactive Power Set Point | 4374 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Frequency | Inverter | inverter073_MODBUS.HR1012_f3_Hz | Frequency | 4375 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV073 | Daggett 3_SUB1_INV073_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Insulation Resistance | Inverter | inverter073_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4376 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Number of DU Channels | Inverter | inverter073_MODBUS.HR0653_duChannels | Number of DU Channels | 4377 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Number of Running Modules | Inverter | inverter073_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4378 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Operating State | Inverter | inverter073_MODBUS.HR1123_currentStatus | Operating State | 4379 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Power Factor | Inverter | inverter073_MODBUS.HR1011_pf3 | Power Factor | 4380 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV073 | Daggett 3_SUB1_INV073_Ramp Down | Inverter | inverter073_MODBUS.HR0286_dropGradient_p | Ramp Down | 4381 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Ramp Up | Inverter | inverter073_MODBUS.HR0282_riseGradient_p | Ramp Up | 4382 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power Delivered | Inverter | inverter073_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4383 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Reactive Power Delivered | Inverter | inverter073_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4384 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power | 4385 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Reactive Power | Inverter | inverter073_MODBUS.HR1009_q3_kvar | Reactive Power | 4386 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Reactive Power Mode | Inverter | inverter073_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4387 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Reactive Power Set Point Percent | Inverter | inverter073_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4388 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power AC Percent | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4389 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power-AC | Inverter | inverter073_MODBUS.HR1008_p3_kW | Real Power-AC | 4390 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power-DC | Inverter | inverter073_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4391 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Air Intake | Inverter | inverter073_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4392 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Cabinet | Inverter | inverter073_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4393 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-IGBT | Inverter | inverter073_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4394 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Temperature-Module | Inverter | inverter073_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4395 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage A-B | Inverter | inverter073_MODBUS.HR1003_vRS_V | Voltage A-B | 4396 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage B-C | Inverter | inverter073_MODBUS.HR1002_vST_V | Voltage B-C | 4397 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage C-A | Inverter | inverter073_MODBUS.HR1003_vTR_V | Voltage C-A | 4398 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Voltage DC | Inverter | inverter073_MODBUS.HR1051_vdcBus_V | Voltage DC | 4399 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV073 | Daggett 3_SUB1_INV073_Fault Code 1 | Inverter | Inverter073_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Warning | Inverter | Inverter073_MODBUS.HRxxxx_currentWarning | Warning | 4401 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Internal Input Status | Inverter | Inverter073_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4402 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Internal Output Status | Inverter | Inverter073_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4403 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Module Fault Code | Inverter | Inverter073_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4404 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Internal Humidity | Inverter | Inverter073_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4405 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Humidity | Inverter | Inverter073_MODBUS.HRxxxx_humidity | Humidity | 4406 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_Comms Fault Time | Inverter | Inverter073_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Status | Inverter | Inverter073_MODBUS.HRxxxx_M1_status | Module Status | 4408 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 IR | Inverter | Inverter073_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 IS | Inverter | Inverter073_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 IT | Inverter | Inverter073_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4413 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4415 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 P | Inverter | Inverter073_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4416 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Q | Inverter | Inverter073_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4417 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4418 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4419 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4420 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M1 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Status | Inverter | Inverter073_MODBUS.HRxxxx_M2_status | Module Status | 4423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 IR | Inverter | Inverter073_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4424 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 IS | Inverter | Inverter073_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 IT | Inverter | Inverter073_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4428 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4429 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4430 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 P | Inverter | Inverter073_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4431 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Q | Inverter | Inverter073_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4432 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4433 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4434 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4435 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4436 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M2 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4437 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Status | Inverter | Inverter073_MODBUS.HRxxxx_M3_status | Module Status | 4438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 IR | Inverter | Inverter073_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4439 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 IS | Inverter | Inverter073_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4440 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 IT | Inverter | Inverter073_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4441 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4442 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4443 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4444 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4445 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 P | Inverter | Inverter073_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4446 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Q | Inverter | Inverter073_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4447 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4448 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4449 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4450 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4451 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M3 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4452 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Status | Inverter | Inverter073_MODBUS.HRxxxx_M4_status | Module Status | 4453 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 IR | Inverter | Inverter073_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4454 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 IS | Inverter | Inverter073_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4455 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 IT | Inverter | Inverter073_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4456 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4457 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4458 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4459 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4460 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 P | Inverter | Inverter073_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4461 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Q | Inverter | Inverter073_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4462 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4463 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4464 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4465 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4466 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M4 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4467 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Status | Inverter | Inverter073_MODBUS.HRxxxx_M5_status | Module Status | 4468 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 IR | Inverter | Inverter073_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 IS | Inverter | Inverter073_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 IT | Inverter | Inverter073_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4472 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4473 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4474 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4475 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 P | Inverter | Inverter073_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4476 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Q | Inverter | Inverter073_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4477 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4478 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4479 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4481 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M5 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4482 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Status | Inverter | Inverter073_MODBUS.HRxxxx_M6_status | Module Status | 4483 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 IR | Inverter | Inverter073_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4484 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 IS | Inverter | Inverter073_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 IT | Inverter | Inverter073_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 IDC | Inverter | Inverter073_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 VDCP | Inverter | Inverter073_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4488 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 VDCN | Inverter | Inverter073_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 VDC | Inverter | Inverter073_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4490 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 P | Inverter | Inverter073_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4491 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Q | Inverter | Inverter073_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4492 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Ambient Temp | Inverter | Inverter073_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4493 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Max IGBT Temp | Inverter | Inverter073_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4494 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 IO Status | Inverter | Inverter073_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4495 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Hardware Version | Inverter | Inverter073_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV073 | Daggett 3_SUB1_INV073_M6 Software Version | Inverter | Inverter073_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_A Phase Current | Inverter | inverter074_MODBUS.HR1004_i1_A | A Phase Current | 4498 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_B Phase Current | Inverter | inverter074_MODBUS.HR1005_i2_A | B Phase Current | 4499 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_C Phase Current | Inverter | inverter074_MODBUS.HR1006_i3_A | C Phase Current | 4500 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Bus Voltage | Inverter | inverter074_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4501 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV074 | Daggett 3_SUB1_INV074_Apparent Power | Inverter | inverter074_MODBUS.HR1010_s3_VA | Apparent Power | 4502 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 1 | Inverter | Inverter074_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC Input 1 | Inverter | Inverter074_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4504 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 2 | Inverter | Inverter074_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4505 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 2 | Inverter | Inverter074_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4506 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 3 | Inverter | Inverter074_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 3 | Inverter | Inverter074_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4508 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 4 | Inverter | Inverter074_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 4 | Inverter | Inverter074_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4510 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 5 | Inverter | Inverter074_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4511 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 5 | Inverter | Inverter074_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4512 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 6 | Inverter | Inverter074_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4513 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 6 | Inverter | Inverter074_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4514 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 7 | Inverter | Inverter074_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 7 | Inverter | Inverter074_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4516 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 8 | Inverter | Inverter074_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4517 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 8 | Inverter | Inverter074_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4518 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 9 | Inverter | Inverter074_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4519 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 9 | Inverter | Inverter074_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4520 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 10 | Inverter | Inverter074_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4521 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 10 | Inverter | Inverter074_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4522 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 11 | Inverter | Inverter074_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 11 | Inverter | Inverter074_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4524 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 12 | Inverter | Inverter074_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 12 | Inverter | Inverter074_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4526 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 13 | Inverter | Inverter074_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4527 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 13 | Inverter | Inverter074_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4528 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 14 | Inverter | Inverter074_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4529 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 14 | Inverter | Inverter074_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4530 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 15 | Inverter | Inverter074_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 15 | Inverter | Inverter074_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4532 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 16 | Inverter | Inverter074_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4533 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 16 | Inverter | Inverter074_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4534 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 17 | Inverter | Inverter074_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4535 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 17 | Inverter | Inverter074_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4536 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 18 | Inverter | Inverter074_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4537 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 18 | Inverter | Inverter074_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4538 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 19 | Inverter | Inverter074_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 19 | Inverter | Inverter074_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4540 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current DC Input 20 | Inverter | Inverter074_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC input 20 | Inverter | Inverter074_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4542 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current-AC | Inverter | inverter074_MODBUS.HR1007_i3Avg_A | Current-AC | 4543 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Current-DC | Inverter | inverter074_MODBUS.HR1062_idcInput_A | Current-DC | 4544 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Daily Energy Delivered | Inverter | inverter074_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4545 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power Set Point | Inverter | inverter074_MODBUS.HR0553_pRef | Real Power Set Point | 4546 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Reactive Power Set Point | Inverter | inverter074_MODBUS.HR0558_qRef | Reactive Power Set Point | 4547 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Frequency | Inverter | inverter074_MODBUS.HR1012_f3_Hz | Frequency | 4548 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV074 | Daggett 3_SUB1_INV074_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Insulation Resistance | Inverter | inverter074_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4549 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Number of DU Channels | Inverter | inverter074_MODBUS.HR0653_duChannels | Number of DU Channels | 4550 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Number of Running Modules | Inverter | inverter074_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4551 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Operating State | Inverter | inverter074_MODBUS.HR1123_currentStatus | Operating State | 4552 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Power Factor | Inverter | inverter074_MODBUS.HR1011_pf3 | Power Factor | 4553 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV074 | Daggett 3_SUB1_INV074_Ramp Down | Inverter | inverter074_MODBUS.HR0286_dropGradient_p | Ramp Down | 4554 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Ramp Up | Inverter | inverter074_MODBUS.HR0282_riseGradient_p | Ramp Up | 4555 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power Delivered | Inverter | inverter074_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4556 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Reactive Power Delivered | Inverter | inverter074_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4557 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power | 4558 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Reactive Power | Inverter | inverter074_MODBUS.HR1009_q3_kvar | Reactive Power | 4559 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Reactive Power Mode | Inverter | inverter074_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4560 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Reactive Power Set Point Percent | Inverter | inverter074_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4561 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power AC Percent | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4562 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power-AC | Inverter | inverter074_MODBUS.HR1008_p3_kW | Real Power-AC | 4563 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power-DC | Inverter | inverter074_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4564 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Air Intake | Inverter | inverter074_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4565 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Cabinet | Inverter | inverter074_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4566 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-IGBT | Inverter | inverter074_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4567 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Temperature-Module | Inverter | inverter074_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4568 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage A-B | Inverter | inverter074_MODBUS.HR1004_vRS_V | Voltage A-B | 4569 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage B-C | Inverter | inverter074_MODBUS.HR1002_vST_V | Voltage B-C | 4570 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage C-A | Inverter | inverter074_MODBUS.HR1003_vTR_V | Voltage C-A | 4571 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Voltage DC | Inverter | inverter074_MODBUS.HR1051_vdcBus_V | Voltage DC | 4572 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV074 | Daggett 3_SUB1_INV074_Fault Code 1 | Inverter | Inverter074_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Warning | Inverter | Inverter074_MODBUS.HRxxxx_currentWarning | Warning | 4574 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Internal Input Status | Inverter | Inverter074_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4575 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Internal Output Status | Inverter | Inverter074_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4576 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Module Fault Code | Inverter | Inverter074_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4577 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Internal Humidity | Inverter | Inverter074_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4578 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Humidity | Inverter | Inverter074_MODBUS.HRxxxx_humidity | Humidity | 4579 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_Comms Fault Time | Inverter | Inverter074_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Status | Inverter | Inverter074_MODBUS.HRxxxx_M1_status | Module Status | 4581 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 IR | Inverter | Inverter074_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 IS | Inverter | Inverter074_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 IT | Inverter | Inverter074_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4586 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4588 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 P | Inverter | Inverter074_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4589 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Q | Inverter | Inverter074_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4590 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4591 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4592 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4593 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M1 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Status | Inverter | Inverter074_MODBUS.HRxxxx_M2_status | Module Status | 4596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 IR | Inverter | Inverter074_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4597 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 IS | Inverter | Inverter074_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 IT | Inverter | Inverter074_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4601 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4602 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4603 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 P | Inverter | Inverter074_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4604 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Q | Inverter | Inverter074_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4605 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4606 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4607 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4608 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4609 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M2 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4610 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Status | Inverter | Inverter074_MODBUS.HRxxxx_M3_status | Module Status | 4611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 IR | Inverter | Inverter074_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4612 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 IS | Inverter | Inverter074_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4613 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 IT | Inverter | Inverter074_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4614 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4615 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4616 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4617 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4618 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 P | Inverter | Inverter074_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4619 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Q | Inverter | Inverter074_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4620 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4621 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4622 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4623 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4624 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M3 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4625 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Status | Inverter | Inverter074_MODBUS.HRxxxx_M4_status | Module Status | 4626 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 IR | Inverter | Inverter074_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4627 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 IS | Inverter | Inverter074_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4628 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 IT | Inverter | Inverter074_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4629 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4630 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4631 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4632 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4633 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 P | Inverter | Inverter074_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4634 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Q | Inverter | Inverter074_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4635 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4636 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4637 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4638 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4639 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M4 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4640 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Status | Inverter | Inverter074_MODBUS.HRxxxx_M5_status | Module Status | 4641 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 IR | Inverter | Inverter074_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 IS | Inverter | Inverter074_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 IT | Inverter | Inverter074_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4645 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4646 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4647 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4648 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 P | Inverter | Inverter074_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4649 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Q | Inverter | Inverter074_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4650 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4651 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4652 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4654 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M5 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4655 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Status | Inverter | Inverter074_MODBUS.HRxxxx_M6_status | Module Status | 4656 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 IR | Inverter | Inverter074_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4657 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 IS | Inverter | Inverter074_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 IT | Inverter | Inverter074_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 IDC | Inverter | Inverter074_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 VDCP | Inverter | Inverter074_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4661 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 VDCN | Inverter | Inverter074_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 VDC | Inverter | Inverter074_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4663 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 P | Inverter | Inverter074_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4664 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Q | Inverter | Inverter074_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4665 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Ambient Temp | Inverter | Inverter074_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4666 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Max IGBT Temp | Inverter | Inverter074_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4667 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 IO Status | Inverter | Inverter074_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4668 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Hardware Version | Inverter | Inverter074_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV074 | Daggett 3_SUB1_INV074_M6 Software Version | Inverter | Inverter074_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_A Phase Current | Inverter | inverter075_MODBUS.HR1004_i1_A | A Phase Current | 4671 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_B Phase Current | Inverter | inverter075_MODBUS.HR1005_i2_A | B Phase Current | 4672 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_C Phase Current | Inverter | inverter075_MODBUS.HR1006_i3_A | C Phase Current | 4673 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Bus Voltage | Inverter | inverter075_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4674 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV075 | Daggett 3_SUB1_INV075_Apparent Power | Inverter | inverter075_MODBUS.HR1010_s3_VA | Apparent Power | 4675 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 1 | Inverter | Inverter075_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC Input 1 | Inverter | Inverter075_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4677 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 2 | Inverter | Inverter075_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4678 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 2 | Inverter | Inverter075_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4679 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 3 | Inverter | Inverter075_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 3 | Inverter | Inverter075_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4681 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 4 | Inverter | Inverter075_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 4 | Inverter | Inverter075_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4683 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 5 | Inverter | Inverter075_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4684 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 5 | Inverter | Inverter075_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4685 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 6 | Inverter | Inverter075_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4686 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 6 | Inverter | Inverter075_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4687 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 7 | Inverter | Inverter075_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 7 | Inverter | Inverter075_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4689 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 8 | Inverter | Inverter075_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4690 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 8 | Inverter | Inverter075_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4691 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 9 | Inverter | Inverter075_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4692 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 9 | Inverter | Inverter075_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4693 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 10 | Inverter | Inverter075_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4694 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 10 | Inverter | Inverter075_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4695 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 11 | Inverter | Inverter075_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 11 | Inverter | Inverter075_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4697 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 12 | Inverter | Inverter075_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 12 | Inverter | Inverter075_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4699 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 13 | Inverter | Inverter075_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4700 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 13 | Inverter | Inverter075_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4701 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 14 | Inverter | Inverter075_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4702 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 14 | Inverter | Inverter075_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4703 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 15 | Inverter | Inverter075_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 15 | Inverter | Inverter075_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4705 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 16 | Inverter | Inverter075_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4706 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 16 | Inverter | Inverter075_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4707 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 17 | Inverter | Inverter075_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4708 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 17 | Inverter | Inverter075_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4709 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 18 | Inverter | Inverter075_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4710 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 18 | Inverter | Inverter075_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4711 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 19 | Inverter | Inverter075_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 19 | Inverter | Inverter075_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4713 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current DC Input 20 | Inverter | Inverter075_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC input 20 | Inverter | Inverter075_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4715 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current-AC | Inverter | inverter075_MODBUS.HR1007_i3Avg_A | Current-AC | 4716 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Current-DC | Inverter | inverter075_MODBUS.HR1062_idcInput_A | Current-DC | 4717 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Daily Energy Delivered | Inverter | inverter075_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4718 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power Set Point | Inverter | inverter075_MODBUS.HR0553_pRef | Real Power Set Point | 4719 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Reactive Power Set Point | Inverter | inverter075_MODBUS.HR0558_qRef | Reactive Power Set Point | 4720 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Frequency | Inverter | inverter075_MODBUS.HR1012_f3_Hz | Frequency | 4721 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV075 | Daggett 3_SUB1_INV075_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Insulation Resistance | Inverter | inverter075_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4722 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Number of DU Channels | Inverter | inverter075_MODBUS.HR0653_duChannels | Number of DU Channels | 4723 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Number of Running Modules | Inverter | inverter075_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4724 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Operating State | Inverter | inverter075_MODBUS.HR1123_currentStatus | Operating State | 4725 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Power Factor | Inverter | inverter075_MODBUS.HR1011_pf3 | Power Factor | 4726 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV075 | Daggett 3_SUB1_INV075_Ramp Down | Inverter | inverter075_MODBUS.HR0286_dropGradient_p | Ramp Down | 4727 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Ramp Up | Inverter | inverter075_MODBUS.HR0282_riseGradient_p | Ramp Up | 4728 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power Delivered | Inverter | inverter075_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4729 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Reactive Power Delivered | Inverter | inverter075_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4730 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power | 4731 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Reactive Power | Inverter | inverter075_MODBUS.HR1009_q3_kvar | Reactive Power | 4732 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Reactive Power Mode | Inverter | inverter075_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4733 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Reactive Power Set Point Percent | Inverter | inverter075_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4734 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power AC Percent | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4735 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power-AC | Inverter | inverter075_MODBUS.HR1008_p3_kW | Real Power-AC | 4736 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power-DC | Inverter | inverter075_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4737 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Air Intake | Inverter | inverter075_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4738 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Cabinet | Inverter | inverter075_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4739 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-IGBT | Inverter | inverter075_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4740 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Temperature-Module | Inverter | inverter075_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4741 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage A-B | Inverter | inverter075_MODBUS.HR1005_vRS_V | Voltage A-B | 4742 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage B-C | Inverter | inverter075_MODBUS.HR1002_vST_V | Voltage B-C | 4743 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage C-A | Inverter | inverter075_MODBUS.HR1003_vTR_V | Voltage C-A | 4744 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Voltage DC | Inverter | inverter075_MODBUS.HR1051_vdcBus_V | Voltage DC | 4745 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV075 | Daggett 3_SUB1_INV075_Fault Code 1 | Inverter | Inverter075_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Warning | Inverter | Inverter075_MODBUS.HRxxxx_currentWarning | Warning | 4747 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Internal Input Status | Inverter | Inverter075_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4748 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Internal Output Status | Inverter | Inverter075_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4749 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Module Fault Code | Inverter | Inverter075_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4750 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Internal Humidity | Inverter | Inverter075_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4751 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Humidity | Inverter | Inverter075_MODBUS.HRxxxx_humidity | Humidity | 4752 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_Comms Fault Time | Inverter | Inverter075_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Status | Inverter | Inverter075_MODBUS.HRxxxx_M1_status | Module Status | 4754 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 IR | Inverter | Inverter075_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 IS | Inverter | Inverter075_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 IT | Inverter | Inverter075_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4759 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4761 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 P | Inverter | Inverter075_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4762 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Q | Inverter | Inverter075_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4763 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4764 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4765 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4766 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M1 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Status | Inverter | Inverter075_MODBUS.HRxxxx_M2_status | Module Status | 4769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 IR | Inverter | Inverter075_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4770 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 IS | Inverter | Inverter075_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 IT | Inverter | Inverter075_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4774 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4775 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4776 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 P | Inverter | Inverter075_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4777 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Q | Inverter | Inverter075_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4778 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4779 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4780 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4781 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4782 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M2 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4783 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Status | Inverter | Inverter075_MODBUS.HRxxxx_M3_status | Module Status | 4784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 IR | Inverter | Inverter075_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4785 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 IS | Inverter | Inverter075_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4786 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 IT | Inverter | Inverter075_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4787 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4788 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4789 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4790 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4791 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 P | Inverter | Inverter075_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4792 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Q | Inverter | Inverter075_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4793 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4794 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4795 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4796 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4797 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M3 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4798 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Status | Inverter | Inverter075_MODBUS.HRxxxx_M4_status | Module Status | 4799 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 IR | Inverter | Inverter075_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4800 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 IS | Inverter | Inverter075_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4801 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 IT | Inverter | Inverter075_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4802 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4803 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4804 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4805 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4806 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 P | Inverter | Inverter075_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4807 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Q | Inverter | Inverter075_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4808 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4809 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4810 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4811 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4812 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M4 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4813 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Status | Inverter | Inverter075_MODBUS.HRxxxx_M5_status | Module Status | 4814 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 IR | Inverter | Inverter075_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 IS | Inverter | Inverter075_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 IT | Inverter | Inverter075_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4818 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4819 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4820 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4821 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 P | Inverter | Inverter075_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4822 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Q | Inverter | Inverter075_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4823 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4824 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4825 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4827 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M5 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4828 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Status | Inverter | Inverter075_MODBUS.HRxxxx_M6_status | Module Status | 4829 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 IR | Inverter | Inverter075_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4830 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 IS | Inverter | Inverter075_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 IT | Inverter | Inverter075_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 IDC | Inverter | Inverter075_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 VDCP | Inverter | Inverter075_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4834 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 VDCN | Inverter | Inverter075_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 VDC | Inverter | Inverter075_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4836 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 P | Inverter | Inverter075_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4837 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Q | Inverter | Inverter075_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4838 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Ambient Temp | Inverter | Inverter075_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4839 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Max IGBT Temp | Inverter | Inverter075_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4840 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 IO Status | Inverter | Inverter075_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4841 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Hardware Version | Inverter | Inverter075_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV075 | Daggett 3_SUB1_INV075_M6 Software Version | Inverter | Inverter075_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_A Phase Current | Inverter | inverter076_MODBUS.HR1004_i1_A | A Phase Current | 4844 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_B Phase Current | Inverter | inverter076_MODBUS.HR1005_i2_A | B Phase Current | 4845 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_C Phase Current | Inverter | inverter076_MODBUS.HR1006_i3_A | C Phase Current | 4846 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Bus Voltage | Inverter | inverter076_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4847 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV076 | Daggett 3_SUB1_INV076_Apparent Power | Inverter | inverter076_MODBUS.HR1010_s3_VA | Apparent Power | 4848 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 1 | Inverter | Inverter076_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC Input 1 | Inverter | Inverter076_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4850 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 2 | Inverter | Inverter076_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4851 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 2 | Inverter | Inverter076_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4852 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 3 | Inverter | Inverter076_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 3 | Inverter | Inverter076_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4854 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 4 | Inverter | Inverter076_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 4 | Inverter | Inverter076_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4856 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 5 | Inverter | Inverter076_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4857 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 5 | Inverter | Inverter076_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4858 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 6 | Inverter | Inverter076_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4859 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 6 | Inverter | Inverter076_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4860 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 7 | Inverter | Inverter076_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 7 | Inverter | Inverter076_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4862 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 8 | Inverter | Inverter076_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4863 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 8 | Inverter | Inverter076_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4864 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 9 | Inverter | Inverter076_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4865 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 9 | Inverter | Inverter076_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4866 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 10 | Inverter | Inverter076_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4867 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 10 | Inverter | Inverter076_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4868 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 11 | Inverter | Inverter076_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 11 | Inverter | Inverter076_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4870 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 12 | Inverter | Inverter076_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 12 | Inverter | Inverter076_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4872 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 13 | Inverter | Inverter076_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4873 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 13 | Inverter | Inverter076_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4874 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 14 | Inverter | Inverter076_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4875 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 14 | Inverter | Inverter076_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4876 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 15 | Inverter | Inverter076_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 15 | Inverter | Inverter076_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4878 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 16 | Inverter | Inverter076_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4879 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 16 | Inverter | Inverter076_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4880 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 17 | Inverter | Inverter076_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4881 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 17 | Inverter | Inverter076_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4882 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 18 | Inverter | Inverter076_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4883 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 18 | Inverter | Inverter076_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4884 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 19 | Inverter | Inverter076_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 19 | Inverter | Inverter076_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4886 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current DC Input 20 | Inverter | Inverter076_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC input 20 | Inverter | Inverter076_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4888 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current-AC | Inverter | inverter076_MODBUS.HR1007_i3Avg_A | Current-AC | 4889 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Current-DC | Inverter | inverter076_MODBUS.HR1062_idcInput_A | Current-DC | 4890 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Daily Energy Delivered | Inverter | inverter076_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4891 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power Set Point | Inverter | inverter076_MODBUS.HR0553_pRef | Real Power Set Point | 4892 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Reactive Power Set Point | Inverter | inverter076_MODBUS.HR0558_qRef | Reactive Power Set Point | 4893 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Frequency | Inverter | inverter076_MODBUS.HR1012_f3_Hz | Frequency | 4894 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV076 | Daggett 3_SUB1_INV076_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Insulation Resistance | Inverter | inverter076_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4895 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Number of DU Channels | Inverter | inverter076_MODBUS.HR0653_duChannels | Number of DU Channels | 4896 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Number of Running Modules | Inverter | inverter076_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4897 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Operating State | Inverter | inverter076_MODBUS.HR1123_currentStatus | Operating State | 4898 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Power Factor | Inverter | inverter076_MODBUS.HR1011_pf3 | Power Factor | 4899 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV076 | Daggett 3_SUB1_INV076_Ramp Down | Inverter | inverter076_MODBUS.HR0286_dropGradient_p | Ramp Down | 4900 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Ramp Up | Inverter | inverter076_MODBUS.HR0282_riseGradient_p | Ramp Up | 4901 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power Delivered | Inverter | inverter076_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4902 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Reactive Power Delivered | Inverter | inverter076_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4903 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power | 4904 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Reactive Power | Inverter | inverter076_MODBUS.HR1009_q3_kvar | Reactive Power | 4905 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Reactive Power Mode | Inverter | inverter076_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4906 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Reactive Power Set Point Percent | Inverter | inverter076_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4907 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power AC Percent | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4908 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power-AC | Inverter | inverter076_MODBUS.HR1008_p3_kW | Real Power-AC | 4909 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power-DC | Inverter | inverter076_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4910 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Air Intake | Inverter | inverter076_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4911 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Cabinet | Inverter | inverter076_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4912 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-IGBT | Inverter | inverter076_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4913 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Temperature-Module | Inverter | inverter076_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4914 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage A-B | Inverter | inverter076_MODBUS.HR1006_vRS_V | Voltage A-B | 4915 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage B-C | Inverter | inverter076_MODBUS.HR1002_vST_V | Voltage B-C | 4916 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage C-A | Inverter | inverter076_MODBUS.HR1003_vTR_V | Voltage C-A | 4917 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Voltage DC | Inverter | inverter076_MODBUS.HR1051_vdcBus_V | Voltage DC | 4918 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV076 | Daggett 3_SUB1_INV076_Fault Code 1 | Inverter | Inverter076_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Warning | Inverter | Inverter076_MODBUS.HRxxxx_currentWarning | Warning | 4920 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Internal Input Status | Inverter | Inverter076_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4921 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Internal Output Status | Inverter | Inverter076_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4922 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Module Fault Code | Inverter | Inverter076_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4923 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Internal Humidity | Inverter | Inverter076_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4924 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Humidity | Inverter | Inverter076_MODBUS.HRxxxx_humidity | Humidity | 4925 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_Comms Fault Time | Inverter | Inverter076_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Status | Inverter | Inverter076_MODBUS.HRxxxx_M1_status | Module Status | 4927 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 IR | Inverter | Inverter076_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 IS | Inverter | Inverter076_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 IT | Inverter | Inverter076_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4932 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4934 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 P | Inverter | Inverter076_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4935 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Q | Inverter | Inverter076_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4936 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4937 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4938 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4939 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M1 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Status | Inverter | Inverter076_MODBUS.HRxxxx_M2_status | Module Status | 4942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 IR | Inverter | Inverter076_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4943 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 IS | Inverter | Inverter076_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 IT | Inverter | Inverter076_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4947 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4948 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4949 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 P | Inverter | Inverter076_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4950 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Q | Inverter | Inverter076_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4951 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4952 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4953 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4954 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4955 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M2 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4956 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Status | Inverter | Inverter076_MODBUS.HRxxxx_M3_status | Module Status | 4957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 IR | Inverter | Inverter076_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4958 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 IS | Inverter | Inverter076_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4959 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 IT | Inverter | Inverter076_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4960 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4961 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4962 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4963 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4964 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 P | Inverter | Inverter076_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4965 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Q | Inverter | Inverter076_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4966 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4967 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4968 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4969 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4970 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M3 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4971 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Status | Inverter | Inverter076_MODBUS.HRxxxx_M4_status | Module Status | 4972 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 IR | Inverter | Inverter076_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4973 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 IS | Inverter | Inverter076_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4974 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 IT | Inverter | Inverter076_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4975 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4976 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4977 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4978 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4979 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 P | Inverter | Inverter076_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4980 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Q | Inverter | Inverter076_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4981 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4982 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4983 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4984 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4985 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M4 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4986 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Status | Inverter | Inverter076_MODBUS.HRxxxx_M5_status | Module Status | 4987 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 IR | Inverter | Inverter076_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 IS | Inverter | Inverter076_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 IT | Inverter | Inverter076_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4991 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4992 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4993 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4994 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 P | Inverter | Inverter076_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4995 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Q | Inverter | Inverter076_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4996 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4997 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4998 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5000 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M5 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5001 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Status | Inverter | Inverter076_MODBUS.HRxxxx_M6_status | Module Status | 5002 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 IR | Inverter | Inverter076_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5003 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 IS | Inverter | Inverter076_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 IT | Inverter | Inverter076_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 IDC | Inverter | Inverter076_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 VDCP | Inverter | Inverter076_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5007 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 VDCN | Inverter | Inverter076_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 VDC | Inverter | Inverter076_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5009 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 P | Inverter | Inverter076_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5010 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Q | Inverter | Inverter076_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5011 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Ambient Temp | Inverter | Inverter076_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5012 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Max IGBT Temp | Inverter | Inverter076_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5013 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 IO Status | Inverter | Inverter076_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5014 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Hardware Version | Inverter | Inverter076_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV076 | Daggett 3_SUB1_INV076_M6 Software Version | Inverter | Inverter076_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_A Phase Current | Inverter | inverter077_MODBUS.HR1004_i1_A | A Phase Current | 5017 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_B Phase Current | Inverter | inverter077_MODBUS.HR1005_i2_A | B Phase Current | 5018 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_C Phase Current | Inverter | inverter077_MODBUS.HR1006_i3_A | C Phase Current | 5019 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Bus Voltage | Inverter | inverter077_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5020 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV077 | Daggett 3_SUB1_INV077_Apparent Power | Inverter | inverter077_MODBUS.HR1010_s3_VA | Apparent Power | 5021 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 1 | Inverter | Inverter077_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC Input 1 | Inverter | Inverter077_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5023 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 2 | Inverter | Inverter077_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5024 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 2 | Inverter | Inverter077_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5025 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 3 | Inverter | Inverter077_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 3 | Inverter | Inverter077_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5027 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 4 | Inverter | Inverter077_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 4 | Inverter | Inverter077_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5029 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 5 | Inverter | Inverter077_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5030 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 5 | Inverter | Inverter077_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5031 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 6 | Inverter | Inverter077_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5032 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 6 | Inverter | Inverter077_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5033 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 7 | Inverter | Inverter077_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 7 | Inverter | Inverter077_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5035 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 8 | Inverter | Inverter077_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5036 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 8 | Inverter | Inverter077_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5037 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 9 | Inverter | Inverter077_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5038 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 9 | Inverter | Inverter077_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5039 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 10 | Inverter | Inverter077_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5040 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 10 | Inverter | Inverter077_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5041 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 11 | Inverter | Inverter077_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 11 | Inverter | Inverter077_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5043 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 12 | Inverter | Inverter077_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 12 | Inverter | Inverter077_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5045 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 13 | Inverter | Inverter077_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5046 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 13 | Inverter | Inverter077_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5047 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 14 | Inverter | Inverter077_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5048 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 14 | Inverter | Inverter077_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5049 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 15 | Inverter | Inverter077_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 15 | Inverter | Inverter077_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5051 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 16 | Inverter | Inverter077_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5052 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 16 | Inverter | Inverter077_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5053 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 17 | Inverter | Inverter077_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5054 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 17 | Inverter | Inverter077_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5055 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 18 | Inverter | Inverter077_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5056 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 18 | Inverter | Inverter077_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5057 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 19 | Inverter | Inverter077_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 19 | Inverter | Inverter077_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5059 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current DC Input 20 | Inverter | Inverter077_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC input 20 | Inverter | Inverter077_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5061 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current-AC | Inverter | inverter077_MODBUS.HR1007_i3Avg_A | Current-AC | 5062 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Current-DC | Inverter | inverter077_MODBUS.HR1062_idcInput_A | Current-DC | 5063 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Daily Energy Delivered | Inverter | inverter077_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5064 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power Set Point | Inverter | inverter077_MODBUS.HR0553_pRef | Real Power Set Point | 5065 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Reactive Power Set Point | Inverter | inverter077_MODBUS.HR0558_qRef | Reactive Power Set Point | 5066 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Frequency | Inverter | inverter077_MODBUS.HR1012_f3_Hz | Frequency | 5067 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV077 | Daggett 3_SUB1_INV077_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Insulation Resistance | Inverter | inverter077_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5068 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Number of DU Channels | Inverter | inverter077_MODBUS.HR0653_duChannels | Number of DU Channels | 5069 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Number of Running Modules | Inverter | inverter077_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5070 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Operating State | Inverter | inverter077_MODBUS.HR1123_currentStatus | Operating State | 5071 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Power Factor | Inverter | inverter077_MODBUS.HR1011_pf3 | Power Factor | 5072 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV077 | Daggett 3_SUB1_INV077_Ramp Down | Inverter | inverter077_MODBUS.HR0286_dropGradient_p | Ramp Down | 5073 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Ramp Up | Inverter | inverter077_MODBUS.HR0282_riseGradient_p | Ramp Up | 5074 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power Delivered | Inverter | inverter077_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5075 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Reactive Power Delivered | Inverter | inverter077_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5076 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power | 5077 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Reactive Power | Inverter | inverter077_MODBUS.HR1009_q3_kvar | Reactive Power | 5078 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Reactive Power Mode | Inverter | inverter077_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5079 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Reactive Power Set Point Percent | Inverter | inverter077_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5080 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power AC Percent | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5081 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power-AC | Inverter | inverter077_MODBUS.HR1008_p3_kW | Real Power-AC | 5082 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power-DC | Inverter | inverter077_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5083 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Air Intake | Inverter | inverter077_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5084 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Cabinet | Inverter | inverter077_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5085 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-IGBT | Inverter | inverter077_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5086 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Temperature-Module | Inverter | inverter077_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5087 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage A-B | Inverter | inverter077_MODBUS.HR1007_vRS_V | Voltage A-B | 5088 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage B-C | Inverter | inverter077_MODBUS.HR1002_vST_V | Voltage B-C | 5089 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage C-A | Inverter | inverter077_MODBUS.HR1003_vTR_V | Voltage C-A | 5090 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Voltage DC | Inverter | inverter077_MODBUS.HR1051_vdcBus_V | Voltage DC | 5091 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV077 | Daggett 3_SUB1_INV077_Fault Code 1 | Inverter | Inverter077_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Warning | Inverter | Inverter077_MODBUS.HRxxxx_currentWarning | Warning | 5093 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Internal Input Status | Inverter | Inverter077_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5094 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Internal Output Status | Inverter | Inverter077_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5095 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Module Fault Code | Inverter | Inverter077_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5096 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Internal Humidity | Inverter | Inverter077_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5097 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Humidity | Inverter | Inverter077_MODBUS.HRxxxx_humidity | Humidity | 5098 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_Comms Fault Time | Inverter | Inverter077_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Status | Inverter | Inverter077_MODBUS.HRxxxx_M1_status | Module Status | 5100 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 IR | Inverter | Inverter077_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 IS | Inverter | Inverter077_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 IT | Inverter | Inverter077_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5107 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 P | Inverter | Inverter077_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5108 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Q | Inverter | Inverter077_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5109 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5110 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5111 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M1 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Status | Inverter | Inverter077_MODBUS.HRxxxx_M2_status | Module Status | 5115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 IR | Inverter | Inverter077_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 IS | Inverter | Inverter077_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 IT | Inverter | Inverter077_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5120 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5121 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5122 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 P | Inverter | Inverter077_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5123 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Q | Inverter | Inverter077_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5124 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5125 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5126 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5127 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M2 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5129 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Status | Inverter | Inverter077_MODBUS.HRxxxx_M3_status | Module Status | 5130 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 IR | Inverter | Inverter077_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 IS | Inverter | Inverter077_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 IT | Inverter | Inverter077_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5133 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5134 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5135 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5136 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5137 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 P | Inverter | Inverter077_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5138 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Q | Inverter | Inverter077_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5139 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5140 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5141 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5142 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5143 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M3 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5144 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Status | Inverter | Inverter077_MODBUS.HRxxxx_M4_status | Module Status | 5145 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 IR | Inverter | Inverter077_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5146 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 IS | Inverter | Inverter077_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 IT | Inverter | Inverter077_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5148 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5149 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5150 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5151 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5152 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 P | Inverter | Inverter077_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5153 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Q | Inverter | Inverter077_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5154 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5155 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5156 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5157 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M4 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5159 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Status | Inverter | Inverter077_MODBUS.HRxxxx_M5_status | Module Status | 5160 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 IR | Inverter | Inverter077_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 IS | Inverter | Inverter077_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 IT | Inverter | Inverter077_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5164 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5166 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5167 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 P | Inverter | Inverter077_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5168 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Q | Inverter | Inverter077_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5169 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5170 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5171 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5173 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M5 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5174 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Status | Inverter | Inverter077_MODBUS.HRxxxx_M6_status | Module Status | 5175 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 IR | Inverter | Inverter077_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5176 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 IS | Inverter | Inverter077_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 IT | Inverter | Inverter077_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 IDC | Inverter | Inverter077_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 VDCP | Inverter | Inverter077_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5180 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 VDCN | Inverter | Inverter077_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 VDC | Inverter | Inverter077_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5182 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 P | Inverter | Inverter077_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5183 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Q | Inverter | Inverter077_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5184 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Ambient Temp | Inverter | Inverter077_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5185 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Max IGBT Temp | Inverter | Inverter077_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5186 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 IO Status | Inverter | Inverter077_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5187 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Hardware Version | Inverter | Inverter077_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV077 | Daggett 3_SUB1_INV077_M6 Software Version | Inverter | Inverter077_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_A Phase Current | Inverter | inverter078_MODBUS.HR1004_i1_A | A Phase Current | 5190 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_B Phase Current | Inverter | inverter078_MODBUS.HR1005_i2_A | B Phase Current | 5191 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_C Phase Current | Inverter | inverter078_MODBUS.HR1006_i3_A | C Phase Current | 5192 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Bus Voltage | Inverter | inverter078_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5193 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV078 | Daggett 3_SUB1_INV078_Apparent Power | Inverter | inverter078_MODBUS.HR1010_s3_VA | Apparent Power | 5194 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 1 | Inverter | Inverter078_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC Input 1 | Inverter | Inverter078_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5196 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 2 | Inverter | Inverter078_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5197 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 2 | Inverter | Inverter078_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5198 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 3 | Inverter | Inverter078_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 3 | Inverter | Inverter078_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5200 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 4 | Inverter | Inverter078_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 4 | Inverter | Inverter078_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5202 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 5 | Inverter | Inverter078_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5203 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 5 | Inverter | Inverter078_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5204 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 6 | Inverter | Inverter078_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5205 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 6 | Inverter | Inverter078_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5206 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 7 | Inverter | Inverter078_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 7 | Inverter | Inverter078_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5208 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 8 | Inverter | Inverter078_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5209 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 8 | Inverter | Inverter078_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5210 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 9 | Inverter | Inverter078_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5211 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 9 | Inverter | Inverter078_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5212 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 10 | Inverter | Inverter078_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5213 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 10 | Inverter | Inverter078_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5214 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 11 | Inverter | Inverter078_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 11 | Inverter | Inverter078_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5216 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 12 | Inverter | Inverter078_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5217 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 12 | Inverter | Inverter078_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5218 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 13 | Inverter | Inverter078_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5219 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 13 | Inverter | Inverter078_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5220 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 14 | Inverter | Inverter078_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5221 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 14 | Inverter | Inverter078_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5222 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 15 | Inverter | Inverter078_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 15 | Inverter | Inverter078_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5224 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 16 | Inverter | Inverter078_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5225 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 16 | Inverter | Inverter078_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5226 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 17 | Inverter | Inverter078_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5227 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 17 | Inverter | Inverter078_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5228 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 18 | Inverter | Inverter078_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5229 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 18 | Inverter | Inverter078_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5230 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 19 | Inverter | Inverter078_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5231 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 19 | Inverter | Inverter078_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5232 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current DC Input 20 | Inverter | Inverter078_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5233 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC input 20 | Inverter | Inverter078_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5234 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current-AC | Inverter | inverter078_MODBUS.HR1007_i3Avg_A | Current-AC | 5235 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Current-DC | Inverter | inverter078_MODBUS.HR1062_idcInput_A | Current-DC | 5236 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Daily Energy Delivered | Inverter | inverter078_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5237 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power Set Point | Inverter | inverter078_MODBUS.HR0553_pRef | Real Power Set Point | 5238 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Reactive Power Set Point | Inverter | inverter078_MODBUS.HR0558_qRef | Reactive Power Set Point | 5239 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Frequency | Inverter | inverter078_MODBUS.HR1012_f3_Hz | Frequency | 5240 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV078 | Daggett 3_SUB1_INV078_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Insulation Resistance | Inverter | inverter078_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5241 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Number of DU Channels | Inverter | inverter078_MODBUS.HR0653_duChannels | Number of DU Channels | 5242 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Number of Running Modules | Inverter | inverter078_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5243 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Operating State | Inverter | inverter078_MODBUS.HR1123_currentStatus | Operating State | 5244 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Power Factor | Inverter | inverter078_MODBUS.HR1011_pf3 | Power Factor | 5245 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV078 | Daggett 3_SUB1_INV078_Ramp Down | Inverter | inverter078_MODBUS.HR0286_dropGradient_p | Ramp Down | 5246 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Ramp Up | Inverter | inverter078_MODBUS.HR0282_riseGradient_p | Ramp Up | 5247 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power Delivered | Inverter | inverter078_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5248 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Reactive Power Delivered | Inverter | inverter078_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5249 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power | 5250 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Reactive Power | Inverter | inverter078_MODBUS.HR1009_q3_kvar | Reactive Power | 5251 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Reactive Power Mode | Inverter | inverter078_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5252 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Reactive Power Set Point Percent | Inverter | inverter078_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5253 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power AC Percent | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5254 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power-AC | Inverter | inverter078_MODBUS.HR1008_p3_kW | Real Power-AC | 5255 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power-DC | Inverter | inverter078_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5256 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Air Intake | Inverter | inverter078_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5257 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Cabinet | Inverter | inverter078_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5258 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-IGBT | Inverter | inverter078_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5259 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Temperature-Module | Inverter | inverter078_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5260 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage A-B | Inverter | inverter078_MODBUS.HR1008_vRS_V | Voltage A-B | 5261 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage B-C | Inverter | inverter078_MODBUS.HR1002_vST_V | Voltage B-C | 5262 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage C-A | Inverter | inverter078_MODBUS.HR1003_vTR_V | Voltage C-A | 5263 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Voltage DC | Inverter | inverter078_MODBUS.HR1051_vdcBus_V | Voltage DC | 5264 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV078 | Daggett 3_SUB1_INV078_Fault Code 1 | Inverter | Inverter078_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Warning | Inverter | Inverter078_MODBUS.HRxxxx_currentWarning | Warning | 5266 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Internal Input Status | Inverter | Inverter078_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5267 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Internal Output Status | Inverter | Inverter078_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5268 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Module Fault Code | Inverter | Inverter078_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Internal Humidity | Inverter | Inverter078_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5270 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Humidity | Inverter | Inverter078_MODBUS.HRxxxx_humidity | Humidity | 5271 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_Comms Fault Time | Inverter | Inverter078_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5272 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Status | Inverter | Inverter078_MODBUS.HRxxxx_M1_status | Module Status | 5273 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 IR | Inverter | Inverter078_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 IS | Inverter | Inverter078_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 IT | Inverter | Inverter078_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5277 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5279 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5280 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 P | Inverter | Inverter078_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5281 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Q | Inverter | Inverter078_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5282 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5283 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5284 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M1 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5287 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Status | Inverter | Inverter078_MODBUS.HRxxxx_M2_status | Module Status | 5288 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 IR | Inverter | Inverter078_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 IS | Inverter | Inverter078_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 IT | Inverter | Inverter078_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5291 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5293 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5294 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5295 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 P | Inverter | Inverter078_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5296 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Q | Inverter | Inverter078_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5297 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5298 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5299 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5300 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5301 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M2 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5302 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Status | Inverter | Inverter078_MODBUS.HRxxxx_M3_status | Module Status | 5303 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 IR | Inverter | Inverter078_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 IS | Inverter | Inverter078_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 IT | Inverter | Inverter078_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5306 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5307 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5308 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5309 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5310 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 P | Inverter | Inverter078_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5311 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Q | Inverter | Inverter078_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5312 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5313 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5314 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5315 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5316 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M3 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5317 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Status | Inverter | Inverter078_MODBUS.HRxxxx_M4_status | Module Status | 5318 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 IR | Inverter | Inverter078_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5319 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 IS | Inverter | Inverter078_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 IT | Inverter | Inverter078_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5321 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5322 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5323 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5324 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5325 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 P | Inverter | Inverter078_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5326 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Q | Inverter | Inverter078_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5327 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5328 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5329 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5330 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M4 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5332 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Status | Inverter | Inverter078_MODBUS.HRxxxx_M5_status | Module Status | 5333 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 IR | Inverter | Inverter078_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 IS | Inverter | Inverter078_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 IT | Inverter | Inverter078_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5337 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5339 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5340 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 P | Inverter | Inverter078_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5341 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Q | Inverter | Inverter078_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5342 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5343 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5344 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5346 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M5 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5347 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Status | Inverter | Inverter078_MODBUS.HRxxxx_M6_status | Module Status | 5348 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 IR | Inverter | Inverter078_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5349 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 IS | Inverter | Inverter078_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 IT | Inverter | Inverter078_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 IDC | Inverter | Inverter078_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 VDCP | Inverter | Inverter078_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5353 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 VDCN | Inverter | Inverter078_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 VDC | Inverter | Inverter078_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5355 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 P | Inverter | Inverter078_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5356 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Q | Inverter | Inverter078_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5357 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Ambient Temp | Inverter | Inverter078_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5358 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Max IGBT Temp | Inverter | Inverter078_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5359 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 IO Status | Inverter | Inverter078_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5360 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Hardware Version | Inverter | Inverter078_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV078 | Daggett 3_SUB1_INV078_M6 Software Version | Inverter | Inverter078_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_A Phase Current | Inverter | inverter079_MODBUS.HR1004_i1_A | A Phase Current | 5363 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_B Phase Current | Inverter | inverter079_MODBUS.HR1005_i2_A | B Phase Current | 5364 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_C Phase Current | Inverter | inverter079_MODBUS.HR1006_i3_A | C Phase Current | 5365 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Bus Voltage | Inverter | inverter079_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5366 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV079 | Daggett 3_SUB1_INV079_Apparent Power | Inverter | inverter079_MODBUS.HR1010_s3_VA | Apparent Power | 5367 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 1 | Inverter | Inverter079_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC Input 1 | Inverter | Inverter079_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5369 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 2 | Inverter | Inverter079_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5370 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 2 | Inverter | Inverter079_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5371 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 3 | Inverter | Inverter079_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 3 | Inverter | Inverter079_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5373 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 4 | Inverter | Inverter079_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 4 | Inverter | Inverter079_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5375 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 5 | Inverter | Inverter079_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5376 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 5 | Inverter | Inverter079_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5377 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 6 | Inverter | Inverter079_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5378 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 6 | Inverter | Inverter079_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5379 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 7 | Inverter | Inverter079_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 7 | Inverter | Inverter079_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5381 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 8 | Inverter | Inverter079_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5382 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 8 | Inverter | Inverter079_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5383 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 9 | Inverter | Inverter079_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5384 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 9 | Inverter | Inverter079_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5385 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 10 | Inverter | Inverter079_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5386 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 10 | Inverter | Inverter079_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5387 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 11 | Inverter | Inverter079_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 11 | Inverter | Inverter079_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5389 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 12 | Inverter | Inverter079_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5390 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 12 | Inverter | Inverter079_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5391 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 13 | Inverter | Inverter079_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5392 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 13 | Inverter | Inverter079_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5393 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 14 | Inverter | Inverter079_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5394 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 14 | Inverter | Inverter079_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5395 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 15 | Inverter | Inverter079_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 15 | Inverter | Inverter079_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5397 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 16 | Inverter | Inverter079_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5398 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 16 | Inverter | Inverter079_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5399 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 17 | Inverter | Inverter079_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5400 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 17 | Inverter | Inverter079_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5401 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 18 | Inverter | Inverter079_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5402 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 18 | Inverter | Inverter079_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5403 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 19 | Inverter | Inverter079_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5404 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 19 | Inverter | Inverter079_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5405 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current DC Input 20 | Inverter | Inverter079_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5406 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC input 20 | Inverter | Inverter079_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5407 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current-AC | Inverter | inverter079_MODBUS.HR1007_i3Avg_A | Current-AC | 5408 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Current-DC | Inverter | inverter079_MODBUS.HR1062_idcInput_A | Current-DC | 5409 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Daily Energy Delivered | Inverter | inverter079_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5410 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power Set Point | Inverter | inverter079_MODBUS.HR0553_pRef | Real Power Set Point | 5411 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Reactive Power Set Point | Inverter | inverter079_MODBUS.HR0558_qRef | Reactive Power Set Point | 5412 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Frequency | Inverter | inverter079_MODBUS.HR1012_f3_Hz | Frequency | 5413 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV079 | Daggett 3_SUB1_INV079_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Insulation Resistance | Inverter | inverter079_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5414 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Number of DU Channels | Inverter | inverter079_MODBUS.HR0653_duChannels | Number of DU Channels | 5415 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Number of Running Modules | Inverter | inverter079_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5416 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Operating State | Inverter | inverter079_MODBUS.HR1123_currentStatus | Operating State | 5417 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Power Factor | Inverter | inverter079_MODBUS.HR1011_pf3 | Power Factor | 5418 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV079 | Daggett 3_SUB1_INV079_Ramp Down | Inverter | inverter079_MODBUS.HR0286_dropGradient_p | Ramp Down | 5419 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Ramp Up | Inverter | inverter079_MODBUS.HR0282_riseGradient_p | Ramp Up | 5420 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power Delivered | Inverter | inverter079_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5421 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Reactive Power Delivered | Inverter | inverter079_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5422 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power | 5423 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Reactive Power | Inverter | inverter079_MODBUS.HR1009_q3_kvar | Reactive Power | 5424 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Reactive Power Mode | Inverter | inverter079_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5425 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Reactive Power Set Point Percent | Inverter | inverter079_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5426 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power AC Percent | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5427 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power-AC | Inverter | inverter079_MODBUS.HR1008_p3_kW | Real Power-AC | 5428 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power-DC | Inverter | inverter079_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5429 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Air Intake | Inverter | inverter079_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5430 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Cabinet | Inverter | inverter079_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5431 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-IGBT | Inverter | inverter079_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5432 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Temperature-Module | Inverter | inverter079_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5433 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage A-B | Inverter | inverter079_MODBUS.HR1009_vRS_V | Voltage A-B | 5434 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage B-C | Inverter | inverter079_MODBUS.HR1002_vST_V | Voltage B-C | 5435 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage C-A | Inverter | inverter079_MODBUS.HR1003_vTR_V | Voltage C-A | 5436 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Voltage DC | Inverter | inverter079_MODBUS.HR1051_vdcBus_V | Voltage DC | 5437 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV079 | Daggett 3_SUB1_INV079_Fault Code 1 | Inverter | Inverter079_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Warning | Inverter | Inverter079_MODBUS.HRxxxx_currentWarning | Warning | 5439 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Internal Input Status | Inverter | Inverter079_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5440 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Internal Output Status | Inverter | Inverter079_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5441 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Module Fault Code | Inverter | Inverter079_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Internal Humidity | Inverter | Inverter079_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5443 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Humidity | Inverter | Inverter079_MODBUS.HRxxxx_humidity | Humidity | 5444 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_Comms Fault Time | Inverter | Inverter079_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5445 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Status | Inverter | Inverter079_MODBUS.HRxxxx_M1_status | Module Status | 5446 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 IR | Inverter | Inverter079_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 IS | Inverter | Inverter079_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 IT | Inverter | Inverter079_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5450 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5452 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5453 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 P | Inverter | Inverter079_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5454 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Q | Inverter | Inverter079_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5455 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5456 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5457 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M1 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5460 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Status | Inverter | Inverter079_MODBUS.HRxxxx_M2_status | Module Status | 5461 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 IR | Inverter | Inverter079_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 IS | Inverter | Inverter079_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 IT | Inverter | Inverter079_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5464 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5466 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5467 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5468 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 P | Inverter | Inverter079_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5469 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Q | Inverter | Inverter079_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5470 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5471 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5472 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5473 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5474 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M2 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5475 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Status | Inverter | Inverter079_MODBUS.HRxxxx_M3_status | Module Status | 5476 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 IR | Inverter | Inverter079_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 IS | Inverter | Inverter079_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 IT | Inverter | Inverter079_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5479 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5480 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5481 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5482 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5483 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 P | Inverter | Inverter079_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5484 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Q | Inverter | Inverter079_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5485 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5486 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5487 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5488 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5489 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M3 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5490 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Status | Inverter | Inverter079_MODBUS.HRxxxx_M4_status | Module Status | 5491 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 IR | Inverter | Inverter079_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5492 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 IS | Inverter | Inverter079_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 IT | Inverter | Inverter079_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5494 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5495 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5496 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5497 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5498 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 P | Inverter | Inverter079_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5499 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Q | Inverter | Inverter079_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5500 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5501 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5502 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5503 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M4 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5505 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Status | Inverter | Inverter079_MODBUS.HRxxxx_M5_status | Module Status | 5506 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 IR | Inverter | Inverter079_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 IS | Inverter | Inverter079_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 IT | Inverter | Inverter079_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5510 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5512 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5513 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 P | Inverter | Inverter079_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5514 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Q | Inverter | Inverter079_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5515 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5516 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5517 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5519 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M5 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5520 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Status | Inverter | Inverter079_MODBUS.HRxxxx_M6_status | Module Status | 5521 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 IR | Inverter | Inverter079_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5522 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 IS | Inverter | Inverter079_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 IT | Inverter | Inverter079_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 IDC | Inverter | Inverter079_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 VDCP | Inverter | Inverter079_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5526 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 VDCN | Inverter | Inverter079_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 VDC | Inverter | Inverter079_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5528 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 P | Inverter | Inverter079_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5529 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Q | Inverter | Inverter079_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5530 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Ambient Temp | Inverter | Inverter079_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5531 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Max IGBT Temp | Inverter | Inverter079_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5532 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 IO Status | Inverter | Inverter079_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5533 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Hardware Version | Inverter | Inverter079_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV079 | Daggett 3_SUB1_INV079_M6 Software Version | Inverter | Inverter079_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_A Phase Current | Inverter | inverter080_MODBUS.HR1004_i1_A | A Phase Current | 5536 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_B Phase Current | Inverter | inverter080_MODBUS.HR1005_i2_A | B Phase Current | 5537 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_C Phase Current | Inverter | inverter080_MODBUS.HR1006_i3_A | C Phase Current | 5538 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Bus Voltage | Inverter | inverter080_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5539 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV080 | Daggett 3_SUB1_INV080_Apparent Power | Inverter | inverter080_MODBUS.HR1010_s3_VA | Apparent Power | 5540 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 1 | Inverter | Inverter080_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC Input 1 | Inverter | Inverter080_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5542 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 2 | Inverter | Inverter080_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5543 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 2 | Inverter | Inverter080_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5544 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 3 | Inverter | Inverter080_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 3 | Inverter | Inverter080_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5546 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 4 | Inverter | Inverter080_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 4 | Inverter | Inverter080_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5548 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 5 | Inverter | Inverter080_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5549 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 5 | Inverter | Inverter080_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5550 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 6 | Inverter | Inverter080_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5551 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 6 | Inverter | Inverter080_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5552 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 7 | Inverter | Inverter080_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 7 | Inverter | Inverter080_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5554 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 8 | Inverter | Inverter080_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5555 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 8 | Inverter | Inverter080_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5556 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 9 | Inverter | Inverter080_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5557 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 9 | Inverter | Inverter080_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5558 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 10 | Inverter | Inverter080_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5559 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 10 | Inverter | Inverter080_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5560 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 11 | Inverter | Inverter080_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 11 | Inverter | Inverter080_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5562 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 12 | Inverter | Inverter080_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5563 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 12 | Inverter | Inverter080_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5564 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 13 | Inverter | Inverter080_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5565 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 13 | Inverter | Inverter080_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5566 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 14 | Inverter | Inverter080_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5567 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 14 | Inverter | Inverter080_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5568 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 15 | Inverter | Inverter080_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 15 | Inverter | Inverter080_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5570 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 16 | Inverter | Inverter080_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5571 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 16 | Inverter | Inverter080_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5572 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 17 | Inverter | Inverter080_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5573 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 17 | Inverter | Inverter080_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5574 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 18 | Inverter | Inverter080_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5575 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 18 | Inverter | Inverter080_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5576 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 19 | Inverter | Inverter080_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5577 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 19 | Inverter | Inverter080_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5578 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current DC Input 20 | Inverter | Inverter080_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5579 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC input 20 | Inverter | Inverter080_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5580 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current-AC | Inverter | inverter080_MODBUS.HR1007_i3Avg_A | Current-AC | 5581 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Current-DC | Inverter | inverter080_MODBUS.HR1062_idcInput_A | Current-DC | 5582 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Daily Energy Delivered | Inverter | inverter080_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5583 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power Set Point | Inverter | inverter080_MODBUS.HR0553_pRef | Real Power Set Point | 5584 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Reactive Power Set Point | Inverter | inverter080_MODBUS.HR0558_qRef | Reactive Power Set Point | 5585 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Frequency | Inverter | inverter080_MODBUS.HR1012_f3_Hz | Frequency | 5586 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV080 | Daggett 3_SUB1_INV080_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Insulation Resistance | Inverter | inverter080_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5587 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Number of DU Channels | Inverter | inverter080_MODBUS.HR0653_duChannels | Number of DU Channels | 5588 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Number of Running Modules | Inverter | inverter080_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5589 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Operating State | Inverter | inverter080_MODBUS.HR1123_currentStatus | Operating State | 5590 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Power Factor | Inverter | inverter080_MODBUS.HR1011_pf3 | Power Factor | 5591 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV080 | Daggett 3_SUB1_INV080_Ramp Down | Inverter | inverter080_MODBUS.HR0286_dropGradient_p | Ramp Down | 5592 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Ramp Up | Inverter | inverter080_MODBUS.HR0282_riseGradient_p | Ramp Up | 5593 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power Delivered | Inverter | inverter080_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5594 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Reactive Power Delivered | Inverter | inverter080_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5595 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power | 5596 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Reactive Power | Inverter | inverter080_MODBUS.HR1009_q3_kvar | Reactive Power | 5597 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Reactive Power Mode | Inverter | inverter080_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5598 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Reactive Power Set Point Percent | Inverter | inverter080_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5599 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power AC Percent | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5600 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power-AC | Inverter | inverter080_MODBUS.HR1008_p3_kW | Real Power-AC | 5601 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power-DC | Inverter | inverter080_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5602 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Air Intake | Inverter | inverter080_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5603 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Cabinet | Inverter | inverter080_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5604 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-IGBT | Inverter | inverter080_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5605 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Temperature-Module | Inverter | inverter080_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5606 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage A-B | Inverter | inverter080_MODBUS.HR1010_vRS_V | Voltage A-B | 5607 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage B-C | Inverter | inverter080_MODBUS.HR1002_vST_V | Voltage B-C | 5608 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage C-A | Inverter | inverter080_MODBUS.HR1003_vTR_V | Voltage C-A | 5609 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Voltage DC | Inverter | inverter080_MODBUS.HR1051_vdcBus_V | Voltage DC | 5610 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV080 | Daggett 3_SUB1_INV080_Fault Code 1 | Inverter | Inverter080_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Warning | Inverter | Inverter080_MODBUS.HRxxxx_currentWarning | Warning | 5612 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Internal Input Status | Inverter | Inverter080_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5613 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Internal Output Status | Inverter | Inverter080_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5614 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Module Fault Code | Inverter | Inverter080_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Internal Humidity | Inverter | Inverter080_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5616 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Humidity | Inverter | Inverter080_MODBUS.HRxxxx_humidity | Humidity | 5617 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_Comms Fault Time | Inverter | Inverter080_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5618 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Status | Inverter | Inverter080_MODBUS.HRxxxx_M1_status | Module Status | 5619 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 IR | Inverter | Inverter080_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 IS | Inverter | Inverter080_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 IT | Inverter | Inverter080_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5623 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5625 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5626 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 P | Inverter | Inverter080_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5627 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Q | Inverter | Inverter080_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5628 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5629 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5630 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M1 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5633 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Status | Inverter | Inverter080_MODBUS.HRxxxx_M2_status | Module Status | 5634 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 IR | Inverter | Inverter080_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 IS | Inverter | Inverter080_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 IT | Inverter | Inverter080_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5637 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5639 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5640 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5641 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 P | Inverter | Inverter080_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5642 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Q | Inverter | Inverter080_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5643 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5644 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5645 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5646 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5647 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M2 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5648 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Status | Inverter | Inverter080_MODBUS.HRxxxx_M3_status | Module Status | 5649 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 IR | Inverter | Inverter080_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 IS | Inverter | Inverter080_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 IT | Inverter | Inverter080_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5652 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5653 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5654 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5655 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5656 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 P | Inverter | Inverter080_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5657 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Q | Inverter | Inverter080_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5658 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5659 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5660 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5661 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5662 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M3 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5663 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Status | Inverter | Inverter080_MODBUS.HRxxxx_M4_status | Module Status | 5664 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 IR | Inverter | Inverter080_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5665 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 IS | Inverter | Inverter080_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 IT | Inverter | Inverter080_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5667 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5668 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5669 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5670 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5671 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 P | Inverter | Inverter080_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5672 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Q | Inverter | Inverter080_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5673 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5674 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5675 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5676 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M4 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5678 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Status | Inverter | Inverter080_MODBUS.HRxxxx_M5_status | Module Status | 5679 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 IR | Inverter | Inverter080_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 IS | Inverter | Inverter080_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 IT | Inverter | Inverter080_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5683 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5685 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5686 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 P | Inverter | Inverter080_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5687 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Q | Inverter | Inverter080_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5688 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5689 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5690 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5692 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M5 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5693 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Status | Inverter | Inverter080_MODBUS.HRxxxx_M6_status | Module Status | 5694 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 IR | Inverter | Inverter080_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5695 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 IS | Inverter | Inverter080_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 IT | Inverter | Inverter080_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 IDC | Inverter | Inverter080_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 VDCP | Inverter | Inverter080_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5699 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 VDCN | Inverter | Inverter080_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 VDC | Inverter | Inverter080_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5701 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 P | Inverter | Inverter080_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5702 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Q | Inverter | Inverter080_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5703 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Ambient Temp | Inverter | Inverter080_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5704 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Max IGBT Temp | Inverter | Inverter080_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5705 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 IO Status | Inverter | Inverter080_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5706 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Hardware Version | Inverter | Inverter080_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV080 | Daggett 3_SUB1_INV080_M6 Software Version | Inverter | Inverter080_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_A Phase Current | Inverter | inverter081_MODBUS.HR1004_i1_A | A Phase Current | 5709 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_B Phase Current | Inverter | inverter081_MODBUS.HR1005_i2_A | B Phase Current | 5710 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_C Phase Current | Inverter | inverter081_MODBUS.HR1006_i3_A | C Phase Current | 5711 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Bus Voltage | Inverter | inverter081_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5712 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV081 | Daggett 3_SUB1_INV081_Apparent Power | Inverter | inverter081_MODBUS.HR1010_s3_VA | Apparent Power | 5713 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 1 | Inverter | Inverter081_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC Input 1 | Inverter | Inverter081_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5715 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 2 | Inverter | Inverter081_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5716 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 2 | Inverter | Inverter081_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5717 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 3 | Inverter | Inverter081_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 3 | Inverter | Inverter081_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5719 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 4 | Inverter | Inverter081_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 4 | Inverter | Inverter081_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5721 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 5 | Inverter | Inverter081_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5722 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 5 | Inverter | Inverter081_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5723 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 6 | Inverter | Inverter081_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5724 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 6 | Inverter | Inverter081_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5725 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 7 | Inverter | Inverter081_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 7 | Inverter | Inverter081_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5727 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 8 | Inverter | Inverter081_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5728 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 8 | Inverter | Inverter081_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5729 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 9 | Inverter | Inverter081_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5730 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 9 | Inverter | Inverter081_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5731 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 10 | Inverter | Inverter081_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5732 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 10 | Inverter | Inverter081_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5733 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 11 | Inverter | Inverter081_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 11 | Inverter | Inverter081_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5735 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 12 | Inverter | Inverter081_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5736 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 12 | Inverter | Inverter081_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5737 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 13 | Inverter | Inverter081_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5738 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 13 | Inverter | Inverter081_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5739 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 14 | Inverter | Inverter081_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5740 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 14 | Inverter | Inverter081_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5741 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 15 | Inverter | Inverter081_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 15 | Inverter | Inverter081_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5743 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 16 | Inverter | Inverter081_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5744 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 16 | Inverter | Inverter081_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5745 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 17 | Inverter | Inverter081_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5746 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 17 | Inverter | Inverter081_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5747 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 18 | Inverter | Inverter081_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5748 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 18 | Inverter | Inverter081_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5749 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 19 | Inverter | Inverter081_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5750 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 19 | Inverter | Inverter081_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5751 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current DC Input 20 | Inverter | Inverter081_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5752 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC input 20 | Inverter | Inverter081_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5753 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current-AC | Inverter | inverter081_MODBUS.HR1007_i3Avg_A | Current-AC | 5754 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Current-DC | Inverter | inverter081_MODBUS.HR1062_idcInput_A | Current-DC | 5755 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Daily Energy Delivered | Inverter | inverter081_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5756 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power Set Point | Inverter | inverter081_MODBUS.HR0553_pRef | Real Power Set Point | 5757 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Reactive Power Set Point | Inverter | inverter081_MODBUS.HR0558_qRef | Reactive Power Set Point | 5758 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Frequency | Inverter | inverter081_MODBUS.HR1012_f3_Hz | Frequency | 5759 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV081 | Daggett 3_SUB1_INV081_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Insulation Resistance | Inverter | inverter081_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5760 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Number of DU Channels | Inverter | inverter081_MODBUS.HR0653_duChannels | Number of DU Channels | 5761 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Number of Running Modules | Inverter | inverter081_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5762 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Operating State | Inverter | inverter081_MODBUS.HR1123_currentStatus | Operating State | 5763 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Power Factor | Inverter | inverter081_MODBUS.HR1011_pf3 | Power Factor | 5764 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV081 | Daggett 3_SUB1_INV081_Ramp Down | Inverter | inverter081_MODBUS.HR0286_dropGradient_p | Ramp Down | 5765 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Ramp Up | Inverter | inverter081_MODBUS.HR0282_riseGradient_p | Ramp Up | 5766 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power Delivered | Inverter | inverter081_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5767 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Reactive Power Delivered | Inverter | inverter081_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5768 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power | 5769 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Reactive Power | Inverter | inverter081_MODBUS.HR1009_q3_kvar | Reactive Power | 5770 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Reactive Power Mode | Inverter | inverter081_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5771 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Reactive Power Set Point Percent | Inverter | inverter081_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5772 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power AC Percent | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5773 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power-AC | Inverter | inverter081_MODBUS.HR1008_p3_kW | Real Power-AC | 5774 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power-DC | Inverter | inverter081_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5775 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Air Intake | Inverter | inverter081_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5776 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Cabinet | Inverter | inverter081_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5777 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-IGBT | Inverter | inverter081_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5778 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Temperature-Module | Inverter | inverter081_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5779 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage A-B | Inverter | inverter081_MODBUS.HR1001_vRS_V | Voltage A-B | 5780 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage B-C | Inverter | inverter081_MODBUS.HR1002_vST_V | Voltage B-C | 5781 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage C-A | Inverter | inverter081_MODBUS.HR1003_vTR_V | Voltage C-A | 5782 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Voltage DC | Inverter | inverter081_MODBUS.HR1051_vdcBus_V | Voltage DC | 5783 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV081 | Daggett 3_SUB1_INV081_Fault Code 1 | Inverter | Inverter081_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Warning | Inverter | Inverter081_MODBUS.HRxxxx_currentWarning | Warning | 5785 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Internal Input Status | Inverter | Inverter081_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5786 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Internal Output Status | Inverter | Inverter081_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5787 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Module Fault Code | Inverter | Inverter081_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Internal Humidity | Inverter | Inverter081_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5789 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Humidity | Inverter | Inverter081_MODBUS.HRxxxx_humidity | Humidity | 5790 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_Comms Fault Time | Inverter | Inverter081_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5791 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Status | Inverter | Inverter081_MODBUS.HRxxxx_M1_status | Module Status | 5792 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 IR | Inverter | Inverter081_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 IS | Inverter | Inverter081_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 IT | Inverter | Inverter081_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5796 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5798 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5799 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 P | Inverter | Inverter081_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5800 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Q | Inverter | Inverter081_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5801 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5802 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5803 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M1 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5806 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Status | Inverter | Inverter081_MODBUS.HRxxxx_M2_status | Module Status | 5807 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 IR | Inverter | Inverter081_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 IS | Inverter | Inverter081_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 IT | Inverter | Inverter081_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5810 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5812 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5813 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5814 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 P | Inverter | Inverter081_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5815 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Q | Inverter | Inverter081_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5816 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5817 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5818 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5819 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5820 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M2 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5821 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Status | Inverter | Inverter081_MODBUS.HRxxxx_M3_status | Module Status | 5822 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 IR | Inverter | Inverter081_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 IS | Inverter | Inverter081_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 IT | Inverter | Inverter081_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5825 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5826 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5827 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5828 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5829 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 P | Inverter | Inverter081_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5830 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Q | Inverter | Inverter081_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5831 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5832 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5833 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5834 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5835 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M3 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5836 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Status | Inverter | Inverter081_MODBUS.HRxxxx_M4_status | Module Status | 5837 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 IR | Inverter | Inverter081_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5838 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 IS | Inverter | Inverter081_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 IT | Inverter | Inverter081_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5840 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5841 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5842 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5843 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5844 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 P | Inverter | Inverter081_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5845 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Q | Inverter | Inverter081_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5846 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5847 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5848 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5849 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M4 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5851 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Status | Inverter | Inverter081_MODBUS.HRxxxx_M5_status | Module Status | 5852 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 IR | Inverter | Inverter081_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 IS | Inverter | Inverter081_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 IT | Inverter | Inverter081_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5856 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5858 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5859 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 P | Inverter | Inverter081_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5860 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Q | Inverter | Inverter081_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5861 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5862 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5863 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5865 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M5 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5866 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Status | Inverter | Inverter081_MODBUS.HRxxxx_M6_status | Module Status | 5867 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 IR | Inverter | Inverter081_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5868 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 IS | Inverter | Inverter081_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 IT | Inverter | Inverter081_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 IDC | Inverter | Inverter081_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 VDCP | Inverter | Inverter081_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5872 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 VDCN | Inverter | Inverter081_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 VDC | Inverter | Inverter081_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5874 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 P | Inverter | Inverter081_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5875 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Q | Inverter | Inverter081_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5876 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Ambient Temp | Inverter | Inverter081_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5877 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Max IGBT Temp | Inverter | Inverter081_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5878 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 IO Status | Inverter | Inverter081_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5879 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Hardware Version | Inverter | Inverter081_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV081 | Daggett 3_SUB1_INV081_M6 Software Version | Inverter | Inverter081_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_A Phase Current | Inverter | inverter082_MODBUS.HR1004_i1_A | A Phase Current | 5882 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_B Phase Current | Inverter | inverter082_MODBUS.HR1005_i2_A | B Phase Current | 5883 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_C Phase Current | Inverter | inverter082_MODBUS.HR1006_i3_A | C Phase Current | 5884 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Bus Voltage | Inverter | inverter082_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5885 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV082 | Daggett 3_SUB1_INV082_Apparent Power | Inverter | inverter082_MODBUS.HR1010_s3_VA | Apparent Power | 5886 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 1 | Inverter | Inverter082_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC Input 1 | Inverter | Inverter082_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5888 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 2 | Inverter | Inverter082_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5889 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 2 | Inverter | Inverter082_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5890 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 3 | Inverter | Inverter082_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 3 | Inverter | Inverter082_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5892 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 4 | Inverter | Inverter082_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 4 | Inverter | Inverter082_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5894 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 5 | Inverter | Inverter082_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5895 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 5 | Inverter | Inverter082_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5896 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 6 | Inverter | Inverter082_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5897 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 6 | Inverter | Inverter082_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5898 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 7 | Inverter | Inverter082_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 7 | Inverter | Inverter082_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5900 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 8 | Inverter | Inverter082_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5901 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 8 | Inverter | Inverter082_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5902 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 9 | Inverter | Inverter082_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5903 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 9 | Inverter | Inverter082_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5904 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 10 | Inverter | Inverter082_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5905 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 10 | Inverter | Inverter082_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5906 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 11 | Inverter | Inverter082_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 11 | Inverter | Inverter082_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5908 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 12 | Inverter | Inverter082_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5909 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 12 | Inverter | Inverter082_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5910 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 13 | Inverter | Inverter082_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5911 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 13 | Inverter | Inverter082_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5912 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 14 | Inverter | Inverter082_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5913 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 14 | Inverter | Inverter082_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5914 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 15 | Inverter | Inverter082_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 15 | Inverter | Inverter082_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5916 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 16 | Inverter | Inverter082_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5917 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 16 | Inverter | Inverter082_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5918 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 17 | Inverter | Inverter082_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5919 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 17 | Inverter | Inverter082_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5920 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 18 | Inverter | Inverter082_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5921 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 18 | Inverter | Inverter082_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5922 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 19 | Inverter | Inverter082_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5923 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 19 | Inverter | Inverter082_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5924 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current DC Input 20 | Inverter | Inverter082_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5925 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC input 20 | Inverter | Inverter082_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5926 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current-AC | Inverter | inverter082_MODBUS.HR1007_i3Avg_A | Current-AC | 5927 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Current-DC | Inverter | inverter082_MODBUS.HR1062_idcInput_A | Current-DC | 5928 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Daily Energy Delivered | Inverter | inverter082_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5929 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power Set Point | Inverter | inverter082_MODBUS.HR0553_pRef | Real Power Set Point | 5930 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Reactive Power Set Point | Inverter | inverter082_MODBUS.HR0558_qRef | Reactive Power Set Point | 5931 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Frequency | Inverter | inverter082_MODBUS.HR1012_f3_Hz | Frequency | 5932 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV082 | Daggett 3_SUB1_INV082_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Insulation Resistance | Inverter | inverter082_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5933 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Number of DU Channels | Inverter | inverter082_MODBUS.HR0653_duChannels | Number of DU Channels | 5934 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Number of Running Modules | Inverter | inverter082_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5935 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Operating State | Inverter | inverter082_MODBUS.HR1123_currentStatus | Operating State | 5936 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Power Factor | Inverter | inverter082_MODBUS.HR1011_pf3 | Power Factor | 5937 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV082 | Daggett 3_SUB1_INV082_Ramp Down | Inverter | inverter082_MODBUS.HR0286_dropGradient_p | Ramp Down | 5938 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Ramp Up | Inverter | inverter082_MODBUS.HR0282_riseGradient_p | Ramp Up | 5939 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power Delivered | Inverter | inverter082_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5940 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Reactive Power Delivered | Inverter | inverter082_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5941 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power | 5942 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Reactive Power | Inverter | inverter082_MODBUS.HR1009_q3_kvar | Reactive Power | 5943 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Reactive Power Mode | Inverter | inverter082_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5944 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Reactive Power Set Point Percent | Inverter | inverter082_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5945 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power AC Percent | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5946 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power-AC | Inverter | inverter082_MODBUS.HR1008_p3_kW | Real Power-AC | 5947 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power-DC | Inverter | inverter082_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5948 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Air Intake | Inverter | inverter082_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5949 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Cabinet | Inverter | inverter082_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5950 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-IGBT | Inverter | inverter082_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5951 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Temperature-Module | Inverter | inverter082_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5952 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage A-B | Inverter | inverter082_MODBUS.HR1002_vRS_V | Voltage A-B | 5953 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage B-C | Inverter | inverter082_MODBUS.HR1002_vST_V | Voltage B-C | 5954 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage C-A | Inverter | inverter082_MODBUS.HR1003_vTR_V | Voltage C-A | 5955 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Voltage DC | Inverter | inverter082_MODBUS.HR1051_vdcBus_V | Voltage DC | 5956 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV082 | Daggett 3_SUB1_INV082_Fault Code 1 | Inverter | Inverter082_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Warning | Inverter | Inverter082_MODBUS.HRxxxx_currentWarning | Warning | 5958 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Internal Input Status | Inverter | Inverter082_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5959 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Internal Output Status | Inverter | Inverter082_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5960 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Module Fault Code | Inverter | Inverter082_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Internal Humidity | Inverter | Inverter082_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5962 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Humidity | Inverter | Inverter082_MODBUS.HRxxxx_humidity | Humidity | 5963 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_Comms Fault Time | Inverter | Inverter082_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5964 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Status | Inverter | Inverter082_MODBUS.HRxxxx_M1_status | Module Status | 5965 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 IR | Inverter | Inverter082_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 IS | Inverter | Inverter082_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 IT | Inverter | Inverter082_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5969 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5971 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5972 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 P | Inverter | Inverter082_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5973 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Q | Inverter | Inverter082_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5974 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5975 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5976 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M1 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5979 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Status | Inverter | Inverter082_MODBUS.HRxxxx_M2_status | Module Status | 5980 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 IR | Inverter | Inverter082_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 IS | Inverter | Inverter082_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 IT | Inverter | Inverter082_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5983 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5985 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5986 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5987 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 P | Inverter | Inverter082_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5988 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Q | Inverter | Inverter082_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5989 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5990 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5991 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5992 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5993 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M2 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5994 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Status | Inverter | Inverter082_MODBUS.HRxxxx_M3_status | Module Status | 5995 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 IR | Inverter | Inverter082_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 IS | Inverter | Inverter082_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 IT | Inverter | Inverter082_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5998 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5999 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6000 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6001 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6002 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 P | Inverter | Inverter082_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6003 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Q | Inverter | Inverter082_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6004 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6005 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6006 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6007 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6008 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M3 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6009 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Status | Inverter | Inverter082_MODBUS.HRxxxx_M4_status | Module Status | 6010 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 IR | Inverter | Inverter082_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6011 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 IS | Inverter | Inverter082_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 IT | Inverter | Inverter082_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6013 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6014 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6015 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6016 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6017 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 P | Inverter | Inverter082_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6018 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Q | Inverter | Inverter082_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6019 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6020 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6021 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6022 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M4 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6024 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Status | Inverter | Inverter082_MODBUS.HRxxxx_M5_status | Module Status | 6025 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 IR | Inverter | Inverter082_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 IS | Inverter | Inverter082_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 IT | Inverter | Inverter082_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6029 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6031 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6032 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 P | Inverter | Inverter082_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6033 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Q | Inverter | Inverter082_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6034 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6035 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6036 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6038 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M5 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6039 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Status | Inverter | Inverter082_MODBUS.HRxxxx_M6_status | Module Status | 6040 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 IR | Inverter | Inverter082_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6041 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 IS | Inverter | Inverter082_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 IT | Inverter | Inverter082_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 IDC | Inverter | Inverter082_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 VDCP | Inverter | Inverter082_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6045 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 VDCN | Inverter | Inverter082_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 VDC | Inverter | Inverter082_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6047 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 P | Inverter | Inverter082_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6048 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Q | Inverter | Inverter082_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6049 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Ambient Temp | Inverter | Inverter082_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6050 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Max IGBT Temp | Inverter | Inverter082_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6051 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 IO Status | Inverter | Inverter082_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6052 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Hardware Version | Inverter | Inverter082_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV082 | Daggett 3_SUB1_INV082_M6 Software Version | Inverter | Inverter082_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_A Phase Current | Inverter | inverter083_MODBUS.HR1004_i1_A | A Phase Current | 6055 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_B Phase Current | Inverter | inverter083_MODBUS.HR1005_i2_A | B Phase Current | 6056 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_C Phase Current | Inverter | inverter083_MODBUS.HR1006_i3_A | C Phase Current | 6057 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Bus Voltage | Inverter | inverter083_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6058 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV083 | Daggett 3_SUB1_INV083_Apparent Power | Inverter | inverter083_MODBUS.HR1010_s3_VA | Apparent Power | 6059 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 1 | Inverter | Inverter083_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC Input 1 | Inverter | Inverter083_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6061 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 2 | Inverter | Inverter083_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6062 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 2 | Inverter | Inverter083_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6063 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 3 | Inverter | Inverter083_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 3 | Inverter | Inverter083_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6065 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 4 | Inverter | Inverter083_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 4 | Inverter | Inverter083_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6067 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 5 | Inverter | Inverter083_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6068 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 5 | Inverter | Inverter083_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6069 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 6 | Inverter | Inverter083_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6070 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 6 | Inverter | Inverter083_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6071 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 7 | Inverter | Inverter083_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 7 | Inverter | Inverter083_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6073 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 8 | Inverter | Inverter083_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6074 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 8 | Inverter | Inverter083_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6075 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 9 | Inverter | Inverter083_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6076 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 9 | Inverter | Inverter083_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6077 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 10 | Inverter | Inverter083_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6078 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 10 | Inverter | Inverter083_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6079 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 11 | Inverter | Inverter083_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 11 | Inverter | Inverter083_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6081 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 12 | Inverter | Inverter083_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6082 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 12 | Inverter | Inverter083_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6083 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 13 | Inverter | Inverter083_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6084 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 13 | Inverter | Inverter083_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6085 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 14 | Inverter | Inverter083_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6086 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 14 | Inverter | Inverter083_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6087 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 15 | Inverter | Inverter083_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 15 | Inverter | Inverter083_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6089 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 16 | Inverter | Inverter083_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6090 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 16 | Inverter | Inverter083_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6091 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 17 | Inverter | Inverter083_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6092 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 17 | Inverter | Inverter083_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6093 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 18 | Inverter | Inverter083_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6094 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 18 | Inverter | Inverter083_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6095 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 19 | Inverter | Inverter083_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6096 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 19 | Inverter | Inverter083_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6097 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current DC Input 20 | Inverter | Inverter083_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6098 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC input 20 | Inverter | Inverter083_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6099 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current-AC | Inverter | inverter083_MODBUS.HR1007_i3Avg_A | Current-AC | 6100 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Current-DC | Inverter | inverter083_MODBUS.HR1062_idcInput_A | Current-DC | 6101 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Daily Energy Delivered | Inverter | inverter083_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6102 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power Set Point | Inverter | inverter083_MODBUS.HR0553_pRef | Real Power Set Point | 6103 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Reactive Power Set Point | Inverter | inverter083_MODBUS.HR0558_qRef | Reactive Power Set Point | 6104 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Frequency | Inverter | inverter083_MODBUS.HR1012_f3_Hz | Frequency | 6105 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV083 | Daggett 3_SUB1_INV083_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Insulation Resistance | Inverter | inverter083_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6106 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Number of DU Channels | Inverter | inverter083_MODBUS.HR0653_duChannels | Number of DU Channels | 6107 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Number of Running Modules | Inverter | inverter083_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6108 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Operating State | Inverter | inverter083_MODBUS.HR1123_currentStatus | Operating State | 6109 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Power Factor | Inverter | inverter083_MODBUS.HR1011_pf3 | Power Factor | 6110 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV083 | Daggett 3_SUB1_INV083_Ramp Down | Inverter | inverter083_MODBUS.HR0286_dropGradient_p | Ramp Down | 6111 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Ramp Up | Inverter | inverter083_MODBUS.HR0282_riseGradient_p | Ramp Up | 6112 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power Delivered | Inverter | inverter083_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6113 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Reactive Power Delivered | Inverter | inverter083_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6114 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power | 6115 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Reactive Power | Inverter | inverter083_MODBUS.HR1009_q3_kvar | Reactive Power | 6116 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Reactive Power Mode | Inverter | inverter083_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6117 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Reactive Power Set Point Percent | Inverter | inverter083_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6118 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power AC Percent | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6119 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power-AC | Inverter | inverter083_MODBUS.HR1008_p3_kW | Real Power-AC | 6120 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power-DC | Inverter | inverter083_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6121 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Air Intake | Inverter | inverter083_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6122 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Cabinet | Inverter | inverter083_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6123 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-IGBT | Inverter | inverter083_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6124 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Temperature-Module | Inverter | inverter083_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6125 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage A-B | Inverter | inverter083_MODBUS.HR1003_vRS_V | Voltage A-B | 6126 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage B-C | Inverter | inverter083_MODBUS.HR1002_vST_V | Voltage B-C | 6127 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage C-A | Inverter | inverter083_MODBUS.HR1003_vTR_V | Voltage C-A | 6128 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Voltage DC | Inverter | inverter083_MODBUS.HR1051_vdcBus_V | Voltage DC | 6129 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV083 | Daggett 3_SUB1_INV083_Fault Code 1 | Inverter | Inverter083_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6130 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Warning | Inverter | Inverter083_MODBUS.HRxxxx_currentWarning | Warning | 6131 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Internal Input Status | Inverter | Inverter083_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6132 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Internal Output Status | Inverter | Inverter083_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6133 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Module Fault Code | Inverter | Inverter083_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Internal Humidity | Inverter | Inverter083_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6135 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Humidity | Inverter | Inverter083_MODBUS.HRxxxx_humidity | Humidity | 6136 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_Comms Fault Time | Inverter | Inverter083_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6137 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Status | Inverter | Inverter083_MODBUS.HRxxxx_M1_status | Module Status | 6138 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 IR | Inverter | Inverter083_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 IS | Inverter | Inverter083_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 IT | Inverter | Inverter083_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6142 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6144 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6145 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 P | Inverter | Inverter083_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6146 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Q | Inverter | Inverter083_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6147 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6148 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6149 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M1 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6152 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Status | Inverter | Inverter083_MODBUS.HRxxxx_M2_status | Module Status | 6153 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 IR | Inverter | Inverter083_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6154 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 IS | Inverter | Inverter083_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 IT | Inverter | Inverter083_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6156 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6158 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6159 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6160 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 P | Inverter | Inverter083_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6161 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Q | Inverter | Inverter083_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6162 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6163 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6164 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6165 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6166 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M2 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6167 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Status | Inverter | Inverter083_MODBUS.HRxxxx_M3_status | Module Status | 6168 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 IR | Inverter | Inverter083_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 IS | Inverter | Inverter083_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6170 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 IT | Inverter | Inverter083_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6171 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6172 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6173 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6174 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6175 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 P | Inverter | Inverter083_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6176 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Q | Inverter | Inverter083_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6177 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6178 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6179 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6180 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6181 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M3 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6182 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Status | Inverter | Inverter083_MODBUS.HRxxxx_M4_status | Module Status | 6183 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 IR | Inverter | Inverter083_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 IS | Inverter | Inverter083_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 IT | Inverter | Inverter083_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6186 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6187 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6188 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6189 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6190 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 P | Inverter | Inverter083_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6191 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Q | Inverter | Inverter083_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6192 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6193 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6194 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6195 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M4 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6197 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Status | Inverter | Inverter083_MODBUS.HRxxxx_M5_status | Module Status | 6198 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 IR | Inverter | Inverter083_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 IS | Inverter | Inverter083_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 IT | Inverter | Inverter083_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6202 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6204 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6205 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 P | Inverter | Inverter083_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6206 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Q | Inverter | Inverter083_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6207 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6208 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6209 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6211 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M5 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6212 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Status | Inverter | Inverter083_MODBUS.HRxxxx_M6_status | Module Status | 6213 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 IR | Inverter | Inverter083_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 IS | Inverter | Inverter083_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 IT | Inverter | Inverter083_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 IDC | Inverter | Inverter083_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6217 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 VDCP | Inverter | Inverter083_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6218 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 VDCN | Inverter | Inverter083_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6219 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 VDC | Inverter | Inverter083_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6220 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 P | Inverter | Inverter083_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6221 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Q | Inverter | Inverter083_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6222 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Ambient Temp | Inverter | Inverter083_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6223 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Max IGBT Temp | Inverter | Inverter083_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6224 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 IO Status | Inverter | Inverter083_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6225 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Hardware Version | Inverter | Inverter083_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6226 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV083 | Daggett 3_SUB1_INV083_M6 Software Version | Inverter | Inverter083_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_A Phase Current | Inverter | inverter084_MODBUS.HR1004_i1_A | A Phase Current | 6228 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_B Phase Current | Inverter | inverter084_MODBUS.HR1005_i2_A | B Phase Current | 6229 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_C Phase Current | Inverter | inverter084_MODBUS.HR1006_i3_A | C Phase Current | 6230 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Bus Voltage | Inverter | inverter084_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6231 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV084 | Daggett 3_SUB1_INV084_Apparent Power | Inverter | inverter084_MODBUS.HR1010_s3_VA | Apparent Power | 6232 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 1 | Inverter | Inverter084_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6233 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC Input 1 | Inverter | Inverter084_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6234 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 2 | Inverter | Inverter084_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6235 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 2 | Inverter | Inverter084_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6236 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 3 | Inverter | Inverter084_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 3 | Inverter | Inverter084_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6238 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 4 | Inverter | Inverter084_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 4 | Inverter | Inverter084_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6240 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 5 | Inverter | Inverter084_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6241 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 5 | Inverter | Inverter084_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6242 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 6 | Inverter | Inverter084_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6243 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 6 | Inverter | Inverter084_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6244 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 7 | Inverter | Inverter084_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6245 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 7 | Inverter | Inverter084_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6246 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 8 | Inverter | Inverter084_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6247 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 8 | Inverter | Inverter084_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6248 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 9 | Inverter | Inverter084_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6249 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 9 | Inverter | Inverter084_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6250 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 10 | Inverter | Inverter084_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6251 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 10 | Inverter | Inverter084_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6252 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 11 | Inverter | Inverter084_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 11 | Inverter | Inverter084_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6254 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 12 | Inverter | Inverter084_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6255 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 12 | Inverter | Inverter084_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6256 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 13 | Inverter | Inverter084_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6257 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 13 | Inverter | Inverter084_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6258 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 14 | Inverter | Inverter084_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 14 | Inverter | Inverter084_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6260 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 15 | Inverter | Inverter084_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6261 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 15 | Inverter | Inverter084_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6262 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 16 | Inverter | Inverter084_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6263 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 16 | Inverter | Inverter084_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6264 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 17 | Inverter | Inverter084_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6265 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 17 | Inverter | Inverter084_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6266 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 18 | Inverter | Inverter084_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6267 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 18 | Inverter | Inverter084_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6268 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 19 | Inverter | Inverter084_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6269 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 19 | Inverter | Inverter084_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6270 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current DC Input 20 | Inverter | Inverter084_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6271 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC input 20 | Inverter | Inverter084_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6272 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current-AC | Inverter | inverter084_MODBUS.HR1007_i3Avg_A | Current-AC | 6273 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Current-DC | Inverter | inverter084_MODBUS.HR1062_idcInput_A | Current-DC | 6274 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Daily Energy Delivered | Inverter | inverter084_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6275 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power Set Point | Inverter | inverter084_MODBUS.HR0553_pRef | Real Power Set Point | 6276 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Reactive Power Set Point | Inverter | inverter084_MODBUS.HR0558_qRef | Reactive Power Set Point | 6277 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Frequency | Inverter | inverter084_MODBUS.HR1012_f3_Hz | Frequency | 6278 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV084 | Daggett 3_SUB1_INV084_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Insulation Resistance | Inverter | inverter084_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6279 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Number of DU Channels | Inverter | inverter084_MODBUS.HR0653_duChannels | Number of DU Channels | 6280 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Number of Running Modules | Inverter | inverter084_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6281 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Operating State | Inverter | inverter084_MODBUS.HR1123_currentStatus | Operating State | 6282 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Power Factor | Inverter | inverter084_MODBUS.HR1011_pf3 | Power Factor | 6283 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV084 | Daggett 3_SUB1_INV084_Ramp Down | Inverter | inverter084_MODBUS.HR0286_dropGradient_p | Ramp Down | 6284 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Ramp Up | Inverter | inverter084_MODBUS.HR0282_riseGradient_p | Ramp Up | 6285 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power Delivered | Inverter | inverter084_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6286 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Reactive Power Delivered | Inverter | inverter084_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6287 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power | 6288 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Reactive Power | Inverter | inverter084_MODBUS.HR1009_q3_kvar | Reactive Power | 6289 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Reactive Power Mode | Inverter | inverter084_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6290 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Reactive Power Set Point Percent | Inverter | inverter084_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6291 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power AC Percent | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6292 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power-AC | Inverter | inverter084_MODBUS.HR1008_p3_kW | Real Power-AC | 6293 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power-DC | Inverter | inverter084_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6294 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Air Intake | Inverter | inverter084_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6295 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Cabinet | Inverter | inverter084_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6296 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-IGBT | Inverter | inverter084_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6297 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Temperature-Module | Inverter | inverter084_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6298 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage A-B | Inverter | inverter084_MODBUS.HR1004_vRS_V | Voltage A-B | 6299 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage B-C | Inverter | inverter084_MODBUS.HR1002_vST_V | Voltage B-C | 6300 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage C-A | Inverter | inverter084_MODBUS.HR1003_vTR_V | Voltage C-A | 6301 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Voltage DC | Inverter | inverter084_MODBUS.HR1051_vdcBus_V | Voltage DC | 6302 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV084 | Daggett 3_SUB1_INV084_Fault Code 1 | Inverter | Inverter084_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6303 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Warning | Inverter | Inverter084_MODBUS.HRxxxx_currentWarning | Warning | 6304 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Internal Input Status | Inverter | Inverter084_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6305 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Internal Output Status | Inverter | Inverter084_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6306 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Module Fault Code | Inverter | Inverter084_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Internal Humidity | Inverter | Inverter084_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6308 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Humidity | Inverter | Inverter084_MODBUS.HRxxxx_humidity | Humidity | 6309 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_Comms Fault Time | Inverter | Inverter084_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6310 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Status | Inverter | Inverter084_MODBUS.HRxxxx_M1_status | Module Status | 6311 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 IR | Inverter | Inverter084_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 IS | Inverter | Inverter084_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 IT | Inverter | Inverter084_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6315 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6317 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6318 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 P | Inverter | Inverter084_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6319 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Q | Inverter | Inverter084_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6320 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6321 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6322 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M1 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6325 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Status | Inverter | Inverter084_MODBUS.HRxxxx_M2_status | Module Status | 6326 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 IR | Inverter | Inverter084_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6327 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 IS | Inverter | Inverter084_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 IT | Inverter | Inverter084_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6329 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6331 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6332 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6333 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 P | Inverter | Inverter084_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6334 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Q | Inverter | Inverter084_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6335 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6336 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6337 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6338 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6339 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M2 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6340 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Status | Inverter | Inverter084_MODBUS.HRxxxx_M3_status | Module Status | 6341 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 IR | Inverter | Inverter084_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 IS | Inverter | Inverter084_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6343 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 IT | Inverter | Inverter084_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6344 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6345 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6346 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6347 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6348 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 P | Inverter | Inverter084_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6349 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Q | Inverter | Inverter084_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6350 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6351 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6352 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6353 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6354 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M3 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6355 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Status | Inverter | Inverter084_MODBUS.HRxxxx_M4_status | Module Status | 6356 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 IR | Inverter | Inverter084_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 IS | Inverter | Inverter084_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 IT | Inverter | Inverter084_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6359 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6360 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6361 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6362 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6363 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 P | Inverter | Inverter084_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6364 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Q | Inverter | Inverter084_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6365 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6366 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6367 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6368 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M4 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6370 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Status | Inverter | Inverter084_MODBUS.HRxxxx_M5_status | Module Status | 6371 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 IR | Inverter | Inverter084_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 IS | Inverter | Inverter084_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 IT | Inverter | Inverter084_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6375 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6377 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6378 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 P | Inverter | Inverter084_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6379 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Q | Inverter | Inverter084_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6380 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6381 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6382 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6384 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M5 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6385 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Status | Inverter | Inverter084_MODBUS.HRxxxx_M6_status | Module Status | 6386 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 IR | Inverter | Inverter084_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 IS | Inverter | Inverter084_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 IT | Inverter | Inverter084_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 IDC | Inverter | Inverter084_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6390 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 VDCP | Inverter | Inverter084_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6391 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 VDCN | Inverter | Inverter084_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6392 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 VDC | Inverter | Inverter084_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6393 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 P | Inverter | Inverter084_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6394 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Q | Inverter | Inverter084_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6395 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Ambient Temp | Inverter | Inverter084_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6396 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Max IGBT Temp | Inverter | Inverter084_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6397 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 IO Status | Inverter | Inverter084_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6398 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Hardware Version | Inverter | Inverter084_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6399 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV084 | Daggett 3_SUB1_INV084_M6 Software Version | Inverter | Inverter084_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_A Phase Current | Inverter | inverter085_MODBUS.HR1004_i1_A | A Phase Current | 6401 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_B Phase Current | Inverter | inverter085_MODBUS.HR1005_i2_A | B Phase Current | 6402 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_C Phase Current | Inverter | inverter085_MODBUS.HR1006_i3_A | C Phase Current | 6403 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Bus Voltage | Inverter | inverter085_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6404 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV085 | Daggett 3_SUB1_INV085_Apparent Power | Inverter | inverter085_MODBUS.HR1010_s3_VA | Apparent Power | 6405 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 1 | Inverter | Inverter085_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6406 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC Input 1 | Inverter | Inverter085_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6407 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 2 | Inverter | Inverter085_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6408 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 2 | Inverter | Inverter085_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6409 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 3 | Inverter | Inverter085_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 3 | Inverter | Inverter085_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6411 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 4 | Inverter | Inverter085_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 4 | Inverter | Inverter085_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6413 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 5 | Inverter | Inverter085_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6414 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 5 | Inverter | Inverter085_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6415 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 6 | Inverter | Inverter085_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6416 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 6 | Inverter | Inverter085_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6417 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 7 | Inverter | Inverter085_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6418 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 7 | Inverter | Inverter085_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6419 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 8 | Inverter | Inverter085_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6420 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 8 | Inverter | Inverter085_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6421 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 9 | Inverter | Inverter085_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6422 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 9 | Inverter | Inverter085_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6423 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 10 | Inverter | Inverter085_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6424 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 10 | Inverter | Inverter085_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6425 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 11 | Inverter | Inverter085_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 11 | Inverter | Inverter085_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6427 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 12 | Inverter | Inverter085_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6428 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 12 | Inverter | Inverter085_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6429 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 13 | Inverter | Inverter085_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6430 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 13 | Inverter | Inverter085_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6431 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 14 | Inverter | Inverter085_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 14 | Inverter | Inverter085_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6433 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 15 | Inverter | Inverter085_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6434 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 15 | Inverter | Inverter085_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6435 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 16 | Inverter | Inverter085_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6436 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 16 | Inverter | Inverter085_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6437 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 17 | Inverter | Inverter085_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6438 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 17 | Inverter | Inverter085_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6439 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 18 | Inverter | Inverter085_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6440 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 18 | Inverter | Inverter085_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6441 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 19 | Inverter | Inverter085_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6442 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 19 | Inverter | Inverter085_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6443 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current DC Input 20 | Inverter | Inverter085_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6444 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC input 20 | Inverter | Inverter085_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6445 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current-AC | Inverter | inverter085_MODBUS.HR1007_i3Avg_A | Current-AC | 6446 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Current-DC | Inverter | inverter085_MODBUS.HR1062_idcInput_A | Current-DC | 6447 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Daily Energy Delivered | Inverter | inverter085_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6448 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power Set Point | Inverter | inverter085_MODBUS.HR0553_pRef | Real Power Set Point | 6449 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Reactive Power Set Point | Inverter | inverter085_MODBUS.HR0558_qRef | Reactive Power Set Point | 6450 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Frequency | Inverter | inverter085_MODBUS.HR1012_f3_Hz | Frequency | 6451 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV085 | Daggett 3_SUB1_INV085_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Insulation Resistance | Inverter | inverter085_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6452 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Number of DU Channels | Inverter | inverter085_MODBUS.HR0653_duChannels | Number of DU Channels | 6453 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Number of Running Modules | Inverter | inverter085_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6454 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Operating State | Inverter | inverter085_MODBUS.HR1123_currentStatus | Operating State | 6455 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Power Factor | Inverter | inverter085_MODBUS.HR1011_pf3 | Power Factor | 6456 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV085 | Daggett 3_SUB1_INV085_Ramp Down | Inverter | inverter085_MODBUS.HR0286_dropGradient_p | Ramp Down | 6457 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Ramp Up | Inverter | inverter085_MODBUS.HR0282_riseGradient_p | Ramp Up | 6458 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power Delivered | Inverter | inverter085_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6459 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Reactive Power Delivered | Inverter | inverter085_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6460 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power | 6461 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Reactive Power | Inverter | inverter085_MODBUS.HR1009_q3_kvar | Reactive Power | 6462 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Reactive Power Mode | Inverter | inverter085_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6463 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Reactive Power Set Point Percent | Inverter | inverter085_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6464 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power AC Percent | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6465 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power-AC | Inverter | inverter085_MODBUS.HR1008_p3_kW | Real Power-AC | 6466 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power-DC | Inverter | inverter085_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6467 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Air Intake | Inverter | inverter085_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6468 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Cabinet | Inverter | inverter085_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6469 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-IGBT | Inverter | inverter085_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6470 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Temperature-Module | Inverter | inverter085_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6471 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage A-B | Inverter | inverter085_MODBUS.HR1005_vRS_V | Voltage A-B | 6472 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage B-C | Inverter | inverter085_MODBUS.HR1002_vST_V | Voltage B-C | 6473 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage C-A | Inverter | inverter085_MODBUS.HR1003_vTR_V | Voltage C-A | 6474 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Voltage DC | Inverter | inverter085_MODBUS.HR1051_vdcBus_V | Voltage DC | 6475 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV085 | Daggett 3_SUB1_INV085_Fault Code 1 | Inverter | Inverter085_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6476 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Warning | Inverter | Inverter085_MODBUS.HRxxxx_currentWarning | Warning | 6477 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Internal Input Status | Inverter | Inverter085_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6478 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Internal Output Status | Inverter | Inverter085_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6479 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Module Fault Code | Inverter | Inverter085_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Internal Humidity | Inverter | Inverter085_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6481 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Humidity | Inverter | Inverter085_MODBUS.HRxxxx_humidity | Humidity | 6482 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_Comms Fault Time | Inverter | Inverter085_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6483 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Status | Inverter | Inverter085_MODBUS.HRxxxx_M1_status | Module Status | 6484 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 IR | Inverter | Inverter085_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 IS | Inverter | Inverter085_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 IT | Inverter | Inverter085_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6488 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6490 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6491 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 P | Inverter | Inverter085_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6492 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Q | Inverter | Inverter085_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6493 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6494 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6495 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M1 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6498 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Status | Inverter | Inverter085_MODBUS.HRxxxx_M2_status | Module Status | 6499 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 IR | Inverter | Inverter085_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6500 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 IS | Inverter | Inverter085_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 IT | Inverter | Inverter085_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6502 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6504 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6505 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6506 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 P | Inverter | Inverter085_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6507 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Q | Inverter | Inverter085_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6508 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6509 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6510 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6511 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6512 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M2 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6513 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Status | Inverter | Inverter085_MODBUS.HRxxxx_M3_status | Module Status | 6514 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 IR | Inverter | Inverter085_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 IS | Inverter | Inverter085_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6516 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 IT | Inverter | Inverter085_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6517 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6518 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6519 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6520 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6521 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 P | Inverter | Inverter085_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6522 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Q | Inverter | Inverter085_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6523 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6524 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6525 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6526 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6527 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M3 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6528 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Status | Inverter | Inverter085_MODBUS.HRxxxx_M4_status | Module Status | 6529 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 IR | Inverter | Inverter085_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 IS | Inverter | Inverter085_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 IT | Inverter | Inverter085_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6532 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6533 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6534 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6535 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6536 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 P | Inverter | Inverter085_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6537 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Q | Inverter | Inverter085_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6538 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6539 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6540 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6541 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M4 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6543 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Status | Inverter | Inverter085_MODBUS.HRxxxx_M5_status | Module Status | 6544 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 IR | Inverter | Inverter085_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 IS | Inverter | Inverter085_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 IT | Inverter | Inverter085_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6548 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6550 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6551 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 P | Inverter | Inverter085_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6552 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Q | Inverter | Inverter085_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6553 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6554 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6555 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6557 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M5 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6558 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Status | Inverter | Inverter085_MODBUS.HRxxxx_M6_status | Module Status | 6559 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 IR | Inverter | Inverter085_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 IS | Inverter | Inverter085_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 IT | Inverter | Inverter085_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 IDC | Inverter | Inverter085_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6563 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 VDCP | Inverter | Inverter085_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6564 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 VDCN | Inverter | Inverter085_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6565 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 VDC | Inverter | Inverter085_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6566 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 P | Inverter | Inverter085_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6567 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Q | Inverter | Inverter085_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6568 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Ambient Temp | Inverter | Inverter085_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6569 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Max IGBT Temp | Inverter | Inverter085_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6570 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 IO Status | Inverter | Inverter085_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6571 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Hardware Version | Inverter | Inverter085_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6572 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV085 | Daggett 3_SUB1_INV085_M6 Software Version | Inverter | Inverter085_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_A Phase Current | Inverter | inverter086_MODBUS.HR1004_i1_A | A Phase Current | 6574 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_B Phase Current | Inverter | inverter086_MODBUS.HR1005_i2_A | B Phase Current | 6575 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_C Phase Current | Inverter | inverter086_MODBUS.HR1006_i3_A | C Phase Current | 6576 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Bus Voltage | Inverter | inverter086_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6577 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV086 | Daggett 3_SUB1_INV086_Apparent Power | Inverter | inverter086_MODBUS.HR1010_s3_VA | Apparent Power | 6578 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 1 | Inverter | Inverter086_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6579 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC Input 1 | Inverter | Inverter086_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6580 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 2 | Inverter | Inverter086_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6581 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 2 | Inverter | Inverter086_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6582 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 3 | Inverter | Inverter086_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 3 | Inverter | Inverter086_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6584 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 4 | Inverter | Inverter086_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 4 | Inverter | Inverter086_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6586 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 5 | Inverter | Inverter086_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6587 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 5 | Inverter | Inverter086_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6588 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 6 | Inverter | Inverter086_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6589 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 6 | Inverter | Inverter086_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6590 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 7 | Inverter | Inverter086_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6591 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 7 | Inverter | Inverter086_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6592 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 8 | Inverter | Inverter086_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6593 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 8 | Inverter | Inverter086_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6594 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 9 | Inverter | Inverter086_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6595 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 9 | Inverter | Inverter086_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6596 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 10 | Inverter | Inverter086_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6597 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 10 | Inverter | Inverter086_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6598 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 11 | Inverter | Inverter086_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 11 | Inverter | Inverter086_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6600 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 12 | Inverter | Inverter086_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6601 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 12 | Inverter | Inverter086_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6602 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 13 | Inverter | Inverter086_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6603 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 13 | Inverter | Inverter086_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6604 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 14 | Inverter | Inverter086_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 14 | Inverter | Inverter086_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6606 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 15 | Inverter | Inverter086_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6607 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 15 | Inverter | Inverter086_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6608 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 16 | Inverter | Inverter086_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6609 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 16 | Inverter | Inverter086_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6610 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 17 | Inverter | Inverter086_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6611 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 17 | Inverter | Inverter086_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6612 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 18 | Inverter | Inverter086_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6613 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 18 | Inverter | Inverter086_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6614 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 19 | Inverter | Inverter086_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6615 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 19 | Inverter | Inverter086_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6616 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current DC Input 20 | Inverter | Inverter086_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6617 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC input 20 | Inverter | Inverter086_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6618 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current-AC | Inverter | inverter086_MODBUS.HR1007_i3Avg_A | Current-AC | 6619 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Current-DC | Inverter | inverter086_MODBUS.HR1062_idcInput_A | Current-DC | 6620 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Daily Energy Delivered | Inverter | inverter086_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6621 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power Set Point | Inverter | inverter086_MODBUS.HR0553_pRef | Real Power Set Point | 6622 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Reactive Power Set Point | Inverter | inverter086_MODBUS.HR0558_qRef | Reactive Power Set Point | 6623 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Frequency | Inverter | inverter086_MODBUS.HR1012_f3_Hz | Frequency | 6624 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV086 | Daggett 3_SUB1_INV086_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Insulation Resistance | Inverter | inverter086_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6625 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Number of DU Channels | Inverter | inverter086_MODBUS.HR0653_duChannels | Number of DU Channels | 6626 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Number of Running Modules | Inverter | inverter086_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6627 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Operating State | Inverter | inverter086_MODBUS.HR1123_currentStatus | Operating State | 6628 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Power Factor | Inverter | inverter086_MODBUS.HR1011_pf3 | Power Factor | 6629 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV086 | Daggett 3_SUB1_INV086_Ramp Down | Inverter | inverter086_MODBUS.HR0286_dropGradient_p | Ramp Down | 6630 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Ramp Up | Inverter | inverter086_MODBUS.HR0282_riseGradient_p | Ramp Up | 6631 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power Delivered | Inverter | inverter086_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6632 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Reactive Power Delivered | Inverter | inverter086_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6633 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power | 6634 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Reactive Power | Inverter | inverter086_MODBUS.HR1009_q3_kvar | Reactive Power | 6635 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Reactive Power Mode | Inverter | inverter086_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6636 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Reactive Power Set Point Percent | Inverter | inverter086_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6637 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power AC Percent | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6638 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power-AC | Inverter | inverter086_MODBUS.HR1008_p3_kW | Real Power-AC | 6639 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power-DC | Inverter | inverter086_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6640 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Air Intake | Inverter | inverter086_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6641 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Cabinet | Inverter | inverter086_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6642 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-IGBT | Inverter | inverter086_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6643 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Temperature-Module | Inverter | inverter086_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6644 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage A-B | Inverter | inverter086_MODBUS.HR1006_vRS_V | Voltage A-B | 6645 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage B-C | Inverter | inverter086_MODBUS.HR1002_vST_V | Voltage B-C | 6646 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage C-A | Inverter | inverter086_MODBUS.HR1003_vTR_V | Voltage C-A | 6647 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Voltage DC | Inverter | inverter086_MODBUS.HR1051_vdcBus_V | Voltage DC | 6648 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV086 | Daggett 3_SUB1_INV086_Fault Code 1 | Inverter | Inverter086_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6649 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Warning | Inverter | Inverter086_MODBUS.HRxxxx_currentWarning | Warning | 6650 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Internal Input Status | Inverter | Inverter086_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6651 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Internal Output Status | Inverter | Inverter086_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6652 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Module Fault Code | Inverter | Inverter086_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Internal Humidity | Inverter | Inverter086_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6654 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Humidity | Inverter | Inverter086_MODBUS.HRxxxx_humidity | Humidity | 6655 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_Comms Fault Time | Inverter | Inverter086_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6656 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Status | Inverter | Inverter086_MODBUS.HRxxxx_M1_status | Module Status | 6657 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 IR | Inverter | Inverter086_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 IS | Inverter | Inverter086_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 IT | Inverter | Inverter086_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6661 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6663 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6664 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 P | Inverter | Inverter086_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6665 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Q | Inverter | Inverter086_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6666 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6667 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6668 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M1 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6671 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Status | Inverter | Inverter086_MODBUS.HRxxxx_M2_status | Module Status | 6672 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 IR | Inverter | Inverter086_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6673 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 IS | Inverter | Inverter086_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 IT | Inverter | Inverter086_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6675 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6677 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6678 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6679 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 P | Inverter | Inverter086_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6680 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Q | Inverter | Inverter086_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6681 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6682 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6683 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6684 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6685 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M2 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6686 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Status | Inverter | Inverter086_MODBUS.HRxxxx_M3_status | Module Status | 6687 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 IR | Inverter | Inverter086_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 IS | Inverter | Inverter086_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6689 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 IT | Inverter | Inverter086_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6690 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6691 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6692 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6693 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6694 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 P | Inverter | Inverter086_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6695 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Q | Inverter | Inverter086_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6696 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6697 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6698 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6699 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6700 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M3 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6701 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Status | Inverter | Inverter086_MODBUS.HRxxxx_M4_status | Module Status | 6702 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 IR | Inverter | Inverter086_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 IS | Inverter | Inverter086_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 IT | Inverter | Inverter086_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6705 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6706 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6707 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6708 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6709 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 P | Inverter | Inverter086_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6710 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Q | Inverter | Inverter086_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6711 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6712 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6713 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6714 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M4 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6716 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Status | Inverter | Inverter086_MODBUS.HRxxxx_M5_status | Module Status | 6717 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 IR | Inverter | Inverter086_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 IS | Inverter | Inverter086_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 IT | Inverter | Inverter086_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6721 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6723 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6724 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 P | Inverter | Inverter086_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6725 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Q | Inverter | Inverter086_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6726 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6727 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6728 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6730 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M5 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6731 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Status | Inverter | Inverter086_MODBUS.HRxxxx_M6_status | Module Status | 6732 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 IR | Inverter | Inverter086_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 IS | Inverter | Inverter086_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 IT | Inverter | Inverter086_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 IDC | Inverter | Inverter086_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6736 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 VDCP | Inverter | Inverter086_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6737 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 VDCN | Inverter | Inverter086_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6738 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 VDC | Inverter | Inverter086_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6739 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 P | Inverter | Inverter086_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6740 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Q | Inverter | Inverter086_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6741 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Ambient Temp | Inverter | Inverter086_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6742 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Max IGBT Temp | Inverter | Inverter086_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6743 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 IO Status | Inverter | Inverter086_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6744 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Hardware Version | Inverter | Inverter086_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6745 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV086 | Daggett 3_SUB1_INV086_M6 Software Version | Inverter | Inverter086_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_A Phase Current | Inverter | inverter087_MODBUS.HR1004_i1_A | A Phase Current | 6747 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_B Phase Current | Inverter | inverter087_MODBUS.HR1005_i2_A | B Phase Current | 6748 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_C Phase Current | Inverter | inverter087_MODBUS.HR1006_i3_A | C Phase Current | 6749 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Bus Voltage | Inverter | inverter087_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6750 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV087 | Daggett 3_SUB1_INV087_Apparent Power | Inverter | inverter087_MODBUS.HR1010_s3_VA | Apparent Power | 6751 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 1 | Inverter | Inverter087_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6752 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC Input 1 | Inverter | Inverter087_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6753 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 2 | Inverter | Inverter087_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6754 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 2 | Inverter | Inverter087_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6755 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 3 | Inverter | Inverter087_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 3 | Inverter | Inverter087_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6757 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 4 | Inverter | Inverter087_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 4 | Inverter | Inverter087_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6759 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 5 | Inverter | Inverter087_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6760 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 5 | Inverter | Inverter087_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6761 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 6 | Inverter | Inverter087_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6762 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 6 | Inverter | Inverter087_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6763 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 7 | Inverter | Inverter087_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6764 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 7 | Inverter | Inverter087_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6765 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 8 | Inverter | Inverter087_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6766 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 8 | Inverter | Inverter087_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6767 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 9 | Inverter | Inverter087_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6768 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 9 | Inverter | Inverter087_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6769 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 10 | Inverter | Inverter087_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6770 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 10 | Inverter | Inverter087_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6771 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 11 | Inverter | Inverter087_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 11 | Inverter | Inverter087_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6773 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 12 | Inverter | Inverter087_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6774 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 12 | Inverter | Inverter087_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6775 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 13 | Inverter | Inverter087_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6776 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 13 | Inverter | Inverter087_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6777 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 14 | Inverter | Inverter087_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 14 | Inverter | Inverter087_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6779 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 15 | Inverter | Inverter087_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6780 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 15 | Inverter | Inverter087_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6781 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 16 | Inverter | Inverter087_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6782 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 16 | Inverter | Inverter087_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6783 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 17 | Inverter | Inverter087_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6784 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 17 | Inverter | Inverter087_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6785 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 18 | Inverter | Inverter087_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6786 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 18 | Inverter | Inverter087_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6787 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 19 | Inverter | Inverter087_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6788 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 19 | Inverter | Inverter087_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6789 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current DC Input 20 | Inverter | Inverter087_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6790 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC input 20 | Inverter | Inverter087_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6791 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current-AC | Inverter | inverter087_MODBUS.HR1007_i3Avg_A | Current-AC | 6792 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Current-DC | Inverter | inverter087_MODBUS.HR1062_idcInput_A | Current-DC | 6793 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Daily Energy Delivered | Inverter | inverter087_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6794 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power Set Point | Inverter | inverter087_MODBUS.HR0553_pRef | Real Power Set Point | 6795 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Reactive Power Set Point | Inverter | inverter087_MODBUS.HR0558_qRef | Reactive Power Set Point | 6796 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Frequency | Inverter | inverter087_MODBUS.HR1012_f3_Hz | Frequency | 6797 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV087 | Daggett 3_SUB1_INV087_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Insulation Resistance | Inverter | inverter087_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6798 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Number of DU Channels | Inverter | inverter087_MODBUS.HR0653_duChannels | Number of DU Channels | 6799 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Number of Running Modules | Inverter | inverter087_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6800 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Operating State | Inverter | inverter087_MODBUS.HR1123_currentStatus | Operating State | 6801 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Power Factor | Inverter | inverter087_MODBUS.HR1011_pf3 | Power Factor | 6802 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV087 | Daggett 3_SUB1_INV087_Ramp Down | Inverter | inverter087_MODBUS.HR0286_dropGradient_p | Ramp Down | 6803 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Ramp Up | Inverter | inverter087_MODBUS.HR0282_riseGradient_p | Ramp Up | 6804 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power Delivered | Inverter | inverter087_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6805 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Reactive Power Delivered | Inverter | inverter087_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6806 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power | 6807 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Reactive Power | Inverter | inverter087_MODBUS.HR1009_q3_kvar | Reactive Power | 6808 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Reactive Power Mode | Inverter | inverter087_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6809 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Reactive Power Set Point Percent | Inverter | inverter087_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6810 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power AC Percent | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6811 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power-AC | Inverter | inverter087_MODBUS.HR1008_p3_kW | Real Power-AC | 6812 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power-DC | Inverter | inverter087_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6813 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Air Intake | Inverter | inverter087_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6814 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Cabinet | Inverter | inverter087_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6815 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-IGBT | Inverter | inverter087_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6816 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Temperature-Module | Inverter | inverter087_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6817 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage A-B | Inverter | inverter087_MODBUS.HR1007_vRS_V | Voltage A-B | 6818 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage B-C | Inverter | inverter087_MODBUS.HR1002_vST_V | Voltage B-C | 6819 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage C-A | Inverter | inverter087_MODBUS.HR1003_vTR_V | Voltage C-A | 6820 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Voltage DC | Inverter | inverter087_MODBUS.HR1051_vdcBus_V | Voltage DC | 6821 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV087 | Daggett 3_SUB1_INV087_Fault Code 1 | Inverter | Inverter087_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6822 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Warning | Inverter | Inverter087_MODBUS.HRxxxx_currentWarning | Warning | 6823 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Internal Input Status | Inverter | Inverter087_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6824 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Internal Output Status | Inverter | Inverter087_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6825 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Module Fault Code | Inverter | Inverter087_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Internal Humidity | Inverter | Inverter087_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6827 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Humidity | Inverter | Inverter087_MODBUS.HRxxxx_humidity | Humidity | 6828 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_Comms Fault Time | Inverter | Inverter087_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6829 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Status | Inverter | Inverter087_MODBUS.HRxxxx_M1_status | Module Status | 6830 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 IR | Inverter | Inverter087_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 IS | Inverter | Inverter087_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 IT | Inverter | Inverter087_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6834 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6836 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6837 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 P | Inverter | Inverter087_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6838 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Q | Inverter | Inverter087_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6839 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6840 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6841 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M1 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6844 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Status | Inverter | Inverter087_MODBUS.HRxxxx_M2_status | Module Status | 6845 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 IR | Inverter | Inverter087_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6846 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 IS | Inverter | Inverter087_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 IT | Inverter | Inverter087_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6848 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6850 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6851 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6852 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 P | Inverter | Inverter087_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6853 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Q | Inverter | Inverter087_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6854 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6855 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6856 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6857 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6858 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M2 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6859 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Status | Inverter | Inverter087_MODBUS.HRxxxx_M3_status | Module Status | 6860 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 IR | Inverter | Inverter087_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 IS | Inverter | Inverter087_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6862 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 IT | Inverter | Inverter087_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6863 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6864 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6865 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6866 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6867 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 P | Inverter | Inverter087_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6868 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Q | Inverter | Inverter087_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6869 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6870 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6871 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6872 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6873 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M3 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6874 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Status | Inverter | Inverter087_MODBUS.HRxxxx_M4_status | Module Status | 6875 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 IR | Inverter | Inverter087_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 IS | Inverter | Inverter087_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 IT | Inverter | Inverter087_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6878 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6879 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6880 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6881 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6882 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 P | Inverter | Inverter087_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6883 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Q | Inverter | Inverter087_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6884 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6885 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6886 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6887 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M4 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6889 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Status | Inverter | Inverter087_MODBUS.HRxxxx_M5_status | Module Status | 6890 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 IR | Inverter | Inverter087_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 IS | Inverter | Inverter087_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 IT | Inverter | Inverter087_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6894 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6896 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6897 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 P | Inverter | Inverter087_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6898 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Q | Inverter | Inverter087_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6899 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6900 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6901 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6903 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M5 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6904 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Status | Inverter | Inverter087_MODBUS.HRxxxx_M6_status | Module Status | 6905 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 IR | Inverter | Inverter087_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 IS | Inverter | Inverter087_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 IT | Inverter | Inverter087_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 IDC | Inverter | Inverter087_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6909 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 VDCP | Inverter | Inverter087_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6910 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 VDCN | Inverter | Inverter087_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6911 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 VDC | Inverter | Inverter087_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6912 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 P | Inverter | Inverter087_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6913 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Q | Inverter | Inverter087_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6914 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Ambient Temp | Inverter | Inverter087_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6915 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Max IGBT Temp | Inverter | Inverter087_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6916 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 IO Status | Inverter | Inverter087_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6917 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Hardware Version | Inverter | Inverter087_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6918 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV087 | Daggett 3_SUB1_INV087_M6 Software Version | Inverter | Inverter087_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_A Phase Current | Inverter | inverter088_MODBUS.HR1004_i1_A | A Phase Current | 6920 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_B Phase Current | Inverter | inverter088_MODBUS.HR1005_i2_A | B Phase Current | 6921 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_C Phase Current | Inverter | inverter088_MODBUS.HR1006_i3_A | C Phase Current | 6922 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Bus Voltage | Inverter | inverter088_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6923 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV088 | Daggett 3_SUB1_INV088_Apparent Power | Inverter | inverter088_MODBUS.HR1010_s3_VA | Apparent Power | 6924 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 1 | Inverter | Inverter088_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6925 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC Input 1 | Inverter | Inverter088_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6926 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 2 | Inverter | Inverter088_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6927 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 2 | Inverter | Inverter088_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6928 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 3 | Inverter | Inverter088_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 3 | Inverter | Inverter088_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6930 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 4 | Inverter | Inverter088_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 4 | Inverter | Inverter088_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6932 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 5 | Inverter | Inverter088_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6933 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 5 | Inverter | Inverter088_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6934 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 6 | Inverter | Inverter088_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6935 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 6 | Inverter | Inverter088_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6936 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 7 | Inverter | Inverter088_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6937 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 7 | Inverter | Inverter088_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6938 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 8 | Inverter | Inverter088_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6939 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 8 | Inverter | Inverter088_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6940 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 9 | Inverter | Inverter088_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6941 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 9 | Inverter | Inverter088_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6942 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 10 | Inverter | Inverter088_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6943 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 10 | Inverter | Inverter088_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6944 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 11 | Inverter | Inverter088_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 11 | Inverter | Inverter088_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6946 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 12 | Inverter | Inverter088_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6947 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 12 | Inverter | Inverter088_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6948 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 13 | Inverter | Inverter088_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6949 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 13 | Inverter | Inverter088_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6950 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 14 | Inverter | Inverter088_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 14 | Inverter | Inverter088_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6952 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 15 | Inverter | Inverter088_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6953 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 15 | Inverter | Inverter088_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6954 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 16 | Inverter | Inverter088_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6955 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 16 | Inverter | Inverter088_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6956 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 17 | Inverter | Inverter088_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6957 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 17 | Inverter | Inverter088_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6958 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 18 | Inverter | Inverter088_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6959 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 18 | Inverter | Inverter088_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6960 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 19 | Inverter | Inverter088_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6961 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 19 | Inverter | Inverter088_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6962 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current DC Input 20 | Inverter | Inverter088_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6963 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC input 20 | Inverter | Inverter088_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6964 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current-AC | Inverter | inverter088_MODBUS.HR1007_i3Avg_A | Current-AC | 6965 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Current-DC | Inverter | inverter088_MODBUS.HR1062_idcInput_A | Current-DC | 6966 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Daily Energy Delivered | Inverter | inverter088_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6967 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power Set Point | Inverter | inverter088_MODBUS.HR0553_pRef | Real Power Set Point | 6968 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Reactive Power Set Point | Inverter | inverter088_MODBUS.HR0558_qRef | Reactive Power Set Point | 6969 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Frequency | Inverter | inverter088_MODBUS.HR1012_f3_Hz | Frequency | 6970 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV088 | Daggett 3_SUB1_INV088_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Insulation Resistance | Inverter | inverter088_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6971 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Number of DU Channels | Inverter | inverter088_MODBUS.HR0653_duChannels | Number of DU Channels | 6972 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Number of Running Modules | Inverter | inverter088_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6973 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Operating State | Inverter | inverter088_MODBUS.HR1123_currentStatus | Operating State | 6974 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Power Factor | Inverter | inverter088_MODBUS.HR1011_pf3 | Power Factor | 6975 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV088 | Daggett 3_SUB1_INV088_Ramp Down | Inverter | inverter088_MODBUS.HR0286_dropGradient_p | Ramp Down | 6976 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Ramp Up | Inverter | inverter088_MODBUS.HR0282_riseGradient_p | Ramp Up | 6977 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power Delivered | Inverter | inverter088_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6978 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Reactive Power Delivered | Inverter | inverter088_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6979 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power | 6980 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Reactive Power | Inverter | inverter088_MODBUS.HR1009_q3_kvar | Reactive Power | 6981 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Reactive Power Mode | Inverter | inverter088_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6982 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Reactive Power Set Point Percent | Inverter | inverter088_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6983 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power AC Percent | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6984 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power-AC | Inverter | inverter088_MODBUS.HR1008_p3_kW | Real Power-AC | 6985 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power-DC | Inverter | inverter088_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6986 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Air Intake | Inverter | inverter088_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6987 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Cabinet | Inverter | inverter088_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6988 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-IGBT | Inverter | inverter088_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6989 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Temperature-Module | Inverter | inverter088_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6990 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage A-B | Inverter | inverter088_MODBUS.HR1008_vRS_V | Voltage A-B | 6991 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage B-C | Inverter | inverter088_MODBUS.HR1002_vST_V | Voltage B-C | 6992 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage C-A | Inverter | inverter088_MODBUS.HR1003_vTR_V | Voltage C-A | 6993 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Voltage DC | Inverter | inverter088_MODBUS.HR1051_vdcBus_V | Voltage DC | 6994 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV088 | Daggett 3_SUB1_INV088_Fault Code 1 | Inverter | Inverter088_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6995 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Warning | Inverter | Inverter088_MODBUS.HRxxxx_currentWarning | Warning | 6996 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Internal Input Status | Inverter | Inverter088_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6997 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Internal Output Status | Inverter | Inverter088_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6998 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Module Fault Code | Inverter | Inverter088_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Internal Humidity | Inverter | Inverter088_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7000 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Humidity | Inverter | Inverter088_MODBUS.HRxxxx_humidity | Humidity | 7001 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_Comms Fault Time | Inverter | Inverter088_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7002 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Status | Inverter | Inverter088_MODBUS.HRxxxx_M1_status | Module Status | 7003 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 IR | Inverter | Inverter088_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 IS | Inverter | Inverter088_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 IT | Inverter | Inverter088_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7007 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7009 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7010 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 P | Inverter | Inverter088_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7011 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Q | Inverter | Inverter088_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7012 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7013 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7014 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M1 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7017 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Status | Inverter | Inverter088_MODBUS.HRxxxx_M2_status | Module Status | 7018 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 IR | Inverter | Inverter088_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7019 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 IS | Inverter | Inverter088_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 IT | Inverter | Inverter088_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7021 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7023 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7024 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7025 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 P | Inverter | Inverter088_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7026 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Q | Inverter | Inverter088_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7027 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7028 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7029 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7030 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7031 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M2 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7032 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Status | Inverter | Inverter088_MODBUS.HRxxxx_M3_status | Module Status | 7033 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 IR | Inverter | Inverter088_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 IS | Inverter | Inverter088_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7035 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 IT | Inverter | Inverter088_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7036 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7037 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7038 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7039 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7040 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 P | Inverter | Inverter088_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7041 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Q | Inverter | Inverter088_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7042 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7043 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7044 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7045 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7046 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M3 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7047 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Status | Inverter | Inverter088_MODBUS.HRxxxx_M4_status | Module Status | 7048 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 IR | Inverter | Inverter088_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 IS | Inverter | Inverter088_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 IT | Inverter | Inverter088_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7051 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7052 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7053 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7054 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7055 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 P | Inverter | Inverter088_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7056 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Q | Inverter | Inverter088_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7057 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7058 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7059 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7060 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M4 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7062 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Status | Inverter | Inverter088_MODBUS.HRxxxx_M5_status | Module Status | 7063 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 IR | Inverter | Inverter088_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 IS | Inverter | Inverter088_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 IT | Inverter | Inverter088_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7067 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7069 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7070 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 P | Inverter | Inverter088_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7071 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Q | Inverter | Inverter088_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7072 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7073 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7074 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7076 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M5 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7077 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Status | Inverter | Inverter088_MODBUS.HRxxxx_M6_status | Module Status | 7078 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 IR | Inverter | Inverter088_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 IS | Inverter | Inverter088_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 IT | Inverter | Inverter088_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 IDC | Inverter | Inverter088_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7082 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 VDCP | Inverter | Inverter088_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7083 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 VDCN | Inverter | Inverter088_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7084 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 VDC | Inverter | Inverter088_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7085 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 P | Inverter | Inverter088_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7086 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Q | Inverter | Inverter088_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7087 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Ambient Temp | Inverter | Inverter088_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7088 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Max IGBT Temp | Inverter | Inverter088_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7089 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 IO Status | Inverter | Inverter088_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7090 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Hardware Version | Inverter | Inverter088_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7091 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV088 | Daggett 3_SUB1_INV088_M6 Software Version | Inverter | Inverter088_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_A Phase Current | Inverter | inverter089_MODBUS.HR1004_i1_A | A Phase Current | 7093 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_B Phase Current | Inverter | inverter089_MODBUS.HR1005_i2_A | B Phase Current | 7094 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_C Phase Current | Inverter | inverter089_MODBUS.HR1006_i3_A | C Phase Current | 7095 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Bus Voltage | Inverter | inverter089_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7096 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV089 | Daggett 3_SUB1_INV089_Apparent Power | Inverter | inverter089_MODBUS.HR1010_s3_VA | Apparent Power | 7097 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 1 | Inverter | Inverter089_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7098 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC Input 1 | Inverter | Inverter089_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7099 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 2 | Inverter | Inverter089_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 2 | Inverter | Inverter089_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7101 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 3 | Inverter | Inverter089_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 3 | Inverter | Inverter089_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7103 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 4 | Inverter | Inverter089_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 4 | Inverter | Inverter089_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7105 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 5 | Inverter | Inverter089_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7106 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 5 | Inverter | Inverter089_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7107 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 6 | Inverter | Inverter089_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7108 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 6 | Inverter | Inverter089_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7109 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 7 | Inverter | Inverter089_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7110 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 7 | Inverter | Inverter089_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7111 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 8 | Inverter | Inverter089_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7112 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 8 | Inverter | Inverter089_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7113 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 9 | Inverter | Inverter089_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7114 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 9 | Inverter | Inverter089_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7115 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 10 | Inverter | Inverter089_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 10 | Inverter | Inverter089_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7117 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 11 | Inverter | Inverter089_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 11 | Inverter | Inverter089_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7119 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 12 | Inverter | Inverter089_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7120 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 12 | Inverter | Inverter089_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7121 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 13 | Inverter | Inverter089_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7122 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 13 | Inverter | Inverter089_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7123 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 14 | Inverter | Inverter089_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 14 | Inverter | Inverter089_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7125 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 15 | Inverter | Inverter089_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7126 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 15 | Inverter | Inverter089_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7127 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 16 | Inverter | Inverter089_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7128 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 16 | Inverter | Inverter089_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7129 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 17 | Inverter | Inverter089_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7130 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 17 | Inverter | Inverter089_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7131 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 18 | Inverter | Inverter089_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 18 | Inverter | Inverter089_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7133 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 19 | Inverter | Inverter089_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7134 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 19 | Inverter | Inverter089_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7135 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current DC Input 20 | Inverter | Inverter089_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7136 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC input 20 | Inverter | Inverter089_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7137 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current-AC | Inverter | inverter089_MODBUS.HR1007_i3Avg_A | Current-AC | 7138 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Current-DC | Inverter | inverter089_MODBUS.HR1062_idcInput_A | Current-DC | 7139 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Daily Energy Delivered | Inverter | inverter089_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7140 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power Set Point | Inverter | inverter089_MODBUS.HR0553_pRef | Real Power Set Point | 7141 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Reactive Power Set Point | Inverter | inverter089_MODBUS.HR0558_qRef | Reactive Power Set Point | 7142 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Frequency | Inverter | inverter089_MODBUS.HR1012_f3_Hz | Frequency | 7143 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV089 | Daggett 3_SUB1_INV089_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Insulation Resistance | Inverter | inverter089_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7144 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Number of DU Channels | Inverter | inverter089_MODBUS.HR0653_duChannels | Number of DU Channels | 7145 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Number of Running Modules | Inverter | inverter089_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7146 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Operating State | Inverter | inverter089_MODBUS.HR1123_currentStatus | Operating State | 7147 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Power Factor | Inverter | inverter089_MODBUS.HR1011_pf3 | Power Factor | 7148 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV089 | Daggett 3_SUB1_INV089_Ramp Down | Inverter | inverter089_MODBUS.HR0286_dropGradient_p | Ramp Down | 7149 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Ramp Up | Inverter | inverter089_MODBUS.HR0282_riseGradient_p | Ramp Up | 7150 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power Delivered | Inverter | inverter089_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7151 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Reactive Power Delivered | Inverter | inverter089_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7152 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power | 7153 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Reactive Power | Inverter | inverter089_MODBUS.HR1009_q3_kvar | Reactive Power | 7154 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Reactive Power Mode | Inverter | inverter089_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7155 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Reactive Power Set Point Percent | Inverter | inverter089_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7156 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power AC Percent | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7157 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power-AC | Inverter | inverter089_MODBUS.HR1008_p3_kW | Real Power-AC | 7158 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power-DC | Inverter | inverter089_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7159 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Air Intake | Inverter | inverter089_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7160 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Cabinet | Inverter | inverter089_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7161 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-IGBT | Inverter | inverter089_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7162 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Temperature-Module | Inverter | inverter089_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7163 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage A-B | Inverter | inverter089_MODBUS.HR1009_vRS_V | Voltage A-B | 7164 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage B-C | Inverter | inverter089_MODBUS.HR1002_vST_V | Voltage B-C | 7165 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage C-A | Inverter | inverter089_MODBUS.HR1003_vTR_V | Voltage C-A | 7166 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Voltage DC | Inverter | inverter089_MODBUS.HR1051_vdcBus_V | Voltage DC | 7167 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV089 | Daggett 3_SUB1_INV089_Fault Code 1 | Inverter | Inverter089_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7168 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Warning | Inverter | Inverter089_MODBUS.HRxxxx_currentWarning | Warning | 7169 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Internal Input Status | Inverter | Inverter089_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7170 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Internal Output Status | Inverter | Inverter089_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Module Fault Code | Inverter | Inverter089_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Internal Humidity | Inverter | Inverter089_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7173 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Humidity | Inverter | Inverter089_MODBUS.HRxxxx_humidity | Humidity | 7174 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_Comms Fault Time | Inverter | Inverter089_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7175 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Status | Inverter | Inverter089_MODBUS.HRxxxx_M1_status | Module Status | 7176 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 IR | Inverter | Inverter089_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 IS | Inverter | Inverter089_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 IT | Inverter | Inverter089_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7180 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7182 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7183 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 P | Inverter | Inverter089_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7184 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Q | Inverter | Inverter089_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7185 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7186 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7187 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M1 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7190 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Status | Inverter | Inverter089_MODBUS.HRxxxx_M2_status | Module Status | 7191 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 IR | Inverter | Inverter089_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 IS | Inverter | Inverter089_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 IT | Inverter | Inverter089_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7194 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7196 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7197 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7198 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 P | Inverter | Inverter089_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7199 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Q | Inverter | Inverter089_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7200 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7201 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7202 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7203 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7204 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M2 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7205 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Status | Inverter | Inverter089_MODBUS.HRxxxx_M3_status | Module Status | 7206 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 IR | Inverter | Inverter089_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 IS | Inverter | Inverter089_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 IT | Inverter | Inverter089_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7209 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7210 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7211 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7212 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7213 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 P | Inverter | Inverter089_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7214 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Q | Inverter | Inverter089_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7215 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7216 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7217 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7218 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7219 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M3 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7220 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Status | Inverter | Inverter089_MODBUS.HRxxxx_M4_status | Module Status | 7221 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 IR | Inverter | Inverter089_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 IS | Inverter | Inverter089_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 IT | Inverter | Inverter089_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7224 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7225 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7226 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7227 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7228 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 P | Inverter | Inverter089_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7229 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Q | Inverter | Inverter089_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7230 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7231 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7232 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7233 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M4 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7235 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Status | Inverter | Inverter089_MODBUS.HRxxxx_M5_status | Module Status | 7236 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 IR | Inverter | Inverter089_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 IS | Inverter | Inverter089_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 IT | Inverter | Inverter089_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7240 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7242 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7243 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 P | Inverter | Inverter089_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7244 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Q | Inverter | Inverter089_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7245 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7246 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7247 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M5 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Status | Inverter | Inverter089_MODBUS.HRxxxx_M6_status | Module Status | 7251 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 IR | Inverter | Inverter089_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 IS | Inverter | Inverter089_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 IT | Inverter | Inverter089_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 IDC | Inverter | Inverter089_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7255 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 VDCP | Inverter | Inverter089_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7256 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 VDCN | Inverter | Inverter089_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7257 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 VDC | Inverter | Inverter089_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7258 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 P | Inverter | Inverter089_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7259 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Q | Inverter | Inverter089_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7260 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Ambient Temp | Inverter | Inverter089_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7261 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Max IGBT Temp | Inverter | Inverter089_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7262 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 IO Status | Inverter | Inverter089_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7263 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Hardware Version | Inverter | Inverter089_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7264 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV089 | Daggett 3_SUB1_INV089_M6 Software Version | Inverter | Inverter089_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_A Phase Current | Inverter | inverter090_MODBUS.HR1004_i1_A | A Phase Current | 7266 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_B Phase Current | Inverter | inverter090_MODBUS.HR1005_i2_A | B Phase Current | 7267 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_C Phase Current | Inverter | inverter090_MODBUS.HR1006_i3_A | C Phase Current | 7268 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Bus Voltage | Inverter | inverter090_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7269 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV090 | Daggett 3_SUB1_INV090_Apparent Power | Inverter | inverter090_MODBUS.HR1010_s3_VA | Apparent Power | 7270 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 1 | Inverter | Inverter090_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7271 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC Input 1 | Inverter | Inverter090_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7272 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 2 | Inverter | Inverter090_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 2 | Inverter | Inverter090_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7274 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 3 | Inverter | Inverter090_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 3 | Inverter | Inverter090_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7276 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 4 | Inverter | Inverter090_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7277 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 4 | Inverter | Inverter090_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7278 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 5 | Inverter | Inverter090_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7279 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 5 | Inverter | Inverter090_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7280 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 6 | Inverter | Inverter090_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7281 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 6 | Inverter | Inverter090_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7282 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 7 | Inverter | Inverter090_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7283 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 7 | Inverter | Inverter090_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7284 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 8 | Inverter | Inverter090_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7285 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 8 | Inverter | Inverter090_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7286 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 9 | Inverter | Inverter090_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7287 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 9 | Inverter | Inverter090_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7288 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 10 | Inverter | Inverter090_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 10 | Inverter | Inverter090_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7290 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 11 | Inverter | Inverter090_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7291 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 11 | Inverter | Inverter090_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7292 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 12 | Inverter | Inverter090_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7293 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 12 | Inverter | Inverter090_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7294 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 13 | Inverter | Inverter090_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7295 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 13 | Inverter | Inverter090_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7296 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 14 | Inverter | Inverter090_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 14 | Inverter | Inverter090_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7298 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 15 | Inverter | Inverter090_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7299 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 15 | Inverter | Inverter090_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7300 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 16 | Inverter | Inverter090_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7301 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 16 | Inverter | Inverter090_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7302 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 17 | Inverter | Inverter090_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7303 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 17 | Inverter | Inverter090_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7304 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 18 | Inverter | Inverter090_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 18 | Inverter | Inverter090_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7306 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 19 | Inverter | Inverter090_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7307 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 19 | Inverter | Inverter090_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7308 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current DC Input 20 | Inverter | Inverter090_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7309 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC input 20 | Inverter | Inverter090_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7310 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current-AC | Inverter | inverter090_MODBUS.HR1007_i3Avg_A | Current-AC | 7311 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Current-DC | Inverter | inverter090_MODBUS.HR1062_idcInput_A | Current-DC | 7312 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Daily Energy Delivered | Inverter | inverter090_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7313 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power Set Point | Inverter | inverter090_MODBUS.HR0553_pRef | Real Power Set Point | 7314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Reactive Power Set Point | Inverter | inverter090_MODBUS.HR0558_qRef | Reactive Power Set Point | 7315 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Frequency | Inverter | inverter090_MODBUS.HR1012_f3_Hz | Frequency | 7316 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV090 | Daggett 3_SUB1_INV090_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Insulation Resistance | Inverter | inverter090_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7317 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Number of DU Channels | Inverter | inverter090_MODBUS.HR0653_duChannels | Number of DU Channels | 7318 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Number of Running Modules | Inverter | inverter090_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7319 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Operating State | Inverter | inverter090_MODBUS.HR1123_currentStatus | Operating State | 7320 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Power Factor | Inverter | inverter090_MODBUS.HR1011_pf3 | Power Factor | 7321 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV090 | Daggett 3_SUB1_INV090_Ramp Down | Inverter | inverter090_MODBUS.HR0286_dropGradient_p | Ramp Down | 7322 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Ramp Up | Inverter | inverter090_MODBUS.HR0282_riseGradient_p | Ramp Up | 7323 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power Delivered | Inverter | inverter090_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7324 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Reactive Power Delivered | Inverter | inverter090_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7325 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power | 7326 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Reactive Power | Inverter | inverter090_MODBUS.HR1009_q3_kvar | Reactive Power | 7327 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Reactive Power Mode | Inverter | inverter090_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7328 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Reactive Power Set Point Percent | Inverter | inverter090_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7329 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power AC Percent | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7330 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power-AC | Inverter | inverter090_MODBUS.HR1008_p3_kW | Real Power-AC | 7331 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power-DC | Inverter | inverter090_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7332 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Air Intake | Inverter | inverter090_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7333 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Cabinet | Inverter | inverter090_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7334 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-IGBT | Inverter | inverter090_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7335 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Temperature-Module | Inverter | inverter090_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7336 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage A-B | Inverter | inverter090_MODBUS.HR1010_vRS_V | Voltage A-B | 7337 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage B-C | Inverter | inverter090_MODBUS.HR1002_vST_V | Voltage B-C | 7338 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage C-A | Inverter | inverter090_MODBUS.HR1003_vTR_V | Voltage C-A | 7339 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Voltage DC | Inverter | inverter090_MODBUS.HR1051_vdcBus_V | Voltage DC | 7340 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV090 | Daggett 3_SUB1_INV090_Fault Code 1 | Inverter | Inverter090_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7341 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Warning | Inverter | Inverter090_MODBUS.HRxxxx_currentWarning | Warning | 7342 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Internal Input Status | Inverter | Inverter090_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7343 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Internal Output Status | Inverter | Inverter090_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Module Fault Code | Inverter | Inverter090_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Internal Humidity | Inverter | Inverter090_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7346 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Humidity | Inverter | Inverter090_MODBUS.HRxxxx_humidity | Humidity | 7347 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_Comms Fault Time | Inverter | Inverter090_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7348 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Status | Inverter | Inverter090_MODBUS.HRxxxx_M1_status | Module Status | 7349 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 IR | Inverter | Inverter090_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 IS | Inverter | Inverter090_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 IT | Inverter | Inverter090_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7353 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7355 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7356 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 P | Inverter | Inverter090_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7357 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Q | Inverter | Inverter090_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7358 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7359 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7360 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M1 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7363 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Status | Inverter | Inverter090_MODBUS.HRxxxx_M2_status | Module Status | 7364 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 IR | Inverter | Inverter090_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 IS | Inverter | Inverter090_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 IT | Inverter | Inverter090_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7367 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7369 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7370 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7371 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 P | Inverter | Inverter090_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7372 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Q | Inverter | Inverter090_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7373 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7374 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7375 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7376 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7377 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M2 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7378 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Status | Inverter | Inverter090_MODBUS.HRxxxx_M3_status | Module Status | 7379 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 IR | Inverter | Inverter090_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 IS | Inverter | Inverter090_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 IT | Inverter | Inverter090_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7382 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7383 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7384 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7385 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7386 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 P | Inverter | Inverter090_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7387 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Q | Inverter | Inverter090_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7388 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7389 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7390 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7391 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7392 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M3 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7393 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Status | Inverter | Inverter090_MODBUS.HRxxxx_M4_status | Module Status | 7394 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 IR | Inverter | Inverter090_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 IS | Inverter | Inverter090_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 IT | Inverter | Inverter090_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7397 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7398 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7399 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7400 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7401 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 P | Inverter | Inverter090_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7402 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Q | Inverter | Inverter090_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7403 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7404 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7405 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7406 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M4 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7408 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Status | Inverter | Inverter090_MODBUS.HRxxxx_M5_status | Module Status | 7409 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 IR | Inverter | Inverter090_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 IS | Inverter | Inverter090_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 IT | Inverter | Inverter090_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7413 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7415 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7416 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 P | Inverter | Inverter090_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7417 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Q | Inverter | Inverter090_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7418 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7419 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7420 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M5 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Status | Inverter | Inverter090_MODBUS.HRxxxx_M6_status | Module Status | 7424 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 IR | Inverter | Inverter090_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 IS | Inverter | Inverter090_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 IT | Inverter | Inverter090_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 IDC | Inverter | Inverter090_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7428 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 VDCP | Inverter | Inverter090_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7429 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 VDCN | Inverter | Inverter090_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7430 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 VDC | Inverter | Inverter090_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7431 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 P | Inverter | Inverter090_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7432 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Q | Inverter | Inverter090_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7433 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Ambient Temp | Inverter | Inverter090_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7434 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Max IGBT Temp | Inverter | Inverter090_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7435 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 IO Status | Inverter | Inverter090_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7436 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Hardware Version | Inverter | Inverter090_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7437 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV090 | Daggett 3_SUB1_INV090_M6 Software Version | Inverter | Inverter090_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_A Phase Current | Inverter | inverter091_MODBUS.HR1004_i1_A | A Phase Current | 7439 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_B Phase Current | Inverter | inverter091_MODBUS.HR1005_i2_A | B Phase Current | 7440 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_C Phase Current | Inverter | inverter091_MODBUS.HR1006_i3_A | C Phase Current | 7441 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Bus Voltage | Inverter | inverter091_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7442 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV091 | Daggett 3_SUB1_INV091_Apparent Power | Inverter | inverter091_MODBUS.HR1010_s3_VA | Apparent Power | 7443 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 1 | Inverter | Inverter091_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7444 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC Input 1 | Inverter | Inverter091_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7445 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 2 | Inverter | Inverter091_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 2 | Inverter | Inverter091_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7447 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 3 | Inverter | Inverter091_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 3 | Inverter | Inverter091_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7449 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 4 | Inverter | Inverter091_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7450 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 4 | Inverter | Inverter091_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7451 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 5 | Inverter | Inverter091_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7452 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 5 | Inverter | Inverter091_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7453 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 6 | Inverter | Inverter091_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7454 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 6 | Inverter | Inverter091_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7455 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 7 | Inverter | Inverter091_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7456 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 7 | Inverter | Inverter091_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7457 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 8 | Inverter | Inverter091_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7458 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 8 | Inverter | Inverter091_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7459 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 9 | Inverter | Inverter091_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7460 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 9 | Inverter | Inverter091_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7461 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 10 | Inverter | Inverter091_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 10 | Inverter | Inverter091_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7463 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 11 | Inverter | Inverter091_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7464 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 11 | Inverter | Inverter091_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7465 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 12 | Inverter | Inverter091_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7466 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 12 | Inverter | Inverter091_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7467 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 13 | Inverter | Inverter091_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7468 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 13 | Inverter | Inverter091_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7469 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 14 | Inverter | Inverter091_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 14 | Inverter | Inverter091_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7471 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 15 | Inverter | Inverter091_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7472 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 15 | Inverter | Inverter091_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7473 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 16 | Inverter | Inverter091_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7474 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 16 | Inverter | Inverter091_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7475 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 17 | Inverter | Inverter091_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7476 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 17 | Inverter | Inverter091_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7477 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 18 | Inverter | Inverter091_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 18 | Inverter | Inverter091_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7479 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 19 | Inverter | Inverter091_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7480 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 19 | Inverter | Inverter091_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7481 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current DC Input 20 | Inverter | Inverter091_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7482 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC input 20 | Inverter | Inverter091_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7483 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current-AC | Inverter | inverter091_MODBUS.HR1007_i3Avg_A | Current-AC | 7484 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Current-DC | Inverter | inverter091_MODBUS.HR1062_idcInput_A | Current-DC | 7485 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Daily Energy Delivered | Inverter | inverter091_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7486 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power Set Point | Inverter | inverter091_MODBUS.HR0553_pRef | Real Power Set Point | 7487 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Reactive Power Set Point | Inverter | inverter091_MODBUS.HR0558_qRef | Reactive Power Set Point | 7488 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Frequency | Inverter | inverter091_MODBUS.HR1012_f3_Hz | Frequency | 7489 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV091 | Daggett 3_SUB1_INV091_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Insulation Resistance | Inverter | inverter091_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7490 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Number of DU Channels | Inverter | inverter091_MODBUS.HR0653_duChannels | Number of DU Channels | 7491 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Number of Running Modules | Inverter | inverter091_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7492 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Operating State | Inverter | inverter091_MODBUS.HR1123_currentStatus | Operating State | 7493 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Power Factor | Inverter | inverter091_MODBUS.HR1011_pf3 | Power Factor | 7494 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV091 | Daggett 3_SUB1_INV091_Ramp Down | Inverter | inverter091_MODBUS.HR0286_dropGradient_p | Ramp Down | 7495 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Ramp Up | Inverter | inverter091_MODBUS.HR0282_riseGradient_p | Ramp Up | 7496 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power Delivered | Inverter | inverter091_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7497 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Reactive Power Delivered | Inverter | inverter091_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7498 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power | 7499 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Reactive Power | Inverter | inverter091_MODBUS.HR1009_q3_kvar | Reactive Power | 7500 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Reactive Power Mode | Inverter | inverter091_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7501 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Reactive Power Set Point Percent | Inverter | inverter091_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7502 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power AC Percent | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7503 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power-AC | Inverter | inverter091_MODBUS.HR1008_p3_kW | Real Power-AC | 7504 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power-DC | Inverter | inverter091_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7505 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Air Intake | Inverter | inverter091_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7506 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Cabinet | Inverter | inverter091_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7507 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-IGBT | Inverter | inverter091_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7508 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Temperature-Module | Inverter | inverter091_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7509 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage A-B | Inverter | inverter091_MODBUS.HR1001_vRS_V | Voltage A-B | 7510 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage B-C | Inverter | inverter091_MODBUS.HR1002_vST_V | Voltage B-C | 7511 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage C-A | Inverter | inverter091_MODBUS.HR1003_vTR_V | Voltage C-A | 7512 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Voltage DC | Inverter | inverter091_MODBUS.HR1051_vdcBus_V | Voltage DC | 7513 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV091 | Daggett 3_SUB1_INV091_Fault Code 1 | Inverter | Inverter091_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7514 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Warning | Inverter | Inverter091_MODBUS.HRxxxx_currentWarning | Warning | 7515 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Internal Input Status | Inverter | Inverter091_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7516 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Internal Output Status | Inverter | Inverter091_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Module Fault Code | Inverter | Inverter091_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Internal Humidity | Inverter | Inverter091_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7519 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Humidity | Inverter | Inverter091_MODBUS.HRxxxx_humidity | Humidity | 7520 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_Comms Fault Time | Inverter | Inverter091_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7521 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Status | Inverter | Inverter091_MODBUS.HRxxxx_M1_status | Module Status | 7522 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 IR | Inverter | Inverter091_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 IS | Inverter | Inverter091_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 IT | Inverter | Inverter091_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7526 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7528 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7529 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 P | Inverter | Inverter091_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7530 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Q | Inverter | Inverter091_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7531 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7532 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7533 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M1 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7536 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Status | Inverter | Inverter091_MODBUS.HRxxxx_M2_status | Module Status | 7537 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 IR | Inverter | Inverter091_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 IS | Inverter | Inverter091_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 IT | Inverter | Inverter091_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7540 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7542 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7543 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7544 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 P | Inverter | Inverter091_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7545 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Q | Inverter | Inverter091_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7546 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7547 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7548 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7549 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7550 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M2 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7551 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Status | Inverter | Inverter091_MODBUS.HRxxxx_M3_status | Module Status | 7552 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 IR | Inverter | Inverter091_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 IS | Inverter | Inverter091_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 IT | Inverter | Inverter091_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7555 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7556 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7557 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7558 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7559 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 P | Inverter | Inverter091_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7560 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Q | Inverter | Inverter091_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7561 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7562 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7563 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7564 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7565 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M3 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7566 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Status | Inverter | Inverter091_MODBUS.HRxxxx_M4_status | Module Status | 7567 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 IR | Inverter | Inverter091_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 IS | Inverter | Inverter091_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 IT | Inverter | Inverter091_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7570 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7571 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7572 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7573 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7574 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 P | Inverter | Inverter091_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7575 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Q | Inverter | Inverter091_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7576 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7577 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7578 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7579 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M4 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7581 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Status | Inverter | Inverter091_MODBUS.HRxxxx_M5_status | Module Status | 7582 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 IR | Inverter | Inverter091_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 IS | Inverter | Inverter091_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 IT | Inverter | Inverter091_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7586 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7588 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7589 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 P | Inverter | Inverter091_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7590 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Q | Inverter | Inverter091_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7591 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7592 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7593 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M5 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Status | Inverter | Inverter091_MODBUS.HRxxxx_M6_status | Module Status | 7597 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 IR | Inverter | Inverter091_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 IS | Inverter | Inverter091_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 IT | Inverter | Inverter091_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 IDC | Inverter | Inverter091_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7601 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 VDCP | Inverter | Inverter091_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7602 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 VDCN | Inverter | Inverter091_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7603 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 VDC | Inverter | Inverter091_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7604 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 P | Inverter | Inverter091_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7605 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Q | Inverter | Inverter091_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7606 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Ambient Temp | Inverter | Inverter091_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7607 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Max IGBT Temp | Inverter | Inverter091_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7608 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 IO Status | Inverter | Inverter091_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7609 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Hardware Version | Inverter | Inverter091_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7610 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV091 | Daggett 3_SUB1_INV091_M6 Software Version | Inverter | Inverter091_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_A Phase Current | Inverter | inverter092_MODBUS.HR1004_i1_A | A Phase Current | 7612 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_B Phase Current | Inverter | inverter092_MODBUS.HR1005_i2_A | B Phase Current | 7613 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_C Phase Current | Inverter | inverter092_MODBUS.HR1006_i3_A | C Phase Current | 7614 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Bus Voltage | Inverter | inverter092_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7615 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV092 | Daggett 3_SUB1_INV092_Apparent Power | Inverter | inverter092_MODBUS.HR1010_s3_VA | Apparent Power | 7616 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 1 | Inverter | Inverter092_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7617 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC Input 1 | Inverter | Inverter092_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7618 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 2 | Inverter | Inverter092_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 2 | Inverter | Inverter092_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7620 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 3 | Inverter | Inverter092_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 3 | Inverter | Inverter092_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7622 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 4 | Inverter | Inverter092_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7623 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 4 | Inverter | Inverter092_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7624 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 5 | Inverter | Inverter092_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7625 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 5 | Inverter | Inverter092_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7626 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 6 | Inverter | Inverter092_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7627 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 6 | Inverter | Inverter092_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7628 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 7 | Inverter | Inverter092_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7629 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 7 | Inverter | Inverter092_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7630 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 8 | Inverter | Inverter092_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7631 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 8 | Inverter | Inverter092_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7632 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 9 | Inverter | Inverter092_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7633 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 9 | Inverter | Inverter092_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7634 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 10 | Inverter | Inverter092_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 10 | Inverter | Inverter092_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7636 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 11 | Inverter | Inverter092_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7637 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 11 | Inverter | Inverter092_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7638 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 12 | Inverter | Inverter092_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7639 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 12 | Inverter | Inverter092_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7640 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 13 | Inverter | Inverter092_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7641 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 13 | Inverter | Inverter092_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7642 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 14 | Inverter | Inverter092_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 14 | Inverter | Inverter092_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7644 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 15 | Inverter | Inverter092_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7645 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 15 | Inverter | Inverter092_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7646 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 16 | Inverter | Inverter092_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7647 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 16 | Inverter | Inverter092_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7648 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 17 | Inverter | Inverter092_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7649 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 17 | Inverter | Inverter092_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7650 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 18 | Inverter | Inverter092_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 18 | Inverter | Inverter092_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7652 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 19 | Inverter | Inverter092_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7653 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 19 | Inverter | Inverter092_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7654 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current DC Input 20 | Inverter | Inverter092_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7655 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC input 20 | Inverter | Inverter092_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7656 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current-AC | Inverter | inverter092_MODBUS.HR1007_i3Avg_A | Current-AC | 7657 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Current-DC | Inverter | inverter092_MODBUS.HR1062_idcInput_A | Current-DC | 7658 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Daily Energy Delivered | Inverter | inverter092_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7659 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power Set Point | Inverter | inverter092_MODBUS.HR0553_pRef | Real Power Set Point | 7660 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Reactive Power Set Point | Inverter | inverter092_MODBUS.HR0558_qRef | Reactive Power Set Point | 7661 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Frequency | Inverter | inverter092_MODBUS.HR1012_f3_Hz | Frequency | 7662 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV092 | Daggett 3_SUB1_INV092_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Insulation Resistance | Inverter | inverter092_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7663 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Number of DU Channels | Inverter | inverter092_MODBUS.HR0653_duChannels | Number of DU Channels | 7664 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Number of Running Modules | Inverter | inverter092_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7665 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Operating State | Inverter | inverter092_MODBUS.HR1123_currentStatus | Operating State | 7666 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Power Factor | Inverter | inverter092_MODBUS.HR1011_pf3 | Power Factor | 7667 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV092 | Daggett 3_SUB1_INV092_Ramp Down | Inverter | inverter092_MODBUS.HR0286_dropGradient_p | Ramp Down | 7668 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Ramp Up | Inverter | inverter092_MODBUS.HR0282_riseGradient_p | Ramp Up | 7669 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power Delivered | Inverter | inverter092_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7670 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Reactive Power Delivered | Inverter | inverter092_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7671 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power | 7672 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Reactive Power | Inverter | inverter092_MODBUS.HR1009_q3_kvar | Reactive Power | 7673 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Reactive Power Mode | Inverter | inverter092_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7674 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Reactive Power Set Point Percent | Inverter | inverter092_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7675 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power AC Percent | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7676 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power-AC | Inverter | inverter092_MODBUS.HR1008_p3_kW | Real Power-AC | 7677 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power-DC | Inverter | inverter092_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7678 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Air Intake | Inverter | inverter092_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7679 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Cabinet | Inverter | inverter092_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7680 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-IGBT | Inverter | inverter092_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7681 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Temperature-Module | Inverter | inverter092_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7682 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage A-B | Inverter | inverter092_MODBUS.HR1002_vRS_V | Voltage A-B | 7683 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage B-C | Inverter | inverter092_MODBUS.HR1002_vST_V | Voltage B-C | 7684 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage C-A | Inverter | inverter092_MODBUS.HR1003_vTR_V | Voltage C-A | 7685 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Voltage DC | Inverter | inverter092_MODBUS.HR1051_vdcBus_V | Voltage DC | 7686 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV092 | Daggett 3_SUB1_INV092_Fault Code 1 | Inverter | Inverter092_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7687 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Warning | Inverter | Inverter092_MODBUS.HRxxxx_currentWarning | Warning | 7688 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Internal Input Status | Inverter | Inverter092_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7689 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Internal Output Status | Inverter | Inverter092_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Module Fault Code | Inverter | Inverter092_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Internal Humidity | Inverter | Inverter092_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7692 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Humidity | Inverter | Inverter092_MODBUS.HRxxxx_humidity | Humidity | 7693 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_Comms Fault Time | Inverter | Inverter092_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7694 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Status | Inverter | Inverter092_MODBUS.HRxxxx_M1_status | Module Status | 7695 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 IR | Inverter | Inverter092_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 IS | Inverter | Inverter092_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 IT | Inverter | Inverter092_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7699 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7701 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7702 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 P | Inverter | Inverter092_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7703 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Q | Inverter | Inverter092_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7704 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7705 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7706 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M1 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7709 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Status | Inverter | Inverter092_MODBUS.HRxxxx_M2_status | Module Status | 7710 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 IR | Inverter | Inverter092_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 IS | Inverter | Inverter092_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 IT | Inverter | Inverter092_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7713 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7715 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7716 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7717 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 P | Inverter | Inverter092_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7718 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Q | Inverter | Inverter092_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7719 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7720 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7721 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7722 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7723 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M2 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7724 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Status | Inverter | Inverter092_MODBUS.HRxxxx_M3_status | Module Status | 7725 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 IR | Inverter | Inverter092_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 IS | Inverter | Inverter092_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 IT | Inverter | Inverter092_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7728 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7729 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7730 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7731 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7732 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 P | Inverter | Inverter092_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7733 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Q | Inverter | Inverter092_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7734 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7735 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7736 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7737 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7738 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M3 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7739 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Status | Inverter | Inverter092_MODBUS.HRxxxx_M4_status | Module Status | 7740 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 IR | Inverter | Inverter092_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 IS | Inverter | Inverter092_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 IT | Inverter | Inverter092_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7743 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7744 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7745 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7746 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7747 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 P | Inverter | Inverter092_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7748 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Q | Inverter | Inverter092_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7749 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7750 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7751 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7752 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M4 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7754 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Status | Inverter | Inverter092_MODBUS.HRxxxx_M5_status | Module Status | 7755 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 IR | Inverter | Inverter092_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 IS | Inverter | Inverter092_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 IT | Inverter | Inverter092_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7759 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7761 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7762 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 P | Inverter | Inverter092_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7763 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Q | Inverter | Inverter092_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7764 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7765 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7766 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M5 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Status | Inverter | Inverter092_MODBUS.HRxxxx_M6_status | Module Status | 7770 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 IR | Inverter | Inverter092_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 IS | Inverter | Inverter092_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 IT | Inverter | Inverter092_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 IDC | Inverter | Inverter092_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7774 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 VDCP | Inverter | Inverter092_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7775 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 VDCN | Inverter | Inverter092_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7776 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 VDC | Inverter | Inverter092_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7777 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 P | Inverter | Inverter092_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7778 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Q | Inverter | Inverter092_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7779 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Ambient Temp | Inverter | Inverter092_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7780 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Max IGBT Temp | Inverter | Inverter092_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7781 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 IO Status | Inverter | Inverter092_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7782 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Hardware Version | Inverter | Inverter092_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7783 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV092 | Daggett 3_SUB1_INV092_M6 Software Version | Inverter | Inverter092_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_A Phase Current | Inverter | inverter093_MODBUS.HR1004_i1_A | A Phase Current | 7785 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_B Phase Current | Inverter | inverter093_MODBUS.HR1005_i2_A | B Phase Current | 7786 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_C Phase Current | Inverter | inverter093_MODBUS.HR1006_i3_A | C Phase Current | 7787 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Bus Voltage | Inverter | inverter093_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7788 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV093 | Daggett 3_SUB1_INV093_Apparent Power | Inverter | inverter093_MODBUS.HR1010_s3_VA | Apparent Power | 7789 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 1 | Inverter | Inverter093_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7790 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC Input 1 | Inverter | Inverter093_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7791 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 2 | Inverter | Inverter093_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 2 | Inverter | Inverter093_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7793 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 3 | Inverter | Inverter093_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 3 | Inverter | Inverter093_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7795 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 4 | Inverter | Inverter093_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7796 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 4 | Inverter | Inverter093_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7797 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 5 | Inverter | Inverter093_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7798 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 5 | Inverter | Inverter093_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7799 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 6 | Inverter | Inverter093_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7800 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 6 | Inverter | Inverter093_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7801 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 7 | Inverter | Inverter093_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7802 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 7 | Inverter | Inverter093_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7803 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 8 | Inverter | Inverter093_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7804 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 8 | Inverter | Inverter093_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7805 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 9 | Inverter | Inverter093_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7806 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 9 | Inverter | Inverter093_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7807 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 10 | Inverter | Inverter093_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 10 | Inverter | Inverter093_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7809 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 11 | Inverter | Inverter093_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7810 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 11 | Inverter | Inverter093_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7811 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 12 | Inverter | Inverter093_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7812 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 12 | Inverter | Inverter093_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7813 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 13 | Inverter | Inverter093_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7814 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 13 | Inverter | Inverter093_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7815 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 14 | Inverter | Inverter093_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 14 | Inverter | Inverter093_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7817 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 15 | Inverter | Inverter093_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7818 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 15 | Inverter | Inverter093_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7819 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 16 | Inverter | Inverter093_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7820 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 16 | Inverter | Inverter093_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7821 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 17 | Inverter | Inverter093_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7822 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 17 | Inverter | Inverter093_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7823 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 18 | Inverter | Inverter093_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 18 | Inverter | Inverter093_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7825 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 19 | Inverter | Inverter093_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7826 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 19 | Inverter | Inverter093_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7827 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current DC Input 20 | Inverter | Inverter093_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7828 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC input 20 | Inverter | Inverter093_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7829 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current-AC | Inverter | inverter093_MODBUS.HR1007_i3Avg_A | Current-AC | 7830 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Current-DC | Inverter | inverter093_MODBUS.HR1062_idcInput_A | Current-DC | 7831 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Daily Energy Delivered | Inverter | inverter093_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7832 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power Set Point | Inverter | inverter093_MODBUS.HR0553_pRef | Real Power Set Point | 7833 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Reactive Power Set Point | Inverter | inverter093_MODBUS.HR0558_qRef | Reactive Power Set Point | 7834 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Frequency | Inverter | inverter093_MODBUS.HR1012_f3_Hz | Frequency | 7835 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV093 | Daggett 3_SUB1_INV093_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Insulation Resistance | Inverter | inverter093_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7836 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Number of DU Channels | Inverter | inverter093_MODBUS.HR0653_duChannels | Number of DU Channels | 7837 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Number of Running Modules | Inverter | inverter093_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7838 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Operating State | Inverter | inverter093_MODBUS.HR1123_currentStatus | Operating State | 7839 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Power Factor | Inverter | inverter093_MODBUS.HR1011_pf3 | Power Factor | 7840 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV093 | Daggett 3_SUB1_INV093_Ramp Down | Inverter | inverter093_MODBUS.HR0286_dropGradient_p | Ramp Down | 7841 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Ramp Up | Inverter | inverter093_MODBUS.HR0282_riseGradient_p | Ramp Up | 7842 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power Delivered | Inverter | inverter093_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7843 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Reactive Power Delivered | Inverter | inverter093_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7844 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power | 7845 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Reactive Power | Inverter | inverter093_MODBUS.HR1009_q3_kvar | Reactive Power | 7846 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Reactive Power Mode | Inverter | inverter093_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7847 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Reactive Power Set Point Percent | Inverter | inverter093_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7848 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power AC Percent | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7849 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power-AC | Inverter | inverter093_MODBUS.HR1008_p3_kW | Real Power-AC | 7850 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power-DC | Inverter | inverter093_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7851 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Air Intake | Inverter | inverter093_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7852 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Cabinet | Inverter | inverter093_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7853 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-IGBT | Inverter | inverter093_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7854 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Temperature-Module | Inverter | inverter093_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7855 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage A-B | Inverter | inverter093_MODBUS.HR1003_vRS_V | Voltage A-B | 7856 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage B-C | Inverter | inverter093_MODBUS.HR1002_vST_V | Voltage B-C | 7857 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage C-A | Inverter | inverter093_MODBUS.HR1003_vTR_V | Voltage C-A | 7858 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Voltage DC | Inverter | inverter093_MODBUS.HR1051_vdcBus_V | Voltage DC | 7859 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV093 | Daggett 3_SUB1_INV093_Fault Code 1 | Inverter | Inverter093_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7860 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Warning | Inverter | Inverter093_MODBUS.HRxxxx_currentWarning | Warning | 7861 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Internal Input Status | Inverter | Inverter093_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7862 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Internal Output Status | Inverter | Inverter093_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Module Fault Code | Inverter | Inverter093_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Internal Humidity | Inverter | Inverter093_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7865 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Humidity | Inverter | Inverter093_MODBUS.HRxxxx_humidity | Humidity | 7866 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_Comms Fault Time | Inverter | Inverter093_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7867 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Status | Inverter | Inverter093_MODBUS.HRxxxx_M1_status | Module Status | 7868 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 IR | Inverter | Inverter093_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 IS | Inverter | Inverter093_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 IT | Inverter | Inverter093_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7872 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7874 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7875 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 P | Inverter | Inverter093_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7876 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Q | Inverter | Inverter093_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7877 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7878 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7879 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M1 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7882 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Status | Inverter | Inverter093_MODBUS.HRxxxx_M2_status | Module Status | 7883 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 IR | Inverter | Inverter093_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 IS | Inverter | Inverter093_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 IT | Inverter | Inverter093_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7886 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7888 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7889 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7890 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 P | Inverter | Inverter093_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7891 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Q | Inverter | Inverter093_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7892 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7893 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7894 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7895 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7896 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M2 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7897 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Status | Inverter | Inverter093_MODBUS.HRxxxx_M3_status | Module Status | 7898 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 IR | Inverter | Inverter093_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 IS | Inverter | Inverter093_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 IT | Inverter | Inverter093_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7901 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7902 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7903 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7904 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7905 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 P | Inverter | Inverter093_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7906 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Q | Inverter | Inverter093_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7907 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7908 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7909 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7910 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7911 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M3 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7912 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Status | Inverter | Inverter093_MODBUS.HRxxxx_M4_status | Module Status | 7913 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 IR | Inverter | Inverter093_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 IS | Inverter | Inverter093_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 IT | Inverter | Inverter093_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7916 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7917 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7918 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7919 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7920 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 P | Inverter | Inverter093_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7921 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Q | Inverter | Inverter093_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7922 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7923 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7924 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7925 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M4 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7927 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Status | Inverter | Inverter093_MODBUS.HRxxxx_M5_status | Module Status | 7928 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 IR | Inverter | Inverter093_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 IS | Inverter | Inverter093_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 IT | Inverter | Inverter093_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7932 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7934 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7935 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 P | Inverter | Inverter093_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7936 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Q | Inverter | Inverter093_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7937 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7938 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7939 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M5 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Status | Inverter | Inverter093_MODBUS.HRxxxx_M6_status | Module Status | 7943 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 IR | Inverter | Inverter093_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 IS | Inverter | Inverter093_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 IT | Inverter | Inverter093_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 IDC | Inverter | Inverter093_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7947 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 VDCP | Inverter | Inverter093_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7948 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 VDCN | Inverter | Inverter093_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7949 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 VDC | Inverter | Inverter093_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7950 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 P | Inverter | Inverter093_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7951 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Q | Inverter | Inverter093_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7952 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Ambient Temp | Inverter | Inverter093_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7953 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Max IGBT Temp | Inverter | Inverter093_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7954 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 IO Status | Inverter | Inverter093_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7955 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Hardware Version | Inverter | Inverter093_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7956 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV093 | Daggett 3_SUB1_INV093_M6 Software Version | Inverter | Inverter093_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_A Phase Current | Inverter | inverter094_MODBUS.HR1004_i1_A | A Phase Current | 7958 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_B Phase Current | Inverter | inverter094_MODBUS.HR1005_i2_A | B Phase Current | 7959 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_C Phase Current | Inverter | inverter094_MODBUS.HR1006_i3_A | C Phase Current | 7960 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Bus Voltage | Inverter | inverter094_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7961 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV094 | Daggett 3_SUB1_INV094_Apparent Power | Inverter | inverter094_MODBUS.HR1010_s3_VA | Apparent Power | 7962 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 1 | Inverter | Inverter094_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7963 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC Input 1 | Inverter | Inverter094_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7964 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 2 | Inverter | Inverter094_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 2 | Inverter | Inverter094_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7966 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 3 | Inverter | Inverter094_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 3 | Inverter | Inverter094_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7968 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 4 | Inverter | Inverter094_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7969 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 4 | Inverter | Inverter094_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7970 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 5 | Inverter | Inverter094_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7971 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 5 | Inverter | Inverter094_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7972 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 6 | Inverter | Inverter094_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7973 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 6 | Inverter | Inverter094_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7974 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 7 | Inverter | Inverter094_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7975 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 7 | Inverter | Inverter094_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7976 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 8 | Inverter | Inverter094_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7977 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 8 | Inverter | Inverter094_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7978 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 9 | Inverter | Inverter094_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7979 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 9 | Inverter | Inverter094_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7980 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 10 | Inverter | Inverter094_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 10 | Inverter | Inverter094_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7982 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 11 | Inverter | Inverter094_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7983 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 11 | Inverter | Inverter094_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7984 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 12 | Inverter | Inverter094_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7985 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 12 | Inverter | Inverter094_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7986 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 13 | Inverter | Inverter094_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7987 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 13 | Inverter | Inverter094_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7988 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 14 | Inverter | Inverter094_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 14 | Inverter | Inverter094_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7990 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 15 | Inverter | Inverter094_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7991 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 15 | Inverter | Inverter094_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7992 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 16 | Inverter | Inverter094_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7993 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 16 | Inverter | Inverter094_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7994 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 17 | Inverter | Inverter094_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7995 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 17 | Inverter | Inverter094_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7996 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 18 | Inverter | Inverter094_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 18 | Inverter | Inverter094_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7998 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 19 | Inverter | Inverter094_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7999 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 19 | Inverter | Inverter094_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 8000 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current DC Input 20 | Inverter | Inverter094_MODBUS.HR5919_du20_idc_A | Current DC Input# | 8001 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC input 20 | Inverter | Inverter094_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 8002 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current-AC | Inverter | inverter094_MODBUS.HR1007_i3Avg_A | Current-AC | 8003 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Current-DC | Inverter | inverter094_MODBUS.HR1062_idcInput_A | Current-DC | 8004 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Daily Energy Delivered | Inverter | inverter094_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 8005 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power Set Point | Inverter | inverter094_MODBUS.HR0553_pRef | Real Power Set Point | 8006 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Reactive Power Set Point | Inverter | inverter094_MODBUS.HR0558_qRef | Reactive Power Set Point | 8007 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Frequency | Inverter | inverter094_MODBUS.HR1012_f3_Hz | Frequency | 8008 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV094 | Daggett 3_SUB1_INV094_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Insulation Resistance | Inverter | inverter094_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 8009 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Number of DU Channels | Inverter | inverter094_MODBUS.HR0653_duChannels | Number of DU Channels | 8010 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Number of Running Modules | Inverter | inverter094_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 8011 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Operating State | Inverter | inverter094_MODBUS.HR1123_currentStatus | Operating State | 8012 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Power Factor | Inverter | inverter094_MODBUS.HR1011_pf3 | Power Factor | 8013 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV094 | Daggett 3_SUB1_INV094_Ramp Down | Inverter | inverter094_MODBUS.HR0286_dropGradient_p | Ramp Down | 8014 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Ramp Up | Inverter | inverter094_MODBUS.HR0282_riseGradient_p | Ramp Up | 8015 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power Delivered | Inverter | inverter094_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 8016 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Reactive Power Delivered | Inverter | inverter094_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 8017 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power | 8018 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Reactive Power | Inverter | inverter094_MODBUS.HR1009_q3_kvar | Reactive Power | 8019 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Reactive Power Mode | Inverter | inverter094_MODBUS.HR0552_qControlMode | Reactive Power Mode | 8020 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Reactive Power Set Point Percent | Inverter | inverter094_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 8021 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power AC Percent | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power AC Percent | 8022 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power-AC | Inverter | inverter094_MODBUS.HR1008_p3_kW | Real Power-AC | 8023 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power-DC | Inverter | inverter094_MODBUS.HR1061_pdcInput_W | Real Power-DC | 8024 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Air Intake | Inverter | inverter094_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 8025 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Cabinet | Inverter | inverter094_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 8026 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-IGBT | Inverter | inverter094_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 8027 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Temperature-Module | Inverter | inverter094_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 8028 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage A-B | Inverter | inverter094_MODBUS.HR1004_vRS_V | Voltage A-B | 8029 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage B-C | Inverter | inverter094_MODBUS.HR1002_vST_V | Voltage B-C | 8030 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage C-A | Inverter | inverter094_MODBUS.HR1003_vTR_V | Voltage C-A | 8031 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Voltage DC | Inverter | inverter094_MODBUS.HR1051_vdcBus_V | Voltage DC | 8032 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV094 | Daggett 3_SUB1_INV094_Fault Code 1 | Inverter | Inverter094_MODBUS.HRxxxx_currentFault | Fault Code 1 | 8033 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Warning | Inverter | Inverter094_MODBUS.HRxxxx_currentWarning | Warning | 8034 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Internal Input Status | Inverter | Inverter094_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 8035 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Internal Output Status | Inverter | Inverter094_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 8036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Module Fault Code | Inverter | Inverter094_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 8037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Internal Humidity | Inverter | Inverter094_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 8038 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Humidity | Inverter | Inverter094_MODBUS.HRxxxx_humidity | Humidity | 8039 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_Comms Fault Time | Inverter | Inverter094_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 8040 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Status | Inverter | Inverter094_MODBUS.HRxxxx_M1_status | Module Status | 8041 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 IR | Inverter | Inverter094_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 8042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 IS | Inverter | Inverter094_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 8043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 IT | Inverter | Inverter094_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 8044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 8045 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 8046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 8047 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 8048 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 P | Inverter | Inverter094_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 8049 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Q | Inverter | Inverter094_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 8050 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 8051 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 8052 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 8053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 8054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M1 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 8055 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Status | Inverter | Inverter094_MODBUS.HRxxxx_M2_status | Module Status | 8056 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 IR | Inverter | Inverter094_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 8057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 IS | Inverter | Inverter094_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 8058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 IT | Inverter | Inverter094_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 8059 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 8060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 8061 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 8062 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 8063 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 P | Inverter | Inverter094_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 8064 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Q | Inverter | Inverter094_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 8065 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 8066 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 8067 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 8068 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 8069 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M2 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 8070 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Status | Inverter | Inverter094_MODBUS.HRxxxx_M3_status | Module Status | 8071 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 IR | Inverter | Inverter094_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 8072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 IS | Inverter | Inverter094_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 8073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 IT | Inverter | Inverter094_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 8074 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 8075 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 8076 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 8077 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 8078 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 P | Inverter | Inverter094_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 8079 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Q | Inverter | Inverter094_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 8080 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 8081 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 8082 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 8083 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 8084 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M3 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 8085 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Status | Inverter | Inverter094_MODBUS.HRxxxx_M4_status | Module Status | 8086 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 IR | Inverter | Inverter094_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 8087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 IS | Inverter | Inverter094_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 8088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 IT | Inverter | Inverter094_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 8089 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 8090 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 8091 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 8092 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 8093 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 P | Inverter | Inverter094_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 8094 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Q | Inverter | Inverter094_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 8095 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 8096 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 8097 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 8098 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 8099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M4 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 8100 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Status | Inverter | Inverter094_MODBUS.HRxxxx_M5_status | Module Status | 8101 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 IR | Inverter | Inverter094_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 8102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 IS | Inverter | Inverter094_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 8103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 IT | Inverter | Inverter094_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 8104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 8105 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 8106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 8107 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 8108 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 P | Inverter | Inverter094_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 8109 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Q | Inverter | Inverter094_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 8110 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 8111 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 8112 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 8113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 8114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M5 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 8115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Status | Inverter | Inverter094_MODBUS.HRxxxx_M6_status | Module Status | 8116 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 IR | Inverter | Inverter094_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 8117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 IS | Inverter | Inverter094_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 8118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 IT | Inverter | Inverter094_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 8119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 IDC | Inverter | Inverter094_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 8120 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 VDCP | Inverter | Inverter094_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 8121 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 VDCN | Inverter | Inverter094_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 8122 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 VDC | Inverter | Inverter094_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 8123 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 P | Inverter | Inverter094_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 8124 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Q | Inverter | Inverter094_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 8125 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Ambient Temp | Inverter | Inverter094_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 8126 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Max IGBT Temp | Inverter | Inverter094_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 8127 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 IO Status | Inverter | Inverter094_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 8128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Hardware Version | Inverter | Inverter094_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 8129 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV094 | Daggett 3_SUB1_INV094_M6 Software Version | Inverter | Inverter094_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 8130 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_A Phase Current | Inverter | inverter095_MODBUS.HR1004_i1_A | A Phase Current | 8131 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_B Phase Current | Inverter | inverter095_MODBUS.HR1005_i2_A | B Phase Current | 8132 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_C Phase Current | Inverter | inverter095_MODBUS.HR1006_i3_A | C Phase Current | 8133 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Bus Voltage | Inverter | inverter095_MODBUS.HR1051_vdcBus_V | Bus Voltage | 8134 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV095 | Daggett 3_SUB1_INV095_Apparent Power | Inverter | inverter095_MODBUS.HR1010_s3_VA | Apparent Power | 8135 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 1 | Inverter | Inverter095_MODBUS.HR5805_du1_idc_A | Current DC Input# | 8136 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC Input 1 | Inverter | Inverter095_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 8137 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 2 | Inverter | Inverter095_MODBUS.HR5811_du2_idc_A | Current DC Input# | 8138 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 2 | Inverter | Inverter095_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 8139 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 3 | Inverter | Inverter095_MODBUS.HR5817_du3_idc_A | Current DC Input# | 8140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 3 | Inverter | Inverter095_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 8141 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 4 | Inverter | Inverter095_MODBUS.HR5823_du4_idc_A | Current DC Input# | 8142 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 4 | Inverter | Inverter095_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 8143 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 5 | Inverter | Inverter095_MODBUS.HR5829_du5_idc_A | Current DC Input# | 8144 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 5 | Inverter | Inverter095_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 8145 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 6 | Inverter | Inverter095_MODBUS.HR5835_du6_idc_A | Current DC Input# | 8146 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 6 | Inverter | Inverter095_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 8147 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 7 | Inverter | Inverter095_MODBUS.HR5841_du7_idc_A | Current DC Input# | 8148 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 7 | Inverter | Inverter095_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 8149 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 8 | Inverter | Inverter095_MODBUS.HR5847_du8_idc_A | Current DC Input# | 8150 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 8 | Inverter | Inverter095_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 8151 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 9 | Inverter | Inverter095_MODBUS.HR5853_du9_idc_A | Current DC Input# | 8152 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 9 | Inverter | Inverter095_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 8153 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 10 | Inverter | Inverter095_MODBUS.HR5859_du10_idc_A | Current DC Input# | 8154 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 10 | Inverter | Inverter095_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 8155 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 11 | Inverter | Inverter095_MODBUS.HR5865_du11_idc_A | Current DC Input# | 8156 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 11 | Inverter | Inverter095_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 8157 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 12 | Inverter | Inverter095_MODBUS.HR5871_du12_idc_A | Current DC Input# | 8158 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 12 | Inverter | Inverter095_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 8159 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 13 | Inverter | Inverter095_MODBUS.HR5877_du13_idc_A | Current DC Input# | 8160 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 13 | Inverter | Inverter095_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 8161 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 14 | Inverter | Inverter095_MODBUS.HR5883_du14_idc_A | Current DC Input# | 8162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 14 | Inverter | Inverter095_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 8163 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 15 | Inverter | Inverter095_MODBUS.HR5889_du15_idc_A | Current DC Input# | 8164 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 15 | Inverter | Inverter095_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 8165 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 16 | Inverter | Inverter095_MODBUS.HR5895_du16_idc_A | Current DC Input# | 8166 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 16 | Inverter | Inverter095_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 8167 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 17 | Inverter | Inverter095_MODBUS.HR5901_du17_idc_A | Current DC Input# | 8168 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 17 | Inverter | Inverter095_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 8169 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 18 | Inverter | Inverter095_MODBUS.HR5907_du18_idc_A | Current DC Input# | 8170 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 18 | Inverter | Inverter095_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 8171 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 19 | Inverter | Inverter095_MODBUS.HR5913_du19_idc_A | Current DC Input# | 8172 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 19 | Inverter | Inverter095_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 8173 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current DC Input 20 | Inverter | Inverter095_MODBUS.HR5919_du20_idc_A | Current DC Input# | 8174 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC input 20 | Inverter | Inverter095_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 8175 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current-AC | Inverter | inverter095_MODBUS.HR1007_i3Avg_A | Current-AC | 8176 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Current-DC | Inverter | inverter095_MODBUS.HR1062_idcInput_A | Current-DC | 8177 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Daily Energy Delivered | Inverter | inverter095_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 8178 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power Set Point | Inverter | inverter095_MODBUS.HR0553_pRef | Real Power Set Point | 8179 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Reactive Power Set Point | Inverter | inverter095_MODBUS.HR0558_qRef | Reactive Power Set Point | 8180 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Frequency | Inverter | inverter095_MODBUS.HR1012_f3_Hz | Frequency | 8181 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV095 | Daggett 3_SUB1_INV095_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Insulation Resistance | Inverter | inverter095_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 8182 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Number of DU Channels | Inverter | inverter095_MODBUS.HR0653_duChannels | Number of DU Channels | 8183 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Number of Running Modules | Inverter | inverter095_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 8184 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Operating State | Inverter | inverter095_MODBUS.HR1123_currentStatus | Operating State | 8185 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Power Factor | Inverter | inverter095_MODBUS.HR1011_pf3 | Power Factor | 8186 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV095 | Daggett 3_SUB1_INV095_Ramp Down | Inverter | inverter095_MODBUS.HR0286_dropGradient_p | Ramp Down | 8187 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Ramp Up | Inverter | inverter095_MODBUS.HR0282_riseGradient_p | Ramp Up | 8188 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power Delivered | Inverter | inverter095_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 8189 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Reactive Power Delivered | Inverter | inverter095_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 8190 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power | 8191 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Reactive Power | Inverter | inverter095_MODBUS.HR1009_q3_kvar | Reactive Power | 8192 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Reactive Power Mode | Inverter | inverter095_MODBUS.HR0552_qControlMode | Reactive Power Mode | 8193 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Reactive Power Set Point Percent | Inverter | inverter095_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 8194 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power AC Percent | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power AC Percent | 8195 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power-AC | Inverter | inverter095_MODBUS.HR1008_p3_kW | Real Power-AC | 8196 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power-DC | Inverter | inverter095_MODBUS.HR1061_pdcInput_W | Real Power-DC | 8197 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Air Intake | Inverter | inverter095_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 8198 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Cabinet | Inverter | inverter095_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 8199 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-IGBT | Inverter | inverter095_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 8200 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Temperature-Module | Inverter | inverter095_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 8201 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage A-B | Inverter | inverter095_MODBUS.HR1005_vRS_V | Voltage A-B | 8202 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage B-C | Inverter | inverter095_MODBUS.HR1002_vST_V | Voltage B-C | 8203 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage C-A | Inverter | inverter095_MODBUS.HR1003_vTR_V | Voltage C-A | 8204 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Voltage DC | Inverter | inverter095_MODBUS.HR1051_vdcBus_V | Voltage DC | 8205 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV095 | Daggett 3_SUB1_INV095_Fault Code 1 | Inverter | Inverter095_MODBUS.HRxxxx_currentFault | Fault Code 1 | 8206 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Warning | Inverter | Inverter095_MODBUS.HRxxxx_currentWarning | Warning | 8207 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Internal Input Status | Inverter | Inverter095_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 8208 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Internal Output Status | Inverter | Inverter095_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 8209 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Module Fault Code | Inverter | Inverter095_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 8210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Internal Humidity | Inverter | Inverter095_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 8211 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Humidity | Inverter | Inverter095_MODBUS.HRxxxx_humidity | Humidity | 8212 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_Comms Fault Time | Inverter | Inverter095_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 8213 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Status | Inverter | Inverter095_MODBUS.HRxxxx_M1_status | Module Status | 8214 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 IR | Inverter | Inverter095_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 8215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 IS | Inverter | Inverter095_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 8216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 IT | Inverter | Inverter095_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 8217 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 8218 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 8219 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 8220 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 8221 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 P | Inverter | Inverter095_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 8222 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Q | Inverter | Inverter095_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 8223 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 8224 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 8225 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 8226 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 8227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M1 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 8228 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Status | Inverter | Inverter095_MODBUS.HRxxxx_M2_status | Module Status | 8229 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 IR | Inverter | Inverter095_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 8230 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 IS | Inverter | Inverter095_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 8231 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 IT | Inverter | Inverter095_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 8232 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 8233 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 8234 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 8235 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 8236 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 P | Inverter | Inverter095_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 8237 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Q | Inverter | Inverter095_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 8238 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 8239 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 8240 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 8241 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 8242 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M2 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 8243 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Status | Inverter | Inverter095_MODBUS.HRxxxx_M3_status | Module Status | 8244 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 IR | Inverter | Inverter095_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 8245 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 IS | Inverter | Inverter095_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 8246 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 IT | Inverter | Inverter095_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 8247 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 8248 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 8249 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 8250 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 8251 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 P | Inverter | Inverter095_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 8252 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Q | Inverter | Inverter095_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 8253 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 8254 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 8255 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 8256 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 8257 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M3 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 8258 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Status | Inverter | Inverter095_MODBUS.HRxxxx_M4_status | Module Status | 8259 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 IR | Inverter | Inverter095_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 8260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 IS | Inverter | Inverter095_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 8261 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 IT | Inverter | Inverter095_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 8262 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 8263 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 8264 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 8265 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 8266 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 P | Inverter | Inverter095_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 8267 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Q | Inverter | Inverter095_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 8268 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 8269 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 8270 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 8271 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 8272 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M4 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 8273 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Status | Inverter | Inverter095_MODBUS.HRxxxx_M5_status | Module Status | 8274 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 IR | Inverter | Inverter095_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 8275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 IS | Inverter | Inverter095_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 8276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 IT | Inverter | Inverter095_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 8277 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 8278 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 8279 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 8280 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 8281 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 P | Inverter | Inverter095_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 8282 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Q | Inverter | Inverter095_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 8283 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 8284 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 8285 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 8286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 8287 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M5 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 8288 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Status | Inverter | Inverter095_MODBUS.HRxxxx_M6_status | Module Status | 8289 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 IR | Inverter | Inverter095_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 8290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 IS | Inverter | Inverter095_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 8291 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 IT | Inverter | Inverter095_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 8292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 IDC | Inverter | Inverter095_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 8293 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 VDCP | Inverter | Inverter095_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 8294 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 VDCN | Inverter | Inverter095_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 8295 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 VDC | Inverter | Inverter095_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 8296 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 P | Inverter | Inverter095_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 8297 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Q | Inverter | Inverter095_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 8298 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Ambient Temp | Inverter | Inverter095_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 8299 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Max IGBT Temp | Inverter | Inverter095_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 8300 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 IO Status | Inverter | Inverter095_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 8301 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Hardware Version | Inverter | Inverter095_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 8302 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV095 | Daggett 3_SUB1_INV095_M6 Software Version | Inverter | Inverter095_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 8303 |  | Requested-Available | 0 | 65535 | 1
Digital Inputs
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV048 | Daggett 3_SUB1_INV048_AutoStart On | Inverter | inverter048_MODBUS.HR0501_restartEn | AutoStart On | 0 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Comm Fail | Inverter | inverter048_commsFail | Comm Fail | 1 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Faulted | Inverter | inverter048_fault | Faulted | 2 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Locked Out | Inverter | inverter048_lockout | Locked Out | 3 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Master Control Enabled | Inverter | inverter048_masterControl | Master Control Enabled | 4 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Offline | Inverter | inverter048_offline | Offline | 5 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Ramp Up Enabled | Inverter | inverter048_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 6 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Ramp Down Enabled | Inverter | inverter048_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 7 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power Curtailment Flag | Inverter | inverter048_curtailed | Real Power Curtailment Flag | 8 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Following Setpoint | Inverter | inverter048_follwing | Following Setpoint | 9 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_AutoStart On | Inverter | inverter049_MODBUS.HR0501_restartEn | AutoStart On | 10 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Comm Fail | Inverter | inverter049_commsFail | Comm Fail | 11 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Faulted | Inverter | inverter049_fault | Faulted | 12 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Locked Out | Inverter | inverter049_lockout | Locked Out | 13 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Master Control Enabled | Inverter | inverter049_masterControl | Master Control Enabled | 14 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Offline | Inverter | inverter049_offline | Offline | 15 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Ramp Up Enabled | Inverter | inverter049_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 16 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Ramp Down Enabled | Inverter | inverter049_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 17 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power Curtailment Flag | Inverter | inverter049_curtailed | Real Power Curtailment Flag | 18 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Following Setpoint | Inverter | inverter049_follwing | Following Setpoint | 19 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_AutoStart On | Inverter | Inverter050_MODBUS.HR0501_restartEn | AutoStart On | 20 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Comm Fail | Inverter | Inverter050_commsFail | Comm Fail | 21 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Faulted | Inverter | Inverter050_fault | Faulted | 22 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Locked Out | Inverter | Inverter050_lockout | Locked Out | 23 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Master Control Enabled | Inverter | Inverter050_masterControl | Master Control Enabled | 24 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Offline | Inverter | Inverter050_offline | Offline | 25 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Ramp Up Enabled | Inverter | Inverter050_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 26 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Ramp Down Enabled | Inverter | Inverter050_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 27 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power Curtailment Flag | Inverter | Inverter050_curtailed | Real Power Curtailment Flag | 28 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Following Setpoint | Inverter | Inverter050_follwing | Following Setpoint | 29 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_AutoStart On | Inverter | Inverter051_MODBUS.HR0501_restartEn | AutoStart On | 30 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Comm Fail | Inverter | Inverter051_commsFail | Comm Fail | 31 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Faulted | Inverter | Inverter051_fault | Faulted | 32 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Locked Out | Inverter | Inverter051_lockout | Locked Out | 33 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Master Control Enabled | Inverter | Inverter051_masterControl | Master Control Enabled | 34 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Offline | Inverter | Inverter051_offline | Offline | 35 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Ramp Up Enabled | Inverter | Inverter051_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 36 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Ramp Down Enabled | Inverter | Inverter051_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 37 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power Curtailment Flag | Inverter | Inverter051_curtailed | Real Power Curtailment Flag | 38 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Following Setpoint | Inverter | Inverter051_follwing | Following Setpoint | 39 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_AutoStart On | Inverter | Inverter052_MODBUS.HR0501_restartEn | AutoStart On | 40 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Comm Fail | Inverter | Inverter052_commsFail | Comm Fail | 41 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Faulted | Inverter | Inverter052_fault | Faulted | 42 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Locked Out | Inverter | Inverter052_lockout | Locked Out | 43 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Master Control Enabled | Inverter | Inverter052_masterControl | Master Control Enabled | 44 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Offline | Inverter | Inverter052_offline | Offline | 45 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Ramp Up Enabled | Inverter | Inverter052_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 46 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Ramp Down Enabled | Inverter | Inverter052_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 47 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power Curtailment Flag | Inverter | Inverter052_curtailed | Real Power Curtailment Flag | 48 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Following Setpoint | Inverter | Inverter052_follwing | Following Setpoint | 49 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_AutoStart On | Inverter | Inverter053_MODBUS.HR0501_restartEn | AutoStart On | 50 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Comm Fail | Inverter | Inverter053_commsFail | Comm Fail | 51 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Faulted | Inverter | Inverter053_fault | Faulted | 52 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Locked Out | Inverter | Inverter053_lockout | Locked Out | 53 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Master Control Enabled | Inverter | Inverter053_masterControl | Master Control Enabled | 54 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Offline | Inverter | Inverter053_offline | Offline | 55 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Ramp Up Enabled | Inverter | Inverter053_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 56 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Ramp Down Enabled | Inverter | Inverter053_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 57 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power Curtailment Flag | Inverter | Inverter053_curtailed | Real Power Curtailment Flag | 58 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Following Setpoint | Inverter | Inverter053_follwing | Following Setpoint | 59 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_AutoStart On | Inverter | Inverter054_MODBUS.HR0501_restartEn | AutoStart On | 60 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Comm Fail | Inverter | Inverter054_commsFail | Comm Fail | 61 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Faulted | Inverter | Inverter054_fault | Faulted | 62 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Locked Out | Inverter | Inverter054_lockout | Locked Out | 63 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Master Control Enabled | Inverter | Inverter054_masterControl | Master Control Enabled | 64 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Offline | Inverter | Inverter054_offline | Offline | 65 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Ramp Up Enabled | Inverter | Inverter054_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 66 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Ramp Down Enabled | Inverter | Inverter054_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 67 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power Curtailment Flag | Inverter | Inverter054_curtailed | Real Power Curtailment Flag | 68 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Following Setpoint | Inverter | Inverter054_follwing | Following Setpoint | 69 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_AutoStart On | Inverter | Inverter055_MODBUS.HR0501_restartEn | AutoStart On | 70 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Comm Fail | Inverter | Inverter055_commsFail | Comm Fail | 71 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Faulted | Inverter | Inverter055_fault | Faulted | 72 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Locked Out | Inverter | Inverter055_lockout | Locked Out | 73 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Master Control Enabled | Inverter | Inverter055_masterControl | Master Control Enabled | 74 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Offline | Inverter | Inverter055_offline | Offline | 75 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Ramp Up Enabled | Inverter | Inverter055_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 76 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Ramp Down Enabled | Inverter | Inverter055_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 77 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power Curtailment Flag | Inverter | Inverter055_curtailed | Real Power Curtailment Flag | 78 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Following Setpoint | Inverter | Inverter055_follwing | Following Setpoint | 79 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_AutoStart On | Inverter | Inverter056_MODBUS.HR0501_restartEn | AutoStart On | 80 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Comm Fail | Inverter | Inverter056_commsFail | Comm Fail | 81 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Faulted | Inverter | Inverter056_fault | Faulted | 82 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Locked Out | Inverter | Inverter056_lockout | Locked Out | 83 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Master Control Enabled | Inverter | Inverter056_masterControl | Master Control Enabled | 84 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Offline | Inverter | Inverter056_offline | Offline | 85 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Ramp Up Enabled | Inverter | Inverter056_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 86 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Ramp Down Enabled | Inverter | Inverter056_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 87 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power Curtailment Flag | Inverter | Inverter056_curtailed | Real Power Curtailment Flag | 88 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Following Setpoint | Inverter | Inverter056_follwing | Following Setpoint | 89 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_AutoStart On | Inverter | Inverter057_MODBUS.HR0501_restartEn | AutoStart On | 90 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Comm Fail | Inverter | Inverter057_commsFail | Comm Fail | 91 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Faulted | Inverter | Inverter057_fault | Faulted | 92 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Locked Out | Inverter | Inverter057_lockout | Locked Out | 93 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Master Control Enabled | Inverter | Inverter057_masterControl | Master Control Enabled | 94 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Offline | Inverter | Inverter057_offline | Offline | 95 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Ramp Up Enabled | Inverter | Inverter057_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 96 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Ramp Down Enabled | Inverter | Inverter057_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 97 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power Curtailment Flag | Inverter | Inverter057_curtailed | Real Power Curtailment Flag | 98 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Following Setpoint | Inverter | Inverter057_follwing | Following Setpoint | 99 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_AutoStart On | Inverter | Inverter058_MODBUS.HR0501_restartEn | AutoStart On | 100 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Comm Fail | Inverter | Inverter058_commsFail | Comm Fail | 101 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Faulted | Inverter | Inverter058_fault | Faulted | 102 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Locked Out | Inverter | Inverter058_lockout | Locked Out | 103 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Master Control Enabled | Inverter | Inverter058_masterControl | Master Control Enabled | 104 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Offline | Inverter | Inverter058_offline | Offline | 105 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Ramp Up Enabled | Inverter | Inverter058_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 106 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Ramp Down Enabled | Inverter | Inverter058_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 107 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power Curtailment Flag | Inverter | Inverter058_curtailed | Real Power Curtailment Flag | 108 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Following Setpoint | Inverter | Inverter058_follwing | Following Setpoint | 109 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_AutoStart On | Inverter | Inverter059_MODBUS.HR0501_restartEn | AutoStart On | 110 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Comm Fail | Inverter | Inverter059_commsFail | Comm Fail | 111 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Faulted | Inverter | Inverter059_fault | Faulted | 112 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Locked Out | Inverter | Inverter059_lockout | Locked Out | 113 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Master Control Enabled | Inverter | Inverter059_masterControl | Master Control Enabled | 114 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Offline | Inverter | Inverter059_offline | Offline | 115 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Ramp Up Enabled | Inverter | Inverter059_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 116 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Ramp Down Enabled | Inverter | Inverter059_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 117 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power Curtailment Flag | Inverter | Inverter059_curtailed | Real Power Curtailment Flag | 118 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Following Setpoint | Inverter | Inverter059_follwing | Following Setpoint | 119 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_AutoStart On | Inverter | Inverter060_MODBUS.HR0501_restartEn | AutoStart On | 120 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Comm Fail | Inverter | Inverter060_commsFail | Comm Fail | 121 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Faulted | Inverter | Inverter060_fault | Faulted | 122 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Locked Out | Inverter | Inverter060_lockout | Locked Out | 123 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Master Control Enabled | Inverter | Inverter060_masterControl | Master Control Enabled | 124 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Offline | Inverter | Inverter060_offline | Offline | 125 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Ramp Up Enabled | Inverter | Inverter060_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 126 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Ramp Down Enabled | Inverter | Inverter060_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 127 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power Curtailment Flag | Inverter | Inverter060_curtailed | Real Power Curtailment Flag | 128 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Following Setpoint | Inverter | Inverter060_follwing | Following Setpoint | 129 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_AutoStart On | Inverter | Inverter061_MODBUS.HR0501_restartEn | AutoStart On | 130 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Comm Fail | Inverter | Inverter061_commsFail | Comm Fail | 131 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Faulted | Inverter | Inverter061_fault | Faulted | 132 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Locked Out | Inverter | Inverter061_lockout | Locked Out | 133 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Master Control Enabled | Inverter | Inverter061_masterControl | Master Control Enabled | 134 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Offline | Inverter | Inverter061_offline | Offline | 135 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Ramp Up Enabled | Inverter | Inverter061_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 136 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Ramp Down Enabled | Inverter | Inverter061_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 137 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power Curtailment Flag | Inverter | Inverter061_curtailed | Real Power Curtailment Flag | 138 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Following Setpoint | Inverter | Inverter061_follwing | Following Setpoint | 139 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_AutoStart On | Inverter | Inverter062_MODBUS.HR0501_restartEn | AutoStart On | 140 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Comm Fail | Inverter | Inverter062_commsFail | Comm Fail | 141 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Faulted | Inverter | Inverter062_fault | Faulted | 142 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Locked Out | Inverter | Inverter062_lockout | Locked Out | 143 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Master Control Enabled | Inverter | Inverter062_masterControl | Master Control Enabled | 144 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Offline | Inverter | Inverter062_offline | Offline | 145 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Ramp Up Enabled | Inverter | Inverter062_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 146 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Ramp Down Enabled | Inverter | Inverter062_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 147 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power Curtailment Flag | Inverter | Inverter062_curtailed | Real Power Curtailment Flag | 148 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Following Setpoint | Inverter | Inverter062_follwing | Following Setpoint | 149 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_AutoStart On | Inverter | Inverter063_MODBUS.HR0501_restartEn | AutoStart On | 150 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Comm Fail | Inverter | Inverter063_commsFail | Comm Fail | 151 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Faulted | Inverter | Inverter063_fault | Faulted | 152 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Locked Out | Inverter | Inverter063_lockout | Locked Out | 153 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Master Control Enabled | Inverter | Inverter063_masterControl | Master Control Enabled | 154 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Offline | Inverter | Inverter063_offline | Offline | 155 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Ramp Up Enabled | Inverter | Inverter063_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 156 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Ramp Down Enabled | Inverter | Inverter063_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 157 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power Curtailment Flag | Inverter | Inverter063_curtailed | Real Power Curtailment Flag | 158 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Following Setpoint | Inverter | Inverter063_follwing | Following Setpoint | 159 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_AutoStart On | Inverter | Inverter064_MODBUS.HR0501_restartEn | AutoStart On | 160 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Comm Fail | Inverter | Inverter064_commsFail | Comm Fail | 161 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Faulted | Inverter | Inverter064_fault | Faulted | 162 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Locked Out | Inverter | Inverter064_lockout | Locked Out | 163 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Master Control Enabled | Inverter | Inverter064_masterControl | Master Control Enabled | 164 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Offline | Inverter | Inverter064_offline | Offline | 165 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Ramp Up Enabled | Inverter | Inverter064_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 166 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Ramp Down Enabled | Inverter | Inverter064_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 167 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power Curtailment Flag | Inverter | Inverter064_curtailed | Real Power Curtailment Flag | 168 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Following Setpoint | Inverter | Inverter064_follwing | Following Setpoint | 169 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_AutoStart On | Inverter | Inverter065_MODBUS.HR0501_restartEn | AutoStart On | 170 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Comm Fail | Inverter | Inverter065_commsFail | Comm Fail | 171 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Faulted | Inverter | Inverter065_fault | Faulted | 172 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Locked Out | Inverter | Inverter065_lockout | Locked Out | 173 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Master Control Enabled | Inverter | Inverter065_masterControl | Master Control Enabled | 174 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Offline | Inverter | Inverter065_offline | Offline | 175 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Ramp Up Enabled | Inverter | Inverter065_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 176 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Ramp Down Enabled | Inverter | Inverter065_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 177 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power Curtailment Flag | Inverter | Inverter065_curtailed | Real Power Curtailment Flag | 178 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Following Setpoint | Inverter | Inverter065_follwing | Following Setpoint | 179 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_AutoStart On | Inverter | Inverter066_MODBUS.HR0501_restartEn | AutoStart On | 180 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Comm Fail | Inverter | Inverter066_commsFail | Comm Fail | 181 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Faulted | Inverter | Inverter066_fault | Faulted | 182 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Locked Out | Inverter | Inverter066_lockout | Locked Out | 183 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Master Control Enabled | Inverter | Inverter066_masterControl | Master Control Enabled | 184 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Offline | Inverter | Inverter066_offline | Offline | 185 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Ramp Up Enabled | Inverter | Inverter066_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 186 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Ramp Down Enabled | Inverter | Inverter066_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 187 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power Curtailment Flag | Inverter | Inverter066_curtailed | Real Power Curtailment Flag | 188 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Following Setpoint | Inverter | Inverter066_follwing | Following Setpoint | 189 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_AutoStart On | Inverter | Inverter067_MODBUS.HR0501_restartEn | AutoStart On | 190 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Comm Fail | Inverter | Inverter067_commsFail | Comm Fail | 191 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Faulted | Inverter | Inverter067_fault | Faulted | 192 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Locked Out | Inverter | Inverter067_lockout | Locked Out | 193 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Master Control Enabled | Inverter | Inverter067_masterControl | Master Control Enabled | 194 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Offline | Inverter | Inverter067_offline | Offline | 195 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Ramp Up Enabled | Inverter | Inverter067_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 196 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Ramp Down Enabled | Inverter | Inverter067_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 197 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power Curtailment Flag | Inverter | Inverter067_curtailed | Real Power Curtailment Flag | 198 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Following Setpoint | Inverter | Inverter067_follwing | Following Setpoint | 199 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_AutoStart On | Inverter | Inverter068_MODBUS.HR0501_restartEn | AutoStart On | 200 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Comm Fail | Inverter | Inverter068_commsFail | Comm Fail | 201 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Faulted | Inverter | Inverter068_fault | Faulted | 202 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Locked Out | Inverter | Inverter068_lockout | Locked Out | 203 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Master Control Enabled | Inverter | Inverter068_masterControl | Master Control Enabled | 204 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Offline | Inverter | Inverter068_offline | Offline | 205 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Ramp Up Enabled | Inverter | Inverter068_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 206 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Ramp Down Enabled | Inverter | Inverter068_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 207 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power Curtailment Flag | Inverter | Inverter068_curtailed | Real Power Curtailment Flag | 208 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Following Setpoint | Inverter | Inverter068_follwing | Following Setpoint | 209 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_AutoStart On | Inverter | Inverter069_MODBUS.HR0501_restartEn | AutoStart On | 210 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Comm Fail | Inverter | Inverter069_commsFail | Comm Fail | 211 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Faulted | Inverter | Inverter069_fault | Faulted | 212 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Locked Out | Inverter | Inverter069_lockout | Locked Out | 213 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Master Control Enabled | Inverter | Inverter069_masterControl | Master Control Enabled | 214 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Offline | Inverter | Inverter069_offline | Offline | 215 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Ramp Up Enabled | Inverter | Inverter069_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 216 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Ramp Down Enabled | Inverter | Inverter069_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 217 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power Curtailment Flag | Inverter | Inverter069_curtailed | Real Power Curtailment Flag | 218 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Following Setpoint | Inverter | Inverter069_follwing | Following Setpoint | 219 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_AutoStart On | Inverter | inverter070_MODBUS.HR0501_restartEn | AutoStart On | 220 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Comm Fail | Inverter | inverter070_commsFail | Comm Fail | 221 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Faulted | Inverter | inverter070_fault | Faulted | 222 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Locked Out | Inverter | inverter070_lockout | Locked Out | 223 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Master Control Enabled | Inverter | inverter070_masterControl | Master Control Enabled | 224 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Offline | Inverter | inverter070_offline | Offline | 225 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Ramp Up Enabled | Inverter | inverter070_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 226 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Ramp Down Enabled | Inverter | inverter070_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 227 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power Curtailment Flag | Inverter | inverter070_curtailed | Real Power Curtailment Flag | 228 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Following Setpoint | Inverter | inverter070_follwing | Following Setpoint | 229 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_AutoStart On | Inverter | inverter071_MODBUS.HR0501_restartEn | AutoStart On | 230 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Comm Fail | Inverter | inverter071_commsFail | Comm Fail | 231 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Faulted | Inverter | inverter071_fault | Faulted | 232 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Locked Out | Inverter | inverter071_lockout | Locked Out | 233 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Master Control Enabled | Inverter | inverter071_masterControl | Master Control Enabled | 234 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Offline | Inverter | inverter071_offline | Offline | 235 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Ramp Up Enabled | Inverter | inverter071_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 236 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Ramp Down Enabled | Inverter | inverter071_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 237 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power Curtailment Flag | Inverter | inverter071_curtailed | Real Power Curtailment Flag | 238 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Following Setpoint | Inverter | inverter071_follwing | Following Setpoint | 239 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_AutoStart On | Inverter | inverter072_MODBUS.HR0501_restartEn | AutoStart On | 240 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Comm Fail | Inverter | inverter072_commsFail | Comm Fail | 241 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Faulted | Inverter | inverter072_fault | Faulted | 242 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Locked Out | Inverter | inverter072_lockout | Locked Out | 243 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Master Control Enabled | Inverter | inverter072_masterControl | Master Control Enabled | 244 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Offline | Inverter | inverter072_offline | Offline | 245 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Ramp Up Enabled | Inverter | inverter072_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 246 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Ramp Down Enabled | Inverter | inverter072_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 247 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power Curtailment Flag | Inverter | inverter072_curtailed | Real Power Curtailment Flag | 248 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Following Setpoint | Inverter | inverter072_follwing | Following Setpoint | 249 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_AutoStart On | Inverter | inverter073_MODBUS.HR0501_restartEn | AutoStart On | 250 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Comm Fail | Inverter | inverter073_commsFail | Comm Fail | 251 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Faulted | Inverter | inverter073_fault | Faulted | 252 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Locked Out | Inverter | inverter073_lockout | Locked Out | 253 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Master Control Enabled | Inverter | inverter073_masterControl | Master Control Enabled | 254 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Offline | Inverter | inverter073_offline | Offline | 255 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Ramp Up Enabled | Inverter | inverter073_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 256 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Ramp Down Enabled | Inverter | inverter073_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 257 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Real Power Curtailment Flag | Inverter | inverter073_curtailed | Real Power Curtailment Flag | 258 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Following Setpoint | Inverter | inverter073_follwing | Following Setpoint | 259 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_AutoStart On | Inverter | inverter074_MODBUS.HR0501_restartEn | AutoStart On | 260 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Comm Fail | Inverter | inverter074_commsFail | Comm Fail | 261 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Faulted | Inverter | inverter074_fault | Faulted | 262 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Locked Out | Inverter | inverter074_lockout | Locked Out | 263 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Master Control Enabled | Inverter | inverter074_masterControl | Master Control Enabled | 264 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Offline | Inverter | inverter074_offline | Offline | 265 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Ramp Up Enabled | Inverter | inverter074_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 266 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Ramp Down Enabled | Inverter | inverter074_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 267 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Real Power Curtailment Flag | Inverter | inverter074_curtailed | Real Power Curtailment Flag | 268 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Following Setpoint | Inverter | inverter074_follwing | Following Setpoint | 269 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_AutoStart On | Inverter | inverter075_MODBUS.HR0501_restartEn | AutoStart On | 270 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Comm Fail | Inverter | inverter075_commsFail | Comm Fail | 271 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Faulted | Inverter | inverter075_fault | Faulted | 272 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Locked Out | Inverter | inverter075_lockout | Locked Out | 273 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Master Control Enabled | Inverter | inverter075_masterControl | Master Control Enabled | 274 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Offline | Inverter | inverter075_offline | Offline | 275 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Ramp Up Enabled | Inverter | inverter075_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 276 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Ramp Down Enabled | Inverter | inverter075_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 277 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Real Power Curtailment Flag | Inverter | inverter075_curtailed | Real Power Curtailment Flag | 278 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Following Setpoint | Inverter | inverter075_follwing | Following Setpoint | 279 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_AutoStart On | Inverter | inverter076_MODBUS.HR0501_restartEn | AutoStart On | 280 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Comm Fail | Inverter | inverter076_commsFail | Comm Fail | 281 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Faulted | Inverter | inverter076_fault | Faulted | 282 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Locked Out | Inverter | inverter076_lockout | Locked Out | 283 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Master Control Enabled | Inverter | inverter076_masterControl | Master Control Enabled | 284 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Offline | Inverter | inverter076_offline | Offline | 285 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Ramp Up Enabled | Inverter | inverter076_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 286 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Ramp Down Enabled | Inverter | inverter076_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 287 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Real Power Curtailment Flag | Inverter | inverter076_curtailed | Real Power Curtailment Flag | 288 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Following Setpoint | Inverter | inverter076_follwing | Following Setpoint | 289 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_AutoStart On | Inverter | inverter077_MODBUS.HR0501_restartEn | AutoStart On | 290 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Comm Fail | Inverter | inverter077_commsFail | Comm Fail | 291 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Faulted | Inverter | inverter077_fault | Faulted | 292 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Locked Out | Inverter | inverter077_lockout | Locked Out | 293 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Master Control Enabled | Inverter | inverter077_masterControl | Master Control Enabled | 294 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Offline | Inverter | inverter077_offline | Offline | 295 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Ramp Up Enabled | Inverter | inverter077_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 296 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Ramp Down Enabled | Inverter | inverter077_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 297 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Real Power Curtailment Flag | Inverter | inverter077_curtailed | Real Power Curtailment Flag | 298 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Following Setpoint | Inverter | inverter077_follwing | Following Setpoint | 299 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_AutoStart On | Inverter | inverter078_MODBUS.HR0501_restartEn | AutoStart On | 300 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Comm Fail | Inverter | inverter078_commsFail | Comm Fail | 301 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Faulted | Inverter | inverter078_fault | Faulted | 302 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Locked Out | Inverter | inverter078_lockout | Locked Out | 303 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Master Control Enabled | Inverter | inverter078_masterControl | Master Control Enabled | 304 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Offline | Inverter | inverter078_offline | Offline | 305 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Ramp Up Enabled | Inverter | inverter078_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 306 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Ramp Down Enabled | Inverter | inverter078_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 307 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Real Power Curtailment Flag | Inverter | inverter078_curtailed | Real Power Curtailment Flag | 308 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Following Setpoint | Inverter | inverter078_follwing | Following Setpoint | 309 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_AutoStart On | Inverter | inverter079_MODBUS.HR0501_restartEn | AutoStart On | 310 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Comm Fail | Inverter | inverter079_commsFail | Comm Fail | 311 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Faulted | Inverter | inverter079_fault | Faulted | 312 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Locked Out | Inverter | inverter079_lockout | Locked Out | 313 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Master Control Enabled | Inverter | inverter079_masterControl | Master Control Enabled | 314 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Offline | Inverter | inverter079_offline | Offline | 315 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Ramp Up Enabled | Inverter | inverter079_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 316 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Ramp Down Enabled | Inverter | inverter079_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 317 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Real Power Curtailment Flag | Inverter | inverter079_curtailed | Real Power Curtailment Flag | 318 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Following Setpoint | Inverter | inverter079_follwing | Following Setpoint | 319 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_AutoStart On | Inverter | inverter080_MODBUS.HR0501_restartEn | AutoStart On | 320 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Comm Fail | Inverter | inverter080_commsFail | Comm Fail | 321 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Faulted | Inverter | inverter080_fault | Faulted | 322 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Locked Out | Inverter | inverter080_lockout | Locked Out | 323 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Master Control Enabled | Inverter | inverter080_masterControl | Master Control Enabled | 324 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Offline | Inverter | inverter080_offline | Offline | 325 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Ramp Up Enabled | Inverter | inverter080_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 326 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Ramp Down Enabled | Inverter | inverter080_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 327 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Real Power Curtailment Flag | Inverter | inverter080_curtailed | Real Power Curtailment Flag | 328 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Following Setpoint | Inverter | inverter080_follwing | Following Setpoint | 329 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_AutoStart On | Inverter | inverter081_MODBUS.HR0501_restartEn | AutoStart On | 330 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Comm Fail | Inverter | inverter081_commsFail | Comm Fail | 331 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Faulted | Inverter | inverter081_fault | Faulted | 332 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Locked Out | Inverter | inverter081_lockout | Locked Out | 333 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Master Control Enabled | Inverter | inverter081_masterControl | Master Control Enabled | 334 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Offline | Inverter | inverter081_offline | Offline | 335 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Ramp Up Enabled | Inverter | inverter081_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 336 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Ramp Down Enabled | Inverter | inverter081_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 337 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Real Power Curtailment Flag | Inverter | inverter081_curtailed | Real Power Curtailment Flag | 338 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Following Setpoint | Inverter | inverter081_follwing | Following Setpoint | 339 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_AutoStart On | Inverter | inverter082_MODBUS.HR0501_restartEn | AutoStart On | 340 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Comm Fail | Inverter | inverter082_commsFail | Comm Fail | 341 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Faulted | Inverter | inverter082_fault | Faulted | 342 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Locked Out | Inverter | inverter082_lockout | Locked Out | 343 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Master Control Enabled | Inverter | inverter082_masterControl | Master Control Enabled | 344 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Offline | Inverter | inverter082_offline | Offline | 345 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Ramp Up Enabled | Inverter | inverter082_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 346 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Ramp Down Enabled | Inverter | inverter082_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 347 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Real Power Curtailment Flag | Inverter | inverter082_curtailed | Real Power Curtailment Flag | 348 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Following Setpoint | Inverter | inverter082_follwing | Following Setpoint | 349 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_AutoStart On | Inverter | inverter083_MODBUS.HR0501_restartEn | AutoStart On | 350 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Comm Fail | Inverter | inverter083_commsFail | Comm Fail | 351 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Faulted | Inverter | inverter083_fault | Faulted | 352 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Locked Out | Inverter | inverter083_lockout | Locked Out | 353 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Master Control Enabled | Inverter | inverter083_masterControl | Master Control Enabled | 354 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Offline | Inverter | inverter083_offline | Offline | 355 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Ramp Up Enabled | Inverter | inverter083_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 356 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Ramp Down Enabled | Inverter | inverter083_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 357 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Real Power Curtailment Flag | Inverter | inverter083_curtailed | Real Power Curtailment Flag | 358 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Following Setpoint | Inverter | inverter083_follwing | Following Setpoint | 359 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_AutoStart On | Inverter | inverter084_MODBUS.HR0501_restartEn | AutoStart On | 360 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Comm Fail | Inverter | inverter084_commsFail | Comm Fail | 361 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Faulted | Inverter | inverter084_fault | Faulted | 362 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Locked Out | Inverter | inverter084_lockout | Locked Out | 363 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Master Control Enabled | Inverter | inverter084_masterControl | Master Control Enabled | 364 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Offline | Inverter | inverter084_offline | Offline | 365 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Ramp Up Enabled | Inverter | inverter084_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 366 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Ramp Down Enabled | Inverter | inverter084_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 367 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Real Power Curtailment Flag | Inverter | inverter084_curtailed | Real Power Curtailment Flag | 368 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Following Setpoint | Inverter | inverter084_follwing | Following Setpoint | 369 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_AutoStart On | Inverter | inverter085_MODBUS.HR0501_restartEn | AutoStart On | 370 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Comm Fail | Inverter | inverter085_commsFail | Comm Fail | 371 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Faulted | Inverter | inverter085_fault | Faulted | 372 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Locked Out | Inverter | inverter085_lockout | Locked Out | 373 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Master Control Enabled | Inverter | inverter085_masterControl | Master Control Enabled | 374 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Offline | Inverter | inverter085_offline | Offline | 375 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Ramp Up Enabled | Inverter | inverter085_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 376 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Ramp Down Enabled | Inverter | inverter085_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 377 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Real Power Curtailment Flag | Inverter | inverter085_curtailed | Real Power Curtailment Flag | 378 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Following Setpoint | Inverter | inverter085_follwing | Following Setpoint | 379 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_AutoStart On | Inverter | inverter086_MODBUS.HR0501_restartEn | AutoStart On | 380 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Comm Fail | Inverter | inverter086_commsFail | Comm Fail | 381 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Faulted | Inverter | inverter086_fault | Faulted | 382 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Locked Out | Inverter | inverter086_lockout | Locked Out | 383 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Master Control Enabled | Inverter | inverter086_masterControl | Master Control Enabled | 384 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Offline | Inverter | inverter086_offline | Offline | 385 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Ramp Up Enabled | Inverter | inverter086_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 386 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Ramp Down Enabled | Inverter | inverter086_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 387 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Real Power Curtailment Flag | Inverter | inverter086_curtailed | Real Power Curtailment Flag | 388 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Following Setpoint | Inverter | inverter086_follwing | Following Setpoint | 389 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_AutoStart On | Inverter | inverter087_MODBUS.HR0501_restartEn | AutoStart On | 390 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Comm Fail | Inverter | inverter087_commsFail | Comm Fail | 391 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Faulted | Inverter | inverter087_fault | Faulted | 392 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Locked Out | Inverter | inverter087_lockout | Locked Out | 393 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Master Control Enabled | Inverter | inverter087_masterControl | Master Control Enabled | 394 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Offline | Inverter | inverter087_offline | Offline | 395 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Ramp Up Enabled | Inverter | inverter087_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 396 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Ramp Down Enabled | Inverter | inverter087_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 397 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Real Power Curtailment Flag | Inverter | inverter087_curtailed | Real Power Curtailment Flag | 398 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Following Setpoint | Inverter | inverter087_follwing | Following Setpoint | 399 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_AutoStart On | Inverter | inverter088_MODBUS.HR0501_restartEn | AutoStart On | 400 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Comm Fail | Inverter | inverter088_commsFail | Comm Fail | 401 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Faulted | Inverter | inverter088_fault | Faulted | 402 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Locked Out | Inverter | inverter088_lockout | Locked Out | 403 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Master Control Enabled | Inverter | inverter088_masterControl | Master Control Enabled | 404 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Offline | Inverter | inverter088_offline | Offline | 405 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Ramp Up Enabled | Inverter | inverter088_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 406 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Ramp Down Enabled | Inverter | inverter088_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 407 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Real Power Curtailment Flag | Inverter | inverter088_curtailed | Real Power Curtailment Flag | 408 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Following Setpoint | Inverter | inverter088_follwing | Following Setpoint | 409 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_AutoStart On | Inverter | inverter089_MODBUS.HR0501_restartEn | AutoStart On | 410 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Comm Fail | Inverter | inverter089_commsFail | Comm Fail | 411 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Faulted | Inverter | inverter089_fault | Faulted | 412 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Locked Out | Inverter | inverter089_lockout | Locked Out | 413 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Master Control Enabled | Inverter | inverter089_masterControl | Master Control Enabled | 414 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Offline | Inverter | inverter089_offline | Offline | 415 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Ramp Up Enabled | Inverter | inverter089_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 416 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Ramp Down Enabled | Inverter | inverter089_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 417 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Real Power Curtailment Flag | Inverter | inverter089_curtailed | Real Power Curtailment Flag | 418 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Following Setpoint | Inverter | inverter089_follwing | Following Setpoint | 419 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_AutoStart On | Inverter | inverter090_MODBUS.HR0501_restartEn | AutoStart On | 420 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Comm Fail | Inverter | inverter090_commsFail | Comm Fail | 421 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Faulted | Inverter | inverter090_fault | Faulted | 422 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Locked Out | Inverter | inverter090_lockout | Locked Out | 423 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Master Control Enabled | Inverter | inverter090_masterControl | Master Control Enabled | 424 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Offline | Inverter | inverter090_offline | Offline | 425 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Ramp Up Enabled | Inverter | inverter090_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 426 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Ramp Down Enabled | Inverter | inverter090_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 427 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Real Power Curtailment Flag | Inverter | inverter090_curtailed | Real Power Curtailment Flag | 428 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Following Setpoint | Inverter | inverter090_follwing | Following Setpoint | 429 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_AutoStart On | Inverter | inverter091_MODBUS.HR0501_restartEn | AutoStart On | 430 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Comm Fail | Inverter | inverter091_commsFail | Comm Fail | 431 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Faulted | Inverter | inverter091_fault | Faulted | 432 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Locked Out | Inverter | inverter091_lockout | Locked Out | 433 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Master Control Enabled | Inverter | inverter091_masterControl | Master Control Enabled | 434 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Offline | Inverter | inverter091_offline | Offline | 435 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Ramp Up Enabled | Inverter | inverter091_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 436 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Ramp Down Enabled | Inverter | inverter091_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 437 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Real Power Curtailment Flag | Inverter | inverter091_curtailed | Real Power Curtailment Flag | 438 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Following Setpoint | Inverter | inverter091_follwing | Following Setpoint | 439 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_AutoStart On | Inverter | inverter092_MODBUS.HR0501_restartEn | AutoStart On | 440 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Comm Fail | Inverter | inverter092_commsFail | Comm Fail | 441 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Faulted | Inverter | inverter092_fault | Faulted | 442 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Locked Out | Inverter | inverter092_lockout | Locked Out | 443 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Master Control Enabled | Inverter | inverter092_masterControl | Master Control Enabled | 444 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Offline | Inverter | inverter092_offline | Offline | 445 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Ramp Up Enabled | Inverter | inverter092_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 446 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Ramp Down Enabled | Inverter | inverter092_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 447 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Real Power Curtailment Flag | Inverter | inverter092_curtailed | Real Power Curtailment Flag | 448 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Following Setpoint | Inverter | inverter092_follwing | Following Setpoint | 449 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_AutoStart On | Inverter | inverter093_MODBUS.HR0501_restartEn | AutoStart On | 450 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Comm Fail | Inverter | inverter093_commsFail | Comm Fail | 451 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Faulted | Inverter | inverter093_fault | Faulted | 452 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Locked Out | Inverter | inverter093_lockout | Locked Out | 453 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Master Control Enabled | Inverter | inverter093_masterControl | Master Control Enabled | 454 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Offline | Inverter | inverter093_offline | Offline | 455 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Ramp Up Enabled | Inverter | inverter093_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 456 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Ramp Down Enabled | Inverter | inverter093_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 457 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Real Power Curtailment Flag | Inverter | inverter093_curtailed | Real Power Curtailment Flag | 458 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Following Setpoint | Inverter | inverter093_follwing | Following Setpoint | 459 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_AutoStart On | Inverter | inverter094_MODBUS.HR0501_restartEn | AutoStart On | 460 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Comm Fail | Inverter | inverter094_commsFail | Comm Fail | 461 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Faulted | Inverter | inverter094_fault | Faulted | 462 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Locked Out | Inverter | inverter094_lockout | Locked Out | 463 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Master Control Enabled | Inverter | inverter094_masterControl | Master Control Enabled | 464 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Offline | Inverter | inverter094_offline | Offline | 465 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Ramp Up Enabled | Inverter | inverter094_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 466 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Ramp Down Enabled | Inverter | inverter094_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 467 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Real Power Curtailment Flag | Inverter | inverter094_curtailed | Real Power Curtailment Flag | 468 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Following Setpoint | Inverter | inverter094_follwing | Following Setpoint | 469 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_AutoStart On | Inverter | inverter095_MODBUS.HR0501_restartEn | AutoStart On | 470 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Comm Fail | Inverter | inverter095_commsFail | Comm Fail | 471 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Faulted | Inverter | inverter095_fault | Faulted | 472 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Locked Out | Inverter | inverter095_lockout | Locked Out | 473 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Master Control Enabled | Inverter | inverter095_masterControl | Master Control Enabled | 474 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Offline | Inverter | inverter095_offline | Offline | 475 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Ramp Up Enabled | Inverter | inverter095_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 476 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Ramp Down Enabled | Inverter | inverter095_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 477 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Real Power Curtailment Flag | Inverter | inverter095_curtailed | Real Power Curtailment Flag | 478 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Following Setpoint | Inverter | inverter095_follwing | Following Setpoint | 479 | 0=False, 1=TRUE | Requested-Available
Counters
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | ROLLOVER VALUE
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV048 | Daggett 3_SUB1_INV048_Start | Inverter | inverter048_start | Start | 0 | LatchOff/LatchOn | Requested-Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Stop | Inverter | inverter048_stop | Stop | 1 | LatchOff/LatchOn | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Start | Inverter | inverter049_start | Start | 2 | LatchOff/LatchOn | Requested-Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Stop | Inverter | inverter049_stop | Stop | 3 | LatchOff/LatchOn | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Start | Inverter | Inverter050_start | Start | 4 | LatchOff/LatchOn | Requested-Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Stop | Inverter | Inverter050_stop | Stop | 5 | LatchOff/LatchOn | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Start | Inverter | Inverter051_start | Start | 6 | LatchOff/LatchOn | Requested-Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Stop | Inverter | Inverter051_stop | Stop | 7 | LatchOff/LatchOn | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Start | Inverter | Inverter052_start | Start | 8 | LatchOff/LatchOn | Requested-Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Stop | Inverter | Inverter052_stop | Stop | 9 | LatchOff/LatchOn | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Start | Inverter | Inverter053_start | Start | 10 | LatchOff/LatchOn | Requested-Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Stop | Inverter | Inverter053_stop | Stop | 11 | LatchOff/LatchOn | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Start | Inverter | Inverter054_start | Start | 12 | LatchOff/LatchOn | Requested-Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Stop | Inverter | Inverter054_stop | Stop | 13 | LatchOff/LatchOn | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Start | Inverter | Inverter055_start | Start | 14 | LatchOff/LatchOn | Requested-Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Stop | Inverter | Inverter055_stop | Stop | 15 | LatchOff/LatchOn | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Start | Inverter | Inverter056_start | Start | 16 | LatchOff/LatchOn | Requested-Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Stop | Inverter | Inverter056_stop | Stop | 17 | LatchOff/LatchOn | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Start | Inverter | Inverter057_start | Start | 18 | LatchOff/LatchOn | Requested-Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Stop | Inverter | Inverter057_stop | Stop | 19 | LatchOff/LatchOn | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Start | Inverter | Inverter058_start | Start | 20 | LatchOff/LatchOn | Requested-Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Stop | Inverter | Inverter058_stop | Stop | 21 | LatchOff/LatchOn | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Start | Inverter | Inverter059_start | Start | 22 | LatchOff/LatchOn | Requested-Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Stop | Inverter | Inverter059_stop | Stop | 23 | LatchOff/LatchOn | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Start | Inverter | Inverter060_start | Start | 24 | LatchOff/LatchOn | Requested-Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Stop | Inverter | Inverter060_stop | Stop | 25 | LatchOff/LatchOn | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Start | Inverter | Inverter061_start | Start | 26 | LatchOff/LatchOn | Requested-Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Stop | Inverter | Inverter061_stop | Stop | 27 | LatchOff/LatchOn | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Start | Inverter | Inverter062_start | Start | 28 | LatchOff/LatchOn | Requested-Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Stop | Inverter | Inverter062_stop | Stop | 29 | LatchOff/LatchOn | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Start | Inverter | Inverter063_start | Start | 30 | LatchOff/LatchOn | Requested-Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Stop | Inverter | Inverter063_stop | Stop | 31 | LatchOff/LatchOn | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Start | Inverter | Inverter064_start | Start | 32 | LatchOff/LatchOn | Requested-Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Stop | Inverter | Inverter064_stop | Stop | 33 | LatchOff/LatchOn | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Start | Inverter | Inverter065_start | Start | 34 | LatchOff/LatchOn | Requested-Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Stop | Inverter | Inverter065_stop | Stop | 35 | LatchOff/LatchOn | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Start | Inverter | Inverter066_start | Start | 36 | LatchOff/LatchOn | Requested-Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Stop | Inverter | Inverter066_stop | Stop | 37 | LatchOff/LatchOn | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Start | Inverter | Inverter067_start | Start | 38 | LatchOff/LatchOn | Requested-Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Stop | Inverter | Inverter067_stop | Stop | 39 | LatchOff/LatchOn | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Start | Inverter | Inverter068_start | Start | 40 | LatchOff/LatchOn | Requested-Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Stop | Inverter | Inverter068_stop | Stop | 41 | LatchOff/LatchOn | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Start | Inverter | Inverter069_start | Start | 42 | LatchOff/LatchOn | Requested-Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Stop | Inverter | Inverter069_stop | Stop | 43 | LatchOff/LatchOn | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Start | Inverter | inverter070_start | Start | 44 | LatchOff/LatchOn | Requested-Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Stop | Inverter | inverter070_stop | Stop | 45 | LatchOff/LatchOn | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Start | Inverter | inverter071_start | Start | 46 | LatchOff/LatchOn | Requested-Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Stop | Inverter | inverter071_stop | Stop | 47 | LatchOff/LatchOn | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Start | Inverter | inverter072_start | Start | 48 | LatchOff/LatchOn | Requested-Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Stop | Inverter | inverter072_stop | Stop | 49 | LatchOff/LatchOn | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Start | Inverter | inverter073_start | Start | 50 | LatchOff/LatchOn | Requested-Available
SUB1 | INV073 | Daggett 3_SUB1_INV073_Stop | Inverter | inverter073_stop | Stop | 51 | LatchOff/LatchOn | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Start | Inverter | inverter074_start | Start | 52 | LatchOff/LatchOn | Requested-Available
SUB1 | INV074 | Daggett 3_SUB1_INV074_Stop | Inverter | inverter074_stop | Stop | 53 | LatchOff/LatchOn | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Start | Inverter | inverter075_start | Start | 54 | LatchOff/LatchOn | Requested-Available
SUB1 | INV075 | Daggett 3_SUB1_INV075_Stop | Inverter | inverter075_stop | Stop | 55 | LatchOff/LatchOn | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Start | Inverter | inverter076_start | Start | 56 | LatchOff/LatchOn | Requested-Available
SUB1 | INV076 | Daggett 3_SUB1_INV076_Stop | Inverter | inverter076_stop | Stop | 57 | LatchOff/LatchOn | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Start | Inverter | inverter077_start | Start | 58 | LatchOff/LatchOn | Requested-Available
SUB1 | INV077 | Daggett 3_SUB1_INV077_Stop | Inverter | inverter077_stop | Stop | 59 | LatchOff/LatchOn | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Start | Inverter | inverter078_start | Start | 60 | LatchOff/LatchOn | Requested-Available
SUB1 | INV078 | Daggett 3_SUB1_INV078_Stop | Inverter | inverter078_stop | Stop | 61 | LatchOff/LatchOn | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Start | Inverter | inverter079_start | Start | 62 | LatchOff/LatchOn | Requested-Available
SUB1 | INV079 | Daggett 3_SUB1_INV079_Stop | Inverter | inverter079_stop | Stop | 63 | LatchOff/LatchOn | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Start | Inverter | inverter080_start | Start | 64 | LatchOff/LatchOn | Requested-Available
SUB1 | INV080 | Daggett 3_SUB1_INV080_Stop | Inverter | inverter080_stop | Stop | 65 | LatchOff/LatchOn | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Start | Inverter | inverter081_start | Start | 66 | LatchOff/LatchOn | Requested-Available
SUB1 | INV081 | Daggett 3_SUB1_INV081_Stop | Inverter | inverter081_stop | Stop | 67 | LatchOff/LatchOn | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Start | Inverter | inverter082_start | Start | 68 | LatchOff/LatchOn | Requested-Available
SUB1 | INV082 | Daggett 3_SUB1_INV082_Stop | Inverter | inverter082_stop | Stop | 69 | LatchOff/LatchOn | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Start | Inverter | inverter083_start | Start | 70 | LatchOff/LatchOn | Requested-Available
SUB1 | INV083 | Daggett 3_SUB1_INV083_Stop | Inverter | inverter083_stop | Stop | 71 | LatchOff/LatchOn | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Start | Inverter | inverter084_start | Start | 72 | LatchOff/LatchOn | Requested-Available
SUB1 | INV084 | Daggett 3_SUB1_INV084_Stop | Inverter | inverter084_stop | Stop | 73 | LatchOff/LatchOn | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Start | Inverter | inverter085_start | Start | 74 | LatchOff/LatchOn | Requested-Available
SUB1 | INV085 | Daggett 3_SUB1_INV085_Stop | Inverter | inverter085_stop | Stop | 75 | LatchOff/LatchOn | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Start | Inverter | inverter086_start | Start | 76 | LatchOff/LatchOn | Requested-Available
SUB1 | INV086 | Daggett 3_SUB1_INV086_Stop | Inverter | inverter086_stop | Stop | 77 | LatchOff/LatchOn | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Start | Inverter | inverter087_start | Start | 78 | LatchOff/LatchOn | Requested-Available
SUB1 | INV087 | Daggett 3_SUB1_INV087_Stop | Inverter | inverter087_stop | Stop | 79 | LatchOff/LatchOn | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Start | Inverter | inverter088_start | Start | 80 | LatchOff/LatchOn | Requested-Available
SUB1 | INV088 | Daggett 3_SUB1_INV088_Stop | Inverter | inverter088_stop | Stop | 81 | LatchOff/LatchOn | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Start | Inverter | inverter089_start | Start | 82 | LatchOff/LatchOn | Requested-Available
SUB1 | INV089 | Daggett 3_SUB1_INV089_Stop | Inverter | inverter089_stop | Stop | 83 | LatchOff/LatchOn | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Start | Inverter | inverter090_start | Start | 84 | LatchOff/LatchOn | Requested-Available
SUB1 | INV090 | Daggett 3_SUB1_INV090_Stop | Inverter | inverter090_stop | Stop | 85 | LatchOff/LatchOn | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Start | Inverter | inverter091_start | Start | 86 | LatchOff/LatchOn | Requested-Available
SUB1 | INV091 | Daggett 3_SUB1_INV091_Stop | Inverter | inverter091_stop | Stop | 87 | LatchOff/LatchOn | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Start | Inverter | inverter092_start | Start | 88 | LatchOff/LatchOn | Requested-Available
SUB1 | INV092 | Daggett 3_SUB1_INV092_Stop | Inverter | inverter092_stop | Stop | 89 | LatchOff/LatchOn | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Start | Inverter | inverter093_start | Start | 90 | LatchOff/LatchOn | Requested-Available
SUB1 | INV093 | Daggett 3_SUB1_INV093_Stop | Inverter | inverter093_stop | Stop | 91 | LatchOff/LatchOn | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Start | Inverter | inverter094_start | Start | 92 | LatchOff/LatchOn | Requested-Available
SUB1 | INV094 | Daggett 3_SUB1_INV094_Stop | Inverter | inverter094_stop | Stop | 93 | LatchOff/LatchOn | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Start | Inverter | inverter095_start | Start | 94 | LatchOff/LatchOn | Requested-Available
SUB1 | INV095 | Daggett 3_SUB1_INV095_Stop | Inverter | inverter095_stop | Stop | 95 | LatchOff/LatchOn | Requested-Available