## Sheet1 (hidden)
Requested, Available
Requested, Not applicable
Requested, Not Available
Not Requested, Available

## 1
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | 10.75.32.2 |  | DNP Server | 10.75.32.2
DNP Server Port# | 20001 |  | DNP Server Port# | 20010 (PROD); 20011 (QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 1 |  | RTAC DNP Server address | 1
| Data Type | DNP Event Class | Event Obj/Var | Static Obj/Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30/5
Digitals | Status with Flags | 1 | 2/2 | 1/2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20/1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband of 0.01 for all points except 0.001 for Frequency and Power Factor
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19971 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 0 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 1 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 2 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 3 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 4 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 5 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 6 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 7 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 8 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 9 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 10 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 11 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 12 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 13 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 14 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit A MW Setpoint Feedback | 15 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 16 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 17 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 18 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 19 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 20 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit A MW Setpoint Feedback | 21 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 22 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 23 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 24 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 25 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 26 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ACK Alarms | PPC |  | ACK Alarms |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Active Power Charge Limit | PPC | PPC.bessStatus.pLimitChg_kw | BESS Site Charge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Active Power Discharge Limit | PPC | PPC.bessStatus.pLimitDischg_kw | BESS Site Discharge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Available Energy | PPC |  | Available Energy |  | MWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Average SOC | PPC | PPC.bessStatus.socAvg_percent | BESS Site Average SOC |  |  | Requested-Not Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Batteries Online | PPC |  | Batteries Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Block 1 Status | PPC |  | Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Block 2 Status | PPC |  | Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Charge Capacity | PPC |  | Charge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Communications Status | PPC |  | Communications Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS A Phase Current | PPC |  | A Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS B Phase Current | PPC |  | B Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS C Phase Current | PPC |  | C Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Current-DC | PPC |  | Current-DC |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Discharge Capacity | PPC |  | Discharge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS E-Stop Status | PPC |  | E-Stop Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Frequency | PPC | PPC.bessStatus.f3_hz | BESS AC Frequency Measured at Plant Interconnect |  | Hz | Requested-Not Available | 56 | 64 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS GBS Critical Alarm | PPC |  | GBS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS GBS Warning Alarm | PPC |  | GBS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Grid Connection Status | PPC |  | Grid Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Grid Status | PPC |  | Grid Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Gross System Energy | PPC |  | Gross System Energy |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Group Mode | PPC |  | Group Mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Heartbeat Out | PPC |  | Heartbeat Out |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Island Frequency | PPC |  | Island Frequency |  | Hz | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Island Indicator | PPC |  | Island Indicator |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Island Reactive Demand | PPC |  | Island Reactive Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Island Real Demand | PPC |  | Island Real Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Island Voltage | PPC |  | Island Voltage |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Measured System Load | PPC |  | Measured System Load |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Number of Zones | PPC |  | Number of Zones |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Operating mode | PPC |  | Operating mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS PCS Critical Alarm | PPC |  | PCS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS PCS Warning Alarm | PPC |  | PCS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Peak Shaving Discharge Threshold | PPC |  | Peak Shaving Discharge Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Peak Shaving Enabled | PPC |  | Peak Shaving Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Peak Shaving Threshold | PPC |  | Peak Shaving Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Power Block 1 Status | PPC |  | Power Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Power Block 2 Status | PPC |  | Power Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Power Block Status | PPC |  | Power Block Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Power Factor | PPC |  | Power Factor |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Q Charge Limit | PPC |  | Q Charge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Q Discharge Limit | PPC |  | Q Discharge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Control Mode Running | PPC |  | Reactive Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Capacity | PPC |  | Reactive Power Capacity |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Charge Limit | PPC |  | Reactive Power Charge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Commanded | PPC |  | Reactive Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Demand | PPC |  | Reactive Power Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Discharge Limit | PPC |  | Reactive Power Discharge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Dispatch Enabled | PPC |  | Reactive Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Reactive Power Output | PPC |  | Reactive Power Output |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Control Mode Running | PPC |  | Real Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power | PPC |  | Real Power |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Capacity | PPC |  | Real Power Capacity |  | kW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Commanded | PPC |  | Real Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Demand | PPC |  | Real Power Demand |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Dispatch Enabled | PPC |  | Real Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Output | PPC |  | Real Power Output |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Real Power Priority | PPC |  | Real Power Priority |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Temperature-Amb1 | PPC |  | Temperature-Amb1 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Temperature-Amb2 | PPC |  | Temperature-Amb2 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Temperature-Avg | PPC |  | Temperature-Avg |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Voltage A-B | PPC |  | Voltage A-B |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Voltage B-C | PPC |  | Voltage B-C |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Voltage C-A | PPC |  | Voltage C-A |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Voltage-DC | PPC |  | Voltage-DC |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Zones Online | PPC |  | Zones Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Voltage-DC | PPC | PPC.bessStatus.ess01_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 27 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Real Power-DC | PPC | PPC.bessStatus.ess01_p3_kw | BESS Site ESS Unit AC Real Power | 28 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Current-DC | PPC | PPC.bessStatus.ess01_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 29 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 State Of Charge | PPC | PPC.bessStatus.ess01_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 30 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Temperature-Avg | PPC | PPC.bessStatus.ess01_temp_degreeC | BESS Site BOP Temperature | 31 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Humidity | PPC | PPC.bessStatus.ess01_humidity_percent | BESS Site BOP Humidity | 32 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Reactive Power | PPC | PPC.bessStatus.ess01_q3_kvar | BESS Site ESS Unit AC Reactive Power | 33 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Effective SOC | PPC | PPC.bessStatus.ess01_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 34 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Charge Power Limit | PPC | PPC.bessStatus.ess01_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 35 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Discharge Power Lim | PPC | PPC.bessStatus.ess01_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 36 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Chargable Energy | PPC | PPC.bessStatus.ess01_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 37 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Dischargable Energy | PPC | PPC.bessStatus.ess01_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 38 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Op Code Indicator | PPC | PPC.bessStatus.ess01_operationCode | BESS Site ESS Unit Operation Code Indicator | 39 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Num Of Strings OL | PPC | PPC.bessStatus.ess01_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 40 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Voltage-DC | PPC | PPC.bessStatus.ESS02_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 41 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Real Power-DC | PPC | PPC.bessStatus.ESS02_p3_kw | BESS Site ESS Unit AC Real Power | 42 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Current-DC | PPC | PPC.bessStatus.ESS02_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 43 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 State Of Charge | PPC | PPC.bessStatus.ESS02_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 44 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Temperature-Avg | PPC | PPC.bessStatus.ESS02_temp_degreeC | BESS Site BOP Temperature | 45 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Humidity | PPC | PPC.bessStatus.ESS02_humidity_percent | BESS Site BOP Humidity | 46 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Reactive Power | PPC | PPC.bessStatus.ESS02_q3_kvar | BESS Site ESS Unit AC Reactive Power | 47 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Effective SOC | PPC | PPC.bessStatus.ESS02_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 48 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Charge Power Limit | PPC | PPC.bessStatus.ESS02_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 49 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Discharge Power Lim | PPC | PPC.bessStatus.ESS02_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 50 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Chargable Energy | PPC | PPC.bessStatus.ESS02_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 51 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Dischargable Energy | PPC | PPC.bessStatus.ESS02_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 52 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Op Code Indicator | PPC | PPC.bessStatus.ESS02_operationCode | BESS Site ESS Unit Operation Code Indicator | 53 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Num Of Strings OL | PPC | PPC.bessStatus.ESS02_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 54 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Voltage-DC | PPC | PPC.bessStatus.ESS03_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 55 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Real Power-DC | PPC | PPC.bessStatus.ESS03_p3_kw | BESS Site ESS Unit AC Real Power | 56 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Current-DC | PPC | PPC.bessStatus.ESS03_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 57 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 State Of Charge | PPC | PPC.bessStatus.ESS03_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 58 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Temperature-Avg | PPC | PPC.bessStatus.ESS03_temp_degreeC | BESS Site BOP Temperature | 59 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Humidity | PPC | PPC.bessStatus.ESS03_humidity_percent | BESS Site BOP Humidity | 60 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Reactive Power | PPC | PPC.bessStatus.ESS03_q3_kvar | BESS Site ESS Unit AC Reactive Power | 61 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Effective SOC | PPC | PPC.bessStatus.ESS03_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 62 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Charge Power Limit | PPC | PPC.bessStatus.ESS03_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 63 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Discharge Power Lim | PPC | PPC.bessStatus.ESS03_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 64 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Chargable Energy | PPC | PPC.bessStatus.ESS03_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 65 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Dischargable Energy | PPC | PPC.bessStatus.ESS03_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 66 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Op Code Indicator | PPC | PPC.bessStatus.ESS03_operationCode | BESS Site ESS Unit Operation Code Indicator | 67 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Num Of Strings OL | PPC | PPC.bessStatus.ESS03_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 68 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Voltage-DC | PPC | PPC.bessStatus.ESS04_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 69 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Real Power-DC | PPC | PPC.bessStatus.ESS04_p3_kw | BESS Site ESS Unit AC Real Power | 70 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Current-DC | PPC | PPC.bessStatus.ESS04_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 71 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 State Of Charge | PPC | PPC.bessStatus.ESS04_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 72 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Temperature-Avg | PPC | PPC.bessStatus.ESS04_temp_degreeC | BESS Site BOP Temperature | 73 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Humidity | PPC | PPC.bessStatus.ESS04_humidity_percent | BESS Site BOP Humidity | 74 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Reactive Power | PPC | PPC.bessStatus.ESS04_q3_kvar | BESS Site ESS Unit AC Reactive Power | 75 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Effective SOC | PPC | PPC.bessStatus.ESS04_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 76 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Charge Power Limit | PPC | PPC.bessStatus.ESS04_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 77 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Discharge Power Lim | PPC | PPC.bessStatus.ESS04_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 78 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Chargable Energy | PPC | PPC.bessStatus.ESS04_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 79 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Dischargable Energy | PPC | PPC.bessStatus.ESS04_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 80 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Op Code Indicator | PPC | PPC.bessStatus.ESS04_operationCode | BESS Site ESS Unit Operation Code Indicator | 81 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Num Of Strings OL | PPC | PPC.bessStatus.ESS04_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 82 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Voltage-DC | PPC | PPC.bessStatus.ESS05_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 83 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Real Power-DC | PPC | PPC.bessStatus.ESS05_p3_kw | BESS Site ESS Unit AC Real Power | 84 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Current-DC | PPC | PPC.bessStatus.ESS05_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 85 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 State Of Charge | PPC | PPC.bessStatus.ESS05_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 86 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Temperature-Avg | PPC | PPC.bessStatus.ESS05_temp_degreeC | BESS Site BOP Temperature | 87 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Humidity | PPC | PPC.bessStatus.ESS05_humidity_percent | BESS Site BOP Humidity | 88 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Reactive Power | PPC | PPC.bessStatus.ESS05_q3_kvar | BESS Site ESS Unit AC Reactive Power | 89 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Effective SOC | PPC | PPC.bessStatus.ESS05_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 90 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Charge Power Limit | PPC | PPC.bessStatus.ESS05_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 91 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Discharge Power Lim | PPC | PPC.bessStatus.ESS05_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 92 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Chargable Energy | PPC | PPC.bessStatus.ESS05_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 93 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Dischargable Energy | PPC | PPC.bessStatus.ESS05_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 94 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Op Code Indicator | PPC | PPC.bessStatus.ESS05_operationCode | BESS Site ESS Unit Operation Code Indicator | 95 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Num Of Strings OL | PPC | PPC.bessStatus.ESS05_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 96 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Voltage-DC | PPC | PPC.bessStatus.ESS06_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 97 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Real Power-DC | PPC | PPC.bessStatus.ESS06_p3_kw | BESS Site ESS Unit AC Real Power | 98 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Current-DC | PPC | PPC.bessStatus.ESS06_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 99 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 State Of Charge | PPC | PPC.bessStatus.ESS06_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 100 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Temperature-Avg | PPC | PPC.bessStatus.ESS06_temp_degreeC | BESS Site BOP Temperature | 101 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Humidity | PPC | PPC.bessStatus.ESS06_humidity_percent | BESS Site BOP Humidity | 102 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Reactive Power | PPC | PPC.bessStatus.ESS06_q3_kvar | BESS Site ESS Unit AC Reactive Power | 103 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Effective SOC | PPC | PPC.bessStatus.ESS06_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 104 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Charge Power Limit | PPC | PPC.bessStatus.ESS06_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 105 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Discharge Power Lim | PPC | PPC.bessStatus.ESS06_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 106 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Chargable Energy | PPC | PPC.bessStatus.ESS06_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 107 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Dischargable Energy | PPC | PPC.bessStatus.ESS06_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 108 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Op Code Indicator | PPC | PPC.bessStatus.ESS06_operationCode | BESS Site ESS Unit Operation Code Indicator | 109 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Num Of Strings OL | PPC | PPC.bessStatus.ESS06_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 110 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Voltage-DC | PPC | PPC.bessStatus.ESS07_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 111 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Real Power-DC | PPC | PPC.bessStatus.ESS07_p3_kw | BESS Site ESS Unit AC Real Power | 112 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Current-DC | PPC | PPC.bessStatus.ESS07_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 113 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 State Of Charge | PPC | PPC.bessStatus.ESS07_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 114 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Temperature-Avg | PPC | PPC.bessStatus.ESS07_temp_degreeC | BESS Site BOP Temperature | 115 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Humidity | PPC | PPC.bessStatus.ESS07_humidity_percent | BESS Site BOP Humidity | 116 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Reactive Power | PPC | PPC.bessStatus.ESS07_q3_kvar | BESS Site ESS Unit AC Reactive Power | 117 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Effective SOC | PPC | PPC.bessStatus.ESS07_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 118 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Charge Power Limit | PPC | PPC.bessStatus.ESS07_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 119 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Discharge Power Lim | PPC | PPC.bessStatus.ESS07_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 120 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Chargable Energy | PPC | PPC.bessStatus.ESS07_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 121 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Dischargable Energy | PPC | PPC.bessStatus.ESS07_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 122 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Op Code Indicator | PPC | PPC.bessStatus.ESS07_operationCode | BESS Site ESS Unit Operation Code Indicator | 123 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Num Of Strings OL | PPC | PPC.bessStatus.ESS07_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 124 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Voltage-DC | PPC | PPC.bessStatus.ESS08_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 125 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Real Power-DC | PPC | PPC.bessStatus.ESS08_p3_kw | BESS Site ESS Unit AC Real Power | 126 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Current-DC | PPC | PPC.bessStatus.ESS08_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 127 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 State Of Charge | PPC | PPC.bessStatus.ESS08_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 128 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Temperature-Avg | PPC | PPC.bessStatus.ESS08_temp_degreeC | BESS Site BOP Temperature | 129 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Humidity | PPC | PPC.bessStatus.ESS08_humidity_percent | BESS Site BOP Humidity | 130 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Reactive Power | PPC | PPC.bessStatus.ESS08_q3_kvar | BESS Site ESS Unit AC Reactive Power | 131 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Effective SOC | PPC | PPC.bessStatus.ESS08_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 132 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Charge Power Limit | PPC | PPC.bessStatus.ESS08_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 133 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Discharge Power Lim | PPC | PPC.bessStatus.ESS08_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 134 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Chargable Energy | PPC | PPC.bessStatus.ESS08_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 135 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Dischargable Energy | PPC | PPC.bessStatus.ESS08_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 136 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Op Code Indicator | PPC | PPC.bessStatus.ESS08_operationCode | BESS Site ESS Unit Operation Code Indicator | 137 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Num Of Strings OL | PPC | PPC.bessStatus.ESS08_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 138 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Voltage-DC | PPC | PPC.bessStatus.ESS09_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 139 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Real Power-DC | PPC | PPC.bessStatus.ESS09_p3_kw | BESS Site ESS Unit AC Real Power | 140 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Current-DC | PPC | PPC.bessStatus.ESS09_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 141 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 State Of Charge | PPC | PPC.bessStatus.ESS09_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 142 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Temperature-Avg | PPC | PPC.bessStatus.ESS09_temp_degreeC | BESS Site BOP Temperature | 143 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Humidity | PPC | PPC.bessStatus.ESS09_humidity_percent | BESS Site BOP Humidity | 144 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Reactive Power | PPC | PPC.bessStatus.ESS09_q3_kvar | BESS Site ESS Unit AC Reactive Power | 145 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Effective SOC | PPC | PPC.bessStatus.ESS09_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 146 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Charge Power Limit | PPC | PPC.bessStatus.ESS09_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 147 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Discharge Power Lim | PPC | PPC.bessStatus.ESS09_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 148 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Chargable Energy | PPC | PPC.bessStatus.ESS09_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 149 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Dischargable Energy | PPC | PPC.bessStatus.ESS09_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 150 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Op Code Indicator | PPC | PPC.bessStatus.ESS09_operationCode | BESS Site ESS Unit Operation Code Indicator | 151 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Num Of Strings OL | PPC | PPC.bessStatus.ESS09_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 152 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Voltage-DC | PPC | PPC.bessStatus.ESS10_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 153 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Real Power-DC | PPC | PPC.bessStatus.ESS10_p3_kw | BESS Site ESS Unit AC Real Power | 154 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Current-DC | PPC | PPC.bessStatus.ESS10_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 155 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 State Of Charge | PPC | PPC.bessStatus.ESS10_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 156 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Temperature-Avg | PPC | PPC.bessStatus.ESS10_temp_degreeC | BESS Site BOP Temperature | 157 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Humidity | PPC | PPC.bessStatus.ESS10_humidity_percent | BESS Site BOP Humidity | 158 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Reactive Power | PPC | PPC.bessStatus.ESS10_q3_kvar | BESS Site ESS Unit AC Reactive Power | 159 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Effective SOC | PPC | PPC.bessStatus.ESS10_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 160 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Charge Power Limit | PPC | PPC.bessStatus.ESS10_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 161 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Discharge Power Lim | PPC | PPC.bessStatus.ESS10_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 162 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Chargable Energy | PPC | PPC.bessStatus.ESS10_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 163 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Dischargable Energy | PPC | PPC.bessStatus.ESS10_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 164 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Op Code Indicator | PPC | PPC.bessStatus.ESS10_operationCode | BESS Site ESS Unit Operation Code Indicator | 165 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Num Of Strings OL | PPC | PPC.bessStatus.ESS10_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 166 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Voltage-DC | PPC | PPC.bessStatus.ESS11_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 167 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Real Power-DC | PPC | PPC.bessStatus.ESS11_p3_kw | BESS Site ESS Unit AC Real Power | 168 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Current-DC | PPC | PPC.bessStatus.ESS11_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 169 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 State Of Charge | PPC | PPC.bessStatus.ESS11_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 170 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Temperature-Avg | PPC | PPC.bessStatus.ESS11_temp_degreeC | BESS Site BOP Temperature | 171 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Humidity | PPC | PPC.bessStatus.ESS11_humidity_percent | BESS Site BOP Humidity | 172 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Reactive Power | PPC | PPC.bessStatus.ESS11_q3_kvar | BESS Site ESS Unit AC Reactive Power | 173 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Effective SOC | PPC | PPC.bessStatus.ESS11_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 174 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Charge Power Limit | PPC | PPC.bessStatus.ESS11_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 175 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Discharge Power Lim | PPC | PPC.bessStatus.ESS11_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 176 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Chargable Energy | PPC | PPC.bessStatus.ESS11_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 177 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Dischargable Energy | PPC | PPC.bessStatus.ESS11_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 178 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Op Code Indicator | PPC | PPC.bessStatus.ESS11_operationCode | BESS Site ESS Unit Operation Code Indicator | 179 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Num Of Strings OL | PPC | PPC.bessStatus.ESS11_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 180 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Voltage-DC | PPC | PPC.bessStatus.ESS12_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 181 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Real Power-DC | PPC | PPC.bessStatus.ESS12_p3_kw | BESS Site ESS Unit AC Real Power | 182 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Current-DC | PPC | PPC.bessStatus.ESS12_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 183 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 State Of Charge | PPC | PPC.bessStatus.ESS12_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 184 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Temperature-Avg | PPC | PPC.bessStatus.ESS12_temp_degreeC | BESS Site BOP Temperature | 185 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Humidity | PPC | PPC.bessStatus.ESS12_humidity_percent | BESS Site BOP Humidity | 186 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Reactive Power | PPC | PPC.bessStatus.ESS12_q3_kvar | BESS Site ESS Unit AC Reactive Power | 187 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Effective SOC | PPC | PPC.bessStatus.ESS12_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 188 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Charge Power Limit | PPC | PPC.bessStatus.ESS12_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 189 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Discharge Power Lim | PPC | PPC.bessStatus.ESS12_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 190 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Chargable Energy | PPC | PPC.bessStatus.ESS12_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 191 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Dischargable Energy | PPC | PPC.bessStatus.ESS12_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 192 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Op Code Indicator | PPC | PPC.bessStatus.ESS12_operationCode | BESS Site ESS Unit Operation Code Indicator | 193 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Num Of Strings OL | PPC | PPC.bessStatus.ESS12_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 194 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Voltage-DC | PPC | PPC.bessStatus.ESS13_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 195 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Real Power-DC | PPC | PPC.bessStatus.ESS13_p3_kw | BESS Site ESS Unit AC Real Power | 196 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Current-DC | PPC | PPC.bessStatus.ESS13_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 197 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 State Of Charge | PPC | PPC.bessStatus.ESS13_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 198 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Temperature-Avg | PPC | PPC.bessStatus.ESS13_temp_degreeC | BESS Site BOP Temperature | 199 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Humidity | PPC | PPC.bessStatus.ESS13_humidity_percent | BESS Site BOP Humidity | 200 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Reactive Power | PPC | PPC.bessStatus.ESS13_q3_kvar | BESS Site ESS Unit AC Reactive Power | 201 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Effective SOC | PPC | PPC.bessStatus.ESS13_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 202 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Charge Power Limit | PPC | PPC.bessStatus.ESS13_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 203 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Discharge Power Lim | PPC | PPC.bessStatus.ESS13_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 204 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Chargable Energy | PPC | PPC.bessStatus.ESS13_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 205 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Dischargable Energy | PPC | PPC.bessStatus.ESS13_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 206 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Op Code Indicator | PPC | PPC.bessStatus.ESS13_operationCode | BESS Site ESS Unit Operation Code Indicator | 207 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Num Of Strings OL | PPC | PPC.bessStatus.ESS13_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 208 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Voltage-DC | PPC | PPC.bessStatus.ESS14_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 209 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Real Power-DC | PPC | PPC.bessStatus.ESS14_p3_kw | BESS Site ESS Unit AC Real Power | 210 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Current-DC | PPC | PPC.bessStatus.ESS14_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 211 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 State Of Charge | PPC | PPC.bessStatus.ESS14_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 212 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Temperature-Avg | PPC | PPC.bessStatus.ESS14_temp_degreeC | BESS Site BOP Temperature | 213 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Humidity | PPC | PPC.bessStatus.ESS14_humidity_percent | BESS Site BOP Humidity | 214 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Reactive Power | PPC | PPC.bessStatus.ESS14_q3_kvar | BESS Site ESS Unit AC Reactive Power | 215 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Effective SOC | PPC | PPC.bessStatus.ESS14_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 216 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Charge Power Limit | PPC | PPC.bessStatus.ESS14_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 217 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Discharge Power Lim | PPC | PPC.bessStatus.ESS14_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 218 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Chargable Energy | PPC | PPC.bessStatus.ESS14_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 219 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Dischargable Energy | PPC | PPC.bessStatus.ESS14_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 220 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Op Code Indicator | PPC | PPC.bessStatus.ESS14_operationCode | BESS Site ESS Unit Operation Code Indicator | 221 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Num Of Strings OL | PPC | PPC.bessStatus.ESS14_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 222 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Voltage-DC | PPC | PPC.bessStatus.ESS15_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 223 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Real Power-DC | PPC | PPC.bessStatus.ESS15_p3_kw | BESS Site ESS Unit AC Real Power | 224 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Current-DC | PPC | PPC.bessStatus.ESS15_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 225 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 State Of Charge | PPC | PPC.bessStatus.ESS15_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 226 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Temperature-Avg | PPC | PPC.bessStatus.ESS15_temp_degreeC | BESS Site BOP Temperature | 227 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Humidity | PPC | PPC.bessStatus.ESS15_humidity_percent | BESS Site BOP Humidity | 228 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Reactive Power | PPC | PPC.bessStatus.ESS15_q3_kvar | BESS Site ESS Unit AC Reactive Power | 229 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Effective SOC | PPC | PPC.bessStatus.ESS15_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 230 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Charge Power Limit | PPC | PPC.bessStatus.ESS15_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 231 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Discharge Power Lim | PPC | PPC.bessStatus.ESS15_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 232 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Chargable Energy | PPC | PPC.bessStatus.ESS15_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 233 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Dischargable Energy | PPC | PPC.bessStatus.ESS15_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 234 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Op Code Indicator | PPC | PPC.bessStatus.ESS15_operationCode | BESS Site ESS Unit Operation Code Indicator | 235 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Num Of Strings OL | PPC | PPC.bessStatus.ESS15_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 236 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Voltage-DC | PPC | PPC.bessStatus.ESS16_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 237 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Real Power-DC | PPC | PPC.bessStatus.ESS16_p3_kw | BESS Site ESS Unit AC Real Power | 238 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Current-DC | PPC | PPC.bessStatus.ESS16_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 239 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 State Of Charge | PPC | PPC.bessStatus.ESS16_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 240 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Temperature-Avg | PPC | PPC.bessStatus.ESS16_temp_degreeC | BESS Site BOP Temperature | 241 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Humidity | PPC | PPC.bessStatus.ESS16_humidity_percent | BESS Site BOP Humidity | 242 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Reactive Power | PPC | PPC.bessStatus.ESS16_q3_kvar | BESS Site ESS Unit AC Reactive Power | 243 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Effective SOC | PPC | PPC.bessStatus.ESS16_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 244 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Charge Power Limit | PPC | PPC.bessStatus.ESS16_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 245 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Discharge Power Lim | PPC | PPC.bessStatus.ESS16_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 246 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Chargable Energy | PPC | PPC.bessStatus.ESS16_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 247 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Dischargable Energy | PPC | PPC.bessStatus.ESS16_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 248 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Op Code Indicator | PPC | PPC.bessStatus.ESS16_operationCode | BESS Site ESS Unit Operation Code Indicator | 249 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Num Of Strings OL | PPC | PPC.bessStatus.ESS16_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 250 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Voltage-DC | PPC | PPC.bessStatus.ESS17_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 251 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Real Power-DC | PPC | PPC.bessStatus.ESS17_p3_kw | BESS Site ESS Unit AC Real Power | 252 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Current-DC | PPC | PPC.bessStatus.ESS17_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 253 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 State Of Charge | PPC | PPC.bessStatus.ESS17_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 254 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Temperature-Avg | PPC | PPC.bessStatus.ESS17_temp_degreeC | BESS Site BOP Temperature | 255 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Humidity | PPC | PPC.bessStatus.ESS17_humidity_percent | BESS Site BOP Humidity | 256 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Reactive Power | PPC | PPC.bessStatus.ESS17_q3_kvar | BESS Site ESS Unit AC Reactive Power | 257 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Effective SOC | PPC | PPC.bessStatus.ESS17_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 258 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Charge Power Limit | PPC | PPC.bessStatus.ESS17_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 259 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Discharge Power Lim | PPC | PPC.bessStatus.ESS17_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 260 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Chargable Energy | PPC | PPC.bessStatus.ESS17_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 261 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Dischargable Energy | PPC | PPC.bessStatus.ESS17_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 262 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Op Code Indicator | PPC | PPC.bessStatus.ESS17_operationCode | BESS Site ESS Unit Operation Code Indicator | 263 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Num Of Strings OL | PPC | PPC.bessStatus.ESS17_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 264 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Voltage-DC | PPC | PPC.bessStatus.ESS18_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 265 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Real Power-DC | PPC | PPC.bessStatus.ESS18_p3_kw | BESS Site ESS Unit AC Real Power | 266 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Current-DC | PPC | PPC.bessStatus.ESS18_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 267 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 State Of Charge | PPC | PPC.bessStatus.ESS18_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 268 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Temperature-Avg | PPC | PPC.bessStatus.ESS18_temp_degreeC | BESS Site BOP Temperature | 269 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Humidity | PPC | PPC.bessStatus.ESS18_humidity_percent | BESS Site BOP Humidity | 270 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Reactive Power | PPC | PPC.bessStatus.ESS18_q3_kvar | BESS Site ESS Unit AC Reactive Power | 271 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Effective SOC | PPC | PPC.bessStatus.ESS18_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 272 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Charge Power Limit | PPC | PPC.bessStatus.ESS18_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 273 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Discharge Power Lim | PPC | PPC.bessStatus.ESS18_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 274 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Chargable Energy | PPC | PPC.bessStatus.ESS18_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 275 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Dischargable Energy | PPC | PPC.bessStatus.ESS18_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 276 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Op Code Indicator | PPC | PPC.bessStatus.ESS18_operationCode | BESS Site ESS Unit Operation Code Indicator | 277 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Num Of Strings OL | PPC | PPC.bessStatus.ESS18_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 278 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Voltage-DC | PPC | PPC.bessStatus.ESS19_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 279 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Real Power-DC | PPC | PPC.bessStatus.ESS19_p3_kw | BESS Site ESS Unit AC Real Power | 280 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Current-DC | PPC | PPC.bessStatus.ESS19_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 281 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 State Of Charge | PPC | PPC.bessStatus.ESS19_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 282 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Temperature-Avg | PPC | PPC.bessStatus.ESS19_temp_degreeC | BESS Site BOP Temperature | 283 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Humidity | PPC | PPC.bessStatus.ESS19_humidity_percent | BESS Site BOP Humidity | 284 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Reactive Power | PPC | PPC.bessStatus.ESS19_q3_kvar | BESS Site ESS Unit AC Reactive Power | 285 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Effective SOC | PPC | PPC.bessStatus.ESS19_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 286 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Charge Power Limit | PPC | PPC.bessStatus.ESS19_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 287 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Discharge Power Lim | PPC | PPC.bessStatus.ESS19_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 288 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Chargable Energy | PPC | PPC.bessStatus.ESS19_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 289 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Dischargable Energy | PPC | PPC.bessStatus.ESS19_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 290 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Op Code Indicator | PPC | PPC.bessStatus.ESS19_operationCode | BESS Site ESS Unit Operation Code Indicator | 291 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Num Of Strings OL | PPC | PPC.bessStatus.ESS19_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 292 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Voltage-DC | PPC | PPC.bessStatus.ESS20_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 293 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Real Power-DC | PPC | PPC.bessStatus.ESS20_p3_kw | BESS Site ESS Unit AC Real Power | 294 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Current-DC | PPC | PPC.bessStatus.ESS20_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 295 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 State Of Charge | PPC | PPC.bessStatus.ESS20_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 296 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Temperature-Avg | PPC | PPC.bessStatus.ESS20_temp_degreeC | BESS Site BOP Temperature | 297 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Humidity | PPC | PPC.bessStatus.ESS20_humidity_percent | BESS Site BOP Humidity | 298 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Reactive Power | PPC | PPC.bessStatus.ESS20_q3_kvar | BESS Site ESS Unit AC Reactive Power | 299 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Effective SOC | PPC | PPC.bessStatus.ESS20_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 300 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Charge Power Limit | PPC | PPC.bessStatus.ESS20_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 301 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Discharge Power Lim | PPC | PPC.bessStatus.ESS20_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 302 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Chargable Energy | PPC | PPC.bessStatus.ESS20_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 303 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Dischargable Energy | PPC | PPC.bessStatus.ESS20_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 304 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Op Code Indicator | PPC | PPC.bessStatus.ESS20_operationCode | BESS Site ESS Unit Operation Code Indicator | 305 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Num Of Strings OL | PPC | PPC.bessStatus.ESS20_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 306 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19975 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 307 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 308 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 309 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 310 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 311 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 312 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 313 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 314 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 315 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 316 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 317 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 318 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 319 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 320 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 321 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit CD MW Setpoint Feedback | 322 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 323 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 324 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 325 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 326 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 327 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit CD MW Setpoint Feedback | 328 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 329 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 330 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 331 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 332 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 333 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ACK Alarms | PPC |  | ACK Alarms |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Active Power Charge Limit | PPC | PPC.bessStatus.pLimitChg_kw | BESS Site Charge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Active Power Discharge Limit | PPC | PPC.bessStatus.pLimitDischg_kw | BESS Site Discharge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Available Energy | PPC |  | Available Energy |  | MWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Average SOC | PPC | PPC.bessStatus.socAvg_percent | BESS Site Average SOC |  |  | Requested-Not Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Batteries Online | PPC |  | Batteries Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Block 1 Status | PPC |  | Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Block 2 Status | PPC |  | Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Charge Capacity | PPC |  | Charge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Communications Status | PPC |  | Communications Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS A Phase Current | PPC |  | A Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS B Phase Current | PPC |  | B Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS C Phase Current | PPC |  | C Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Current-DC | PPC |  | Current-DC |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Discharge Capacity | PPC |  | Discharge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS E-Stop Status | PPC |  | E-Stop Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Frequency | PPC | PPC.bessStatus.f3_hz | BESS AC Frequency Measured at Plant Interconnect |  | Hz | Requested-Not Available | 56 | 64 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS GBS Critical Alarm | PPC |  | GBS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS GBS Warning Alarm | PPC |  | GBS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Grid Connection Status | PPC |  | Grid Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Grid Status | PPC |  | Grid Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Gross System Energy | PPC |  | Gross System Energy |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Group Mode | PPC |  | Group Mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Heartbeat Out | PPC |  | Heartbeat Out |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Island Frequency | PPC |  | Island Frequency |  | Hz | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Island Indicator | PPC |  | Island Indicator |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Island Reactive Demand | PPC |  | Island Reactive Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Island Real Demand | PPC |  | Island Real Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Island Voltage | PPC |  | Island Voltage |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Measured System Load | PPC |  | Measured System Load |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Number of Zones | PPC |  | Number of Zones |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Operating mode | PPC |  | Operating mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS PCS Critical Alarm | PPC |  | PCS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS PCS Warning Alarm | PPC |  | PCS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Peak Shaving Discharge Threshold | PPC |  | Peak Shaving Discharge Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Peak Shaving Enabled | PPC |  | Peak Shaving Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Peak Shaving Threshold | PPC |  | Peak Shaving Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Power Block 1 Status | PPC |  | Power Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Power Block 2 Status | PPC |  | Power Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Power Block Status | PPC |  | Power Block Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Power Factor | PPC |  | Power Factor |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Q Charge Limit | PPC |  | Q Charge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Q Discharge Limit | PPC |  | Q Discharge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Control Mode Running | PPC |  | Reactive Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Capacity | PPC |  | Reactive Power Capacity |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Charge Limit | PPC |  | Reactive Power Charge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Commanded | PPC |  | Reactive Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Demand | PPC |  | Reactive Power Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Discharge Limit | PPC |  | Reactive Power Discharge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Dispatch Enabled | PPC |  | Reactive Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Reactive Power Output | PPC |  | Reactive Power Output |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Control Mode Running | PPC |  | Real Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power | PPC |  | Real Power |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Capacity | PPC |  | Real Power Capacity |  | kW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Commanded | PPC |  | Real Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Demand | PPC |  | Real Power Demand |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Dispatch Enabled | PPC |  | Real Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Output | PPC |  | Real Power Output |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Real Power Priority | PPC |  | Real Power Priority |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Temperature-Amb1 | PPC |  | Temperature-Amb1 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Temperature-Amb2 | PPC |  | Temperature-Amb2 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Temperature-Avg | PPC |  | Temperature-Avg |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Voltage A-B | PPC |  | Voltage A-B |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Voltage B-C | PPC |  | Voltage B-C |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Voltage C-A | PPC |  | Voltage C-A |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Voltage-DC | PPC |  | Voltage-DC |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Zones Online | PPC |  | Zones Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Voltage-DC | PPC | PPC.bessStatus.ess01_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 334 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Real Power-DC | PPC | PPC.bessStatus.ess01_p3_kw | BESS Site ESS Unit AC Real Power | 335 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Current-DC | PPC | PPC.bessStatus.ess01_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 336 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 State Of Charge | PPC | PPC.bessStatus.ess01_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 337 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Temperature-Avg | PPC | PPC.bessStatus.ess01_temp_degreeC | BESS Site BOP Temperature | 338 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Humidity | PPC | PPC.bessStatus.ess01_humidity_percent | BESS Site BOP Humidity | 339 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Reactive Power | PPC | PPC.bessStatus.ess01_q3_kvar | BESS Site ESS Unit AC Reactive Power | 340 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Effective SOC | PPC | PPC.bessStatus.ess01_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 341 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Charge Power Limit | PPC | PPC.bessStatus.ess01_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 342 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Discharge Power Lim | PPC | PPC.bessStatus.ess01_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 343 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Chargable Energy | PPC | PPC.bessStatus.ess01_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 344 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Dischargable Energy | PPC | PPC.bessStatus.ess01_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 345 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Op Code Indicator | PPC | PPC.bessStatus.ess01_operationCode | BESS Site ESS Unit Operation Code Indicator | 346 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Num Of Strings OL | PPC | PPC.bessStatus.ess01_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 347 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Voltage-DC | PPC | PPC.bessStatus.ESS02_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 348 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Real Power-DC | PPC | PPC.bessStatus.ESS02_p3_kw | BESS Site ESS Unit AC Real Power | 349 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Current-DC | PPC | PPC.bessStatus.ESS02_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 350 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 State Of Charge | PPC | PPC.bessStatus.ESS02_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 351 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Temperature-Avg | PPC | PPC.bessStatus.ESS02_temp_degreeC | BESS Site BOP Temperature | 352 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Humidity | PPC | PPC.bessStatus.ESS02_humidity_percent | BESS Site BOP Humidity | 353 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Reactive Power | PPC | PPC.bessStatus.ESS02_q3_kvar | BESS Site ESS Unit AC Reactive Power | 354 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Effective SOC | PPC | PPC.bessStatus.ESS02_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 355 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Charge Power Limit | PPC | PPC.bessStatus.ESS02_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 356 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Discharge Power Lim | PPC | PPC.bessStatus.ESS02_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 357 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Chargable Energy | PPC | PPC.bessStatus.ESS02_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 358 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Dischargable Energy | PPC | PPC.bessStatus.ESS02_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 359 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Op Code Indicator | PPC | PPC.bessStatus.ESS02_operationCode | BESS Site ESS Unit Operation Code Indicator | 360 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Num Of Strings OL | PPC | PPC.bessStatus.ESS02_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 361 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Voltage-DC | PPC | PPC.bessStatus.ESS03_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 362 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Real Power-DC | PPC | PPC.bessStatus.ESS03_p3_kw | BESS Site ESS Unit AC Real Power | 363 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Current-DC | PPC | PPC.bessStatus.ESS03_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 364 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 State Of Charge | PPC | PPC.bessStatus.ESS03_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 365 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Temperature-Avg | PPC | PPC.bessStatus.ESS03_temp_degreeC | BESS Site BOP Temperature | 366 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Humidity | PPC | PPC.bessStatus.ESS03_humidity_percent | BESS Site BOP Humidity | 367 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Reactive Power | PPC | PPC.bessStatus.ESS03_q3_kvar | BESS Site ESS Unit AC Reactive Power | 368 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Effective SOC | PPC | PPC.bessStatus.ESS03_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 369 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Charge Power Limit | PPC | PPC.bessStatus.ESS03_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 370 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Discharge Power Lim | PPC | PPC.bessStatus.ESS03_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 371 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Chargable Energy | PPC | PPC.bessStatus.ESS03_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 372 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Dischargable Energy | PPC | PPC.bessStatus.ESS03_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 373 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Op Code Indicator | PPC | PPC.bessStatus.ESS03_operationCode | BESS Site ESS Unit Operation Code Indicator | 374 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Num Of Strings OL | PPC | PPC.bessStatus.ESS03_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 375 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Voltage-DC | PPC | PPC.bessStatus.ESS04_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 376 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Real Power-DC | PPC | PPC.bessStatus.ESS04_p3_kw | BESS Site ESS Unit AC Real Power | 377 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Current-DC | PPC | PPC.bessStatus.ESS04_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 378 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 State Of Charge | PPC | PPC.bessStatus.ESS04_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 379 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Temperature-Avg | PPC | PPC.bessStatus.ESS04_temp_degreeC | BESS Site BOP Temperature | 380 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Humidity | PPC | PPC.bessStatus.ESS04_humidity_percent | BESS Site BOP Humidity | 381 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Reactive Power | PPC | PPC.bessStatus.ESS04_q3_kvar | BESS Site ESS Unit AC Reactive Power | 382 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Effective SOC | PPC | PPC.bessStatus.ESS04_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 383 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Charge Power Limit | PPC | PPC.bessStatus.ESS04_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 384 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Discharge Power Lim | PPC | PPC.bessStatus.ESS04_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 385 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Chargable Energy | PPC | PPC.bessStatus.ESS04_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 386 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Dischargable Energy | PPC | PPC.bessStatus.ESS04_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 387 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Op Code Indicator | PPC | PPC.bessStatus.ESS04_operationCode | BESS Site ESS Unit Operation Code Indicator | 388 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Num Of Strings OL | PPC | PPC.bessStatus.ESS04_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 389 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19979 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 390 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 391 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 392 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 393 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 394 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 395 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 396 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 397 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 398 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 399 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 400 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 401 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 402 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 403 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 404 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit E MW Setpoint Feedback | 405 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 406 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 407 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 408 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 409 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 410 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit E MW Setpoint Feedback | 411 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 412 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 413 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 414 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 415 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 416 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ACK Alarms | PPC |  | ACK Alarms |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Active Power Charge Limit | PPC | PPC.bessStatus.pLimitChg_kw | BESS Site Charge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Active Power Discharge Limit | PPC | PPC.bessStatus.pLimitDischg_kw | BESS Site Discharge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Available Energy | PPC |  | Available Energy |  | MWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Average SOC | PPC | PPC.bessStatus.socAvg_percent | BESS Site Average SOC |  |  | Requested-Not Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Batteries Online | PPC |  | Batteries Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Block 1 Status | PPC |  | Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Block 2 Status | PPC |  | Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Charge Capacity | PPC |  | Charge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Communications Status | PPC |  | Communications Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS A Phase Current | PPC |  | A Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS B Phase Current | PPC |  | B Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS C Phase Current | PPC |  | C Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Current-DC | PPC |  | Current-DC |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Discharge Capacity | PPC |  | Discharge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS E-Stop Status | PPC |  | E-Stop Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Frequency | PPC | PPC.bessStatus.f3_hz | BESS AC Frequency Measured at Plant Interconnect |  | Hz | Requested-Not Available | 56 | 64 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS GBS Critical Alarm | PPC |  | GBS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS GBS Warning Alarm | PPC |  | GBS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Grid Connection Status | PPC |  | Grid Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Grid Status | PPC |  | Grid Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Gross System Energy | PPC |  | Gross System Energy |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Group Mode | PPC |  | Group Mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Heartbeat Out | PPC |  | Heartbeat Out |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Island Frequency | PPC |  | Island Frequency |  | Hz | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Island Indicator | PPC |  | Island Indicator |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Island Reactive Demand | PPC |  | Island Reactive Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Island Real Demand | PPC |  | Island Real Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Island Voltage | PPC |  | Island Voltage |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Measured System Load | PPC |  | Measured System Load |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Number of Zones | PPC |  | Number of Zones |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Operating mode | PPC |  | Operating mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS PCS Critical Alarm | PPC |  | PCS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS PCS Warning Alarm | PPC |  | PCS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Peak Shaving Discharge Threshold | PPC |  | Peak Shaving Discharge Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Peak Shaving Enabled | PPC |  | Peak Shaving Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Peak Shaving Threshold | PPC |  | Peak Shaving Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Power Block 1 Status | PPC |  | Power Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Power Block 2 Status | PPC |  | Power Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Power Block Status | PPC |  | Power Block Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Power Factor | PPC |  | Power Factor |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Q Charge Limit | PPC |  | Q Charge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Q Discharge Limit | PPC |  | Q Discharge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Control Mode Running | PPC |  | Reactive Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Capacity | PPC |  | Reactive Power Capacity |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Charge Limit | PPC |  | Reactive Power Charge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Commanded | PPC |  | Reactive Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Demand | PPC |  | Reactive Power Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Discharge Limit | PPC |  | Reactive Power Discharge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Dispatch Enabled | PPC |  | Reactive Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Reactive Power Output | PPC |  | Reactive Power Output |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Control Mode Running | PPC |  | Real Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power | PPC |  | Real Power |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Capacity | PPC |  | Real Power Capacity |  | kW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Commanded | PPC |  | Real Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Demand | PPC |  | Real Power Demand |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Dispatch Enabled | PPC |  | Real Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Output | PPC |  | Real Power Output |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Real Power Priority | PPC |  | Real Power Priority |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Temperature-Amb1 | PPC |  | Temperature-Amb1 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Temperature-Amb2 | PPC |  | Temperature-Amb2 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Temperature-Avg | PPC |  | Temperature-Avg |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Voltage A-B | PPC |  | Voltage A-B |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Voltage B-C | PPC |  | Voltage B-C |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Voltage C-A | PPC |  | Voltage C-A |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Voltage-DC | PPC |  | Voltage-DC |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Zones Online | PPC |  | Zones Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Voltage-DC | PPC | PPC.bessStatus.ess01_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 417 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Real Power-DC | PPC | PPC.bessStatus.ess01_p3_kw | BESS Site ESS Unit AC Real Power | 418 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Current-DC | PPC | PPC.bessStatus.ess01_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 419 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 State Of Charge | PPC | PPC.bessStatus.ess01_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 420 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Temperature-Avg | PPC | PPC.bessStatus.ess01_temp_degreeC | BESS Site BOP Temperature | 421 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Humidity | PPC | PPC.bessStatus.ess01_humidity_percent | BESS Site BOP Humidity | 422 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Reactive Power | PPC | PPC.bessStatus.ess01_q3_kvar | BESS Site ESS Unit AC Reactive Power | 423 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Effective SOC | PPC | PPC.bessStatus.ess01_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 424 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Charge Power Limit | PPC | PPC.bessStatus.ess01_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 425 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Discharge Power Lim | PPC | PPC.bessStatus.ess01_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 426 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Chargable Energy | PPC | PPC.bessStatus.ess01_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 427 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Dischargable Energy | PPC | PPC.bessStatus.ess01_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 428 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Op Code Indicator | PPC | PPC.bessStatus.ess01_operationCode | BESS Site ESS Unit Operation Code Indicator | 429 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Num Of Strings OL | PPC | PPC.bessStatus.ess01_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 430 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Voltage-DC | PPC | PPC.bessStatus.ESS02_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 431 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Real Power-DC | PPC | PPC.bessStatus.ESS02_p3_kw | BESS Site ESS Unit AC Real Power | 432 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Current-DC | PPC | PPC.bessStatus.ESS02_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 433 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 State Of Charge | PPC | PPC.bessStatus.ESS02_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 434 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Temperature-Avg | PPC | PPC.bessStatus.ESS02_temp_degreeC | BESS Site BOP Temperature | 435 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Humidity | PPC | PPC.bessStatus.ESS02_humidity_percent | BESS Site BOP Humidity | 436 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Reactive Power | PPC | PPC.bessStatus.ESS02_q3_kvar | BESS Site ESS Unit AC Reactive Power | 437 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Effective SOC | PPC | PPC.bessStatus.ESS02_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 438 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Charge Power Limit | PPC | PPC.bessStatus.ESS02_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 439 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Discharge Power Lim | PPC | PPC.bessStatus.ESS02_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 440 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Chargable Energy | PPC | PPC.bessStatus.ESS02_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 441 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Dischargable Energy | PPC | PPC.bessStatus.ESS02_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 442 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Op Code Indicator | PPC | PPC.bessStatus.ESS02_operationCode | BESS Site ESS Unit Operation Code Indicator | 443 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Num Of Strings OL | PPC | PPC.bessStatus.ESS02_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 444 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Voltage-DC | PPC | PPC.bessStatus.ESS03_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 445 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Real Power-DC | PPC | PPC.bessStatus.ESS03_p3_kw | BESS Site ESS Unit AC Real Power | 446 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Current-DC | PPC | PPC.bessStatus.ESS03_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 447 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 State Of Charge | PPC | PPC.bessStatus.ESS03_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 448 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Temperature-Avg | PPC | PPC.bessStatus.ESS03_temp_degreeC | BESS Site BOP Temperature | 449 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Humidity | PPC | PPC.bessStatus.ESS03_humidity_percent | BESS Site BOP Humidity | 450 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Reactive Power | PPC | PPC.bessStatus.ESS03_q3_kvar | BESS Site ESS Unit AC Reactive Power | 451 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Effective SOC | PPC | PPC.bessStatus.ESS03_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 452 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Charge Power Limit | PPC | PPC.bessStatus.ESS03_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 453 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Discharge Power Lim | PPC | PPC.bessStatus.ESS03_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 454 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Chargable Energy | PPC | PPC.bessStatus.ESS03_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 455 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Dischargable Energy | PPC | PPC.bessStatus.ESS03_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 456 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Op Code Indicator | PPC | PPC.bessStatus.ESS03_operationCode | BESS Site ESS Unit Operation Code Indicator | 457 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Num Of Strings OL | PPC | PPC.bessStatus.ESS03_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 458 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Voltage-DC | PPC | PPC.bessStatus.ESS04_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 459 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Real Power-DC | PPC | PPC.bessStatus.ESS04_p3_kw | BESS Site ESS Unit AC Real Power | 460 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Current-DC | PPC | PPC.bessStatus.ESS04_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 461 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 State Of Charge | PPC | PPC.bessStatus.ESS04_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 462 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Temperature-Avg | PPC | PPC.bessStatus.ESS04_temp_degreeC | BESS Site BOP Temperature | 463 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Humidity | PPC | PPC.bessStatus.ESS04_humidity_percent | BESS Site BOP Humidity | 464 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Reactive Power | PPC | PPC.bessStatus.ESS04_q3_kvar | BESS Site ESS Unit AC Reactive Power | 465 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Effective SOC | PPC | PPC.bessStatus.ESS04_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 466 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Charge Power Limit | PPC | PPC.bessStatus.ESS04_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 467 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Discharge Power Lim | PPC | PPC.bessStatus.ESS04_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 468 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Chargable Energy | PPC | PPC.bessStatus.ESS04_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 469 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Dischargable Energy | PPC | PPC.bessStatus.ESS04_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 470 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Op Code Indicator | PPC | PPC.bessStatus.ESS04_operationCode | BESS Site ESS Unit Operation Code Indicator | 471 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Num Of Strings OL | PPC | PPC.bessStatus.ESS04_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 472 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Voltage-DC | PPC | PPC.bessStatus.ESS05_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 473 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Real Power-DC | PPC | PPC.bessStatus.ESS05_p3_kw | BESS Site ESS Unit AC Real Power | 474 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Current-DC | PPC | PPC.bessStatus.ESS05_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 475 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 State Of Charge | PPC | PPC.bessStatus.ESS05_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 476 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Temperature-Avg | PPC | PPC.bessStatus.ESS05_temp_degreeC | BESS Site BOP Temperature | 477 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Humidity | PPC | PPC.bessStatus.ESS05_humidity_percent | BESS Site BOP Humidity | 478 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Reactive Power | PPC | PPC.bessStatus.ESS05_q3_kvar | BESS Site ESS Unit AC Reactive Power | 479 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Effective SOC | PPC | PPC.bessStatus.ESS05_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 480 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Charge Power Limit | PPC | PPC.bessStatus.ESS05_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 481 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Discharge Power Lim | PPC | PPC.bessStatus.ESS05_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 482 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Chargable Energy | PPC | PPC.bessStatus.ESS05_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 483 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Dischargable Energy | PPC | PPC.bessStatus.ESS05_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 484 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Op Code Indicator | PPC | PPC.bessStatus.ESS05_operationCode | BESS Site ESS Unit Operation Code Indicator | 485 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Num Of Strings OL | PPC | PPC.bessStatus.ESS05_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 486 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19973 MW Setpoint Feedback | PPC | PPC.status.pSp_MW | GMS MW Setpoint Feedback | 487 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS POI VAR Setpoint Feedback | PPC | PPC.status.qSp_Mvar | GMS POI VAR Setpoint Feedback | 488 | MVAR | Requested-Available | -300 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS POI PF Setpoint Feedback | PPC | PPC.status.pfSp | GMS POI PF Setpoint Feedback | 489 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS POI Voltage Setpoint Feedback | PPC | PPC.status.vSp_kV | GMS POI Voltage Setpoint Feedback | 490 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Up Rate Setpoint Feedback | PPC | PPC.status.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint Feedback | 491 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Down Rate Setpoint Feedback | PPC | PPC.status.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint Feedback | 492 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Real Power Setpoint | PPC | PPC.status.pTarget_MW | PPC Real Power Setpoint | 493 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Reactive Power Setpoint | PPC | PPC.status.qTarget_Mvar | PPC Reactive Power Setpoint | 494 | MVAR | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Power Factor Setpoint | PPC | PPC.status.pfTarget | PPC Power Factor Setpoint | 495 | positive is lagging, negative is leading | Requested-Available | -1 | 1 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Voltage Setpoint | PPC | PPC.status.vTarget_kV | PPC Voltage Setpoint | 496 | KV | Requested-Available | 210 | 250 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Ramp Rate Up Setpoint | PPC | PPC.status.pUpRate_MWpMin | PPC Ramp Rate Up Setpoint | 497 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Ramp Rate Down Setpoint | PPC | PPC.status.pDownRate_MWpMin | PPC Ramp Rate Down Setpoint | 498 | MW/Min | Requested-Available | 0 | 30 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Effective Reactive Power Control Mode | PPC | PPC.status.qControlMode | PPC Control Status | 499 | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Real Time Power Potential | PPC | PPC.status.pAvailable_MW | PPC Real Time Power Potential | 500 | MW | Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed MW | PPC | PPC.status.pCurtailed_MW | Amount in MW Curtailed | 501 | MW | Not Requested-Available | 0 | 300 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI MW SP Feedback | PPC | PPC.hmi.ppa1_pSp_MW | HMI Unit B MW Setpoint Feedback | 502 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI POI PF SP Feedback | PPC | PPC.hmi.pfSp | HMI POI PF Setpoint Feedback | 503 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI POI Volt SP Feedback | PPC | PPC.hmi.vSp_kV | HMI POI Voltage Setpoint Feedback | 504 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI POI VAR SP Feedback | PPC | PPC.hmi.qSp_kvar | HMI POI VAR Setpoint Feedback | 505 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Ramp Up Rate SP Feedback | PPC | PPC.hmi.pUpSp_MWpMin | HMI Ramp Up Rate Setpoint Feedback | 506 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Ramp Down Rate SP Feedback | PPC | PPC.hmi.pDownSp_MWpMin | HMI Ramp Down Rate Setpoint Feedback | 507 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P MW SP Feedback | PPC | PPC.rem.ppa1_pSp_MW | 3rd PartyUnit B MW Setpoint Feedback | 508 | MW | Not Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P POI PF SP Feedback | PPC | PPC.rem.pfSp | 3rd PartyPOI PF Setpoint Feedback | 509 | MVAR | Not Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P POI Volt SP Feedback | PPC | PPC.rem.vSp_kV | 3rd PartyPOI Voltage Setpoint Feedback | 510 | PF | Not Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P POI VAR SP Feedback | PPC | PPC.rem.qSp_kvar | 3rd PartyPOI VAR Setpoint Feedback | 511 | KV | Not Requested-Available | 210 | 250 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Ramp Up Rate SP Feedback | PPC | PPC.rem.pUpSp_MWpMin | 3rd PartyRamp Up Rate Setpoint Feedback | 512 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Ramp Down Rate SP Feedback | PPC | PPC.rem.pDownSp_MWpMin | 3rd PartyRamp Down Rate Setpoint Feedback | 513 | MW/min | Not Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ACK Alarms | PPC |  | ACK Alarms |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Active Power Charge Limit | PPC | PPC.bessStatus.pLimitChg_kw | BESS Site Charge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Active Power Discharge Limit | PPC | PPC.bessStatus.pLimitDischg_kw | BESS Site Discharge Power Limit |  | kW | Requested-Not Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Available Energy | PPC |  | Available Energy |  | MWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Average SOC | PPC | PPC.bessStatus.socAvg_percent | BESS Site Average SOC |  |  | Requested-Not Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Batteries Online | PPC |  | Batteries Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Block 1 Status | PPC |  | Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Block 2 Status | PPC |  | Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Charge Capacity | PPC |  | Charge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Communications Status | PPC |  | Communications Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS A Phase Current | PPC |  | A Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS B Phase Current | PPC |  | B Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS C Phase Current | PPC |  | C Phase Current |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Current-DC | PPC |  | Current-DC |  | A | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Discharge Capacity | PPC |  | Discharge Capacity |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS E-Stop Status | PPC |  | E-Stop Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Frequency | PPC | PPC.bessStatus.f3_hz | BESS AC Frequency Measured at Plant Interconnect |  | Hz | Requested-Not Available | 56 | 64 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS GBS Critical Alarm | PPC |  | GBS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS GBS Warning Alarm | PPC |  | GBS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Grid Connection Status | PPC |  | Grid Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Grid Status | PPC |  | Grid Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Gross System Energy | PPC |  | Gross System Energy |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Group Mode | PPC |  | Group Mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Heartbeat Out | PPC |  | Heartbeat Out |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Island Frequency | PPC |  | Island Frequency |  | Hz | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Island Indicator | PPC |  | Island Indicator |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Island Reactive Demand | PPC |  | Island Reactive Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Island Real Demand | PPC |  | Island Real Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Island Voltage | PPC |  | Island Voltage |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Measured System Load | PPC |  | Measured System Load |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Number of Zones | PPC |  | Number of Zones |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Operating mode | PPC |  | Operating mode |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS PCS Critical Alarm | PPC |  | PCS Critical Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS PCS Warning Alarm | PPC |  | PCS Warning Alarm |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Peak Shaving Discharge Threshold | PPC |  | Peak Shaving Discharge Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Peak Shaving Enabled | PPC |  | Peak Shaving Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Peak Shaving Threshold | PPC |  | Peak Shaving Threshold |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Power Block 1 Status | PPC |  | Power Block 1 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Power Block 2 Status | PPC |  | Power Block 2 Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Power Block Status | PPC |  | Power Block Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Power Factor | PPC |  | Power Factor |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Q Charge Limit | PPC |  | Q Charge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Q Discharge Limit | PPC |  | Q Discharge Limit |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Control Mode Running | PPC |  | Reactive Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Capacity | PPC |  | Reactive Power Capacity |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Charge Limit | PPC |  | Reactive Power Charge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Commanded | PPC |  | Reactive Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Demand | PPC |  | Reactive Power Demand |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Discharge Limit | PPC |  | Reactive Power Discharge Limit |  | kVAR | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Dispatch Enabled | PPC |  | Reactive Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Reactive Power Output | PPC |  | Reactive Power Output |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Control Mode Running | PPC |  | Real Control Mode Running |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power | PPC |  | Real Power |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Capacity | PPC |  | Real Power Capacity |  | kW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Commanded | PPC |  | Real Power Commanded |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Demand | PPC |  | Real Power Demand |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Dispatch Enabled | PPC |  | Real Power Dispatch Enabled |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Output | PPC |  | Real Power Output |  | MW | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Real Power Priority | PPC |  | Real Power Priority |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Temperature-Amb1 | PPC |  | Temperature-Amb1 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Temperature-Amb2 | PPC |  | Temperature-Amb2 |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Temperature-Avg | PPC |  | Temperature-Avg |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Voltage A-B | PPC |  | Voltage A-B |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Voltage B-C | PPC |  | Voltage B-C |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Voltage C-A | PPC |  | Voltage C-A |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Voltage-DC | PPC |  | Voltage-DC |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Zones Online | PPC |  | Zones Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Voltage-DC | PPC | PPC.bessStatus.ess01_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 514 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Real Power-DC | PPC | PPC.bessStatus.ess01_p3_kw | BESS Site ESS Unit AC Real Power | 515 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Current-DC | PPC | PPC.bessStatus.ess01_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 516 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 State Of Charge | PPC | PPC.bessStatus.ess01_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 517 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Temperature-Avg | PPC | PPC.bessStatus.ess01_temp_degreeC | BESS Site BOP Temperature | 518 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Humidity | PPC | PPC.bessStatus.ess01_humidity_percent | BESS Site BOP Humidity | 519 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Reactive Power | PPC | PPC.bessStatus.ess01_q3_kvar | BESS Site ESS Unit AC Reactive Power | 520 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Effective SOC | PPC | PPC.bessStatus.ess01_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 521 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Charge Power Limit | PPC | PPC.bessStatus.ess01_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 522 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Discharge Power Lim | PPC | PPC.bessStatus.ess01_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 523 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Chargable Energy | PPC | PPC.bessStatus.ess01_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 524 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Dischargable Energy | PPC | PPC.bessStatus.ess01_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 525 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Op Code Indicator | PPC | PPC.bessStatus.ess01_operationCode | BESS Site ESS Unit Operation Code Indicator | 526 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Num Of Strings OL | PPC | PPC.bessStatus.ess01_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 527 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Voltage-DC | PPC | PPC.bessStatus.ESS02_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 528 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Real Power-DC | PPC | PPC.bessStatus.ESS02_p3_kw | BESS Site ESS Unit AC Real Power | 529 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Current-DC | PPC | PPC.bessStatus.ESS02_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 530 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 State Of Charge | PPC | PPC.bessStatus.ESS02_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 531 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Temperature-Avg | PPC | PPC.bessStatus.ESS02_temp_degreeC | BESS Site BOP Temperature | 532 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Humidity | PPC | PPC.bessStatus.ESS02_humidity_percent | BESS Site BOP Humidity | 533 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Reactive Power | PPC | PPC.bessStatus.ESS02_q3_kvar | BESS Site ESS Unit AC Reactive Power | 534 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Effective SOC | PPC | PPC.bessStatus.ESS02_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 535 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Charge Power Limit | PPC | PPC.bessStatus.ESS02_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 536 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Discharge Power Lim | PPC | PPC.bessStatus.ESS02_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 537 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Chargable Energy | PPC | PPC.bessStatus.ESS02_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 538 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Dischargable Energy | PPC | PPC.bessStatus.ESS02_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 539 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Op Code Indicator | PPC | PPC.bessStatus.ESS02_operationCode | BESS Site ESS Unit Operation Code Indicator | 540 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Num Of Strings OL | PPC | PPC.bessStatus.ESS02_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 541 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Voltage-DC | PPC | PPC.bessStatus.ESS03_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 542 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Real Power-DC | PPC | PPC.bessStatus.ESS03_p3_kw | BESS Site ESS Unit AC Real Power | 543 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Current-DC | PPC | PPC.bessStatus.ESS03_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 544 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 State Of Charge | PPC | PPC.bessStatus.ESS03_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 545 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Temperature-Avg | PPC | PPC.bessStatus.ESS03_temp_degreeC | BESS Site BOP Temperature | 546 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Humidity | PPC | PPC.bessStatus.ESS03_humidity_percent | BESS Site BOP Humidity | 547 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Reactive Power | PPC | PPC.bessStatus.ESS03_q3_kvar | BESS Site ESS Unit AC Reactive Power | 548 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Effective SOC | PPC | PPC.bessStatus.ESS03_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 549 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Charge Power Limit | PPC | PPC.bessStatus.ESS03_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 550 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Discharge Power Lim | PPC | PPC.bessStatus.ESS03_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 551 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Chargable Energy | PPC | PPC.bessStatus.ESS03_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 552 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Dischargable Energy | PPC | PPC.bessStatus.ESS03_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 553 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Op Code Indicator | PPC | PPC.bessStatus.ESS03_operationCode | BESS Site ESS Unit Operation Code Indicator | 554 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Num Of Strings OL | PPC | PPC.bessStatus.ESS03_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 555 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Voltage-DC | PPC | PPC.bessStatus.ESS04_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 556 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Real Power-DC | PPC | PPC.bessStatus.ESS04_p3_kw | BESS Site ESS Unit AC Real Power | 557 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Current-DC | PPC | PPC.bessStatus.ESS04_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 558 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 State Of Charge | PPC | PPC.bessStatus.ESS04_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 559 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Temperature-Avg | PPC | PPC.bessStatus.ESS04_temp_degreeC | BESS Site BOP Temperature | 560 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Humidity | PPC | PPC.bessStatus.ESS04_humidity_percent | BESS Site BOP Humidity | 561 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Reactive Power | PPC | PPC.bessStatus.ESS04_q3_kvar | BESS Site ESS Unit AC Reactive Power | 562 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Effective SOC | PPC | PPC.bessStatus.ESS04_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 563 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Charge Power Limit | PPC | PPC.bessStatus.ESS04_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 564 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Discharge Power Lim | PPC | PPC.bessStatus.ESS04_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 565 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Chargable Energy | PPC | PPC.bessStatus.ESS04_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 566 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Dischargable Energy | PPC | PPC.bessStatus.ESS04_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 567 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Op Code Indicator | PPC | PPC.bessStatus.ESS04_operationCode | BESS Site ESS Unit Operation Code Indicator | 568 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Num Of Strings OL | PPC | PPC.bessStatus.ESS04_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 569 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Voltage-DC | PPC | PPC.bessStatus.ESS05_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 570 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Real Power-DC | PPC | PPC.bessStatus.ESS05_p3_kw | BESS Site ESS Unit AC Real Power | 571 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Current-DC | PPC | PPC.bessStatus.ESS05_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 572 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 State Of Charge | PPC | PPC.bessStatus.ESS05_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 573 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Temperature-Avg | PPC | PPC.bessStatus.ESS05_temp_degreeC | BESS Site BOP Temperature | 574 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Humidity | PPC | PPC.bessStatus.ESS05_humidity_percent | BESS Site BOP Humidity | 575 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Reactive Power | PPC | PPC.bessStatus.ESS05_q3_kvar | BESS Site ESS Unit AC Reactive Power | 576 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Effective SOC | PPC | PPC.bessStatus.ESS05_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 577 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Charge Power Limit | PPC | PPC.bessStatus.ESS05_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 578 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Discharge Power Lim | PPC | PPC.bessStatus.ESS05_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 579 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Chargable Energy | PPC | PPC.bessStatus.ESS05_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 580 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Dischargable Energy | PPC | PPC.bessStatus.ESS05_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 581 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Op Code Indicator | PPC | PPC.bessStatus.ESS05_operationCode | BESS Site ESS Unit Operation Code Indicator | 582 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Num Of Strings OL | PPC | PPC.bessStatus.ESS05_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 583 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Voltage-DC | PPC | PPC.bessStatus.ESS06_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 584 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Real Power-DC | PPC | PPC.bessStatus.ESS06_p3_kw | BESS Site ESS Unit AC Real Power | 585 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Current-DC | PPC | PPC.bessStatus.ESS06_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 586 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 State Of Charge | PPC | PPC.bessStatus.ESS06_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 587 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Temperature-Avg | PPC | PPC.bessStatus.ESS06_temp_degreeC | BESS Site BOP Temperature | 588 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Humidity | PPC | PPC.bessStatus.ESS06_humidity_percent | BESS Site BOP Humidity | 589 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Reactive Power | PPC | PPC.bessStatus.ESS06_q3_kvar | BESS Site ESS Unit AC Reactive Power | 590 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Effective SOC | PPC | PPC.bessStatus.ESS06_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 591 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Charge Power Limit | PPC | PPC.bessStatus.ESS06_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 592 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Discharge Power Lim | PPC | PPC.bessStatus.ESS06_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 593 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Chargable Energy | PPC | PPC.bessStatus.ESS06_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 594 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Dischargable Energy | PPC | PPC.bessStatus.ESS06_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 595 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Op Code Indicator | PPC | PPC.bessStatus.ESS06_operationCode | BESS Site ESS Unit Operation Code Indicator | 596 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Num Of Strings OL | PPC | PPC.bessStatus.ESS06_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 597 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Voltage-DC | PPC | PPC.bessStatus.ESS07_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 598 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Real Power-DC | PPC | PPC.bessStatus.ESS07_p3_kw | BESS Site ESS Unit AC Real Power | 599 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Current-DC | PPC | PPC.bessStatus.ESS07_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 600 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 State Of Charge | PPC | PPC.bessStatus.ESS07_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 601 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Temperature-Avg | PPC | PPC.bessStatus.ESS07_temp_degreeC | BESS Site BOP Temperature | 602 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Humidity | PPC | PPC.bessStatus.ESS07_humidity_percent | BESS Site BOP Humidity | 603 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Reactive Power | PPC | PPC.bessStatus.ESS07_q3_kvar | BESS Site ESS Unit AC Reactive Power | 604 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Effective SOC | PPC | PPC.bessStatus.ESS07_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 605 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Charge Power Limit | PPC | PPC.bessStatus.ESS07_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 606 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Discharge Power Lim | PPC | PPC.bessStatus.ESS07_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 607 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Chargable Energy | PPC | PPC.bessStatus.ESS07_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 608 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Dischargable Energy | PPC | PPC.bessStatus.ESS07_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 609 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Op Code Indicator | PPC | PPC.bessStatus.ESS07_operationCode | BESS Site ESS Unit Operation Code Indicator | 610 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Num Of Strings OL | PPC | PPC.bessStatus.ESS07_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 611 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Voltage-DC | PPC | PPC.bessStatus.ESS08_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 612 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Real Power-DC | PPC | PPC.bessStatus.ESS08_p3_kw | BESS Site ESS Unit AC Real Power | 613 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Current-DC | PPC | PPC.bessStatus.ESS08_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 614 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 State Of Charge | PPC | PPC.bessStatus.ESS08_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 615 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Temperature-Avg | PPC | PPC.bessStatus.ESS08_temp_degreeC | BESS Site BOP Temperature | 616 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Humidity | PPC | PPC.bessStatus.ESS08_humidity_percent | BESS Site BOP Humidity | 617 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Reactive Power | PPC | PPC.bessStatus.ESS08_q3_kvar | BESS Site ESS Unit AC Reactive Power | 618 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Effective SOC | PPC | PPC.bessStatus.ESS08_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 619 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Charge Power Limit | PPC | PPC.bessStatus.ESS08_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 620 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Discharge Power Lim | PPC | PPC.bessStatus.ESS08_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 621 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Chargable Energy | PPC | PPC.bessStatus.ESS08_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 622 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Dischargable Energy | PPC | PPC.bessStatus.ESS08_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 623 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Op Code Indicator | PPC | PPC.bessStatus.ESS08_operationCode | BESS Site ESS Unit Operation Code Indicator | 624 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Num Of Strings OL | PPC | PPC.bessStatus.ESS08_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 625 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Voltage-DC | PPC | PPC.bessStatus.ESS09_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 626 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Real Power-DC | PPC | PPC.bessStatus.ESS09_p3_kw | BESS Site ESS Unit AC Real Power | 627 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Current-DC | PPC | PPC.bessStatus.ESS09_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 628 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 State Of Charge | PPC | PPC.bessStatus.ESS09_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 629 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Temperature-Avg | PPC | PPC.bessStatus.ESS09_temp_degreeC | BESS Site BOP Temperature | 630 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Humidity | PPC | PPC.bessStatus.ESS09_humidity_percent | BESS Site BOP Humidity | 631 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Reactive Power | PPC | PPC.bessStatus.ESS09_q3_kvar | BESS Site ESS Unit AC Reactive Power | 632 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Effective SOC | PPC | PPC.bessStatus.ESS09_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 633 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Charge Power Limit | PPC | PPC.bessStatus.ESS09_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 634 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Discharge Power Lim | PPC | PPC.bessStatus.ESS09_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 635 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Chargable Energy | PPC | PPC.bessStatus.ESS09_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 636 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Dischargable Energy | PPC | PPC.bessStatus.ESS09_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 637 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Op Code Indicator | PPC | PPC.bessStatus.ESS09_operationCode | BESS Site ESS Unit Operation Code Indicator | 638 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Num Of Strings OL | PPC | PPC.bessStatus.ESS09_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 639 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Voltage-DC | PPC | PPC.bessStatus.ESS10_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 640 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Real Power-DC | PPC | PPC.bessStatus.ESS10_p3_kw | BESS Site ESS Unit AC Real Power | 641 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Current-DC | PPC | PPC.bessStatus.ESS10_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 642 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 State Of Charge | PPC | PPC.bessStatus.ESS10_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 643 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Temperature-Avg | PPC | PPC.bessStatus.ESS10_temp_degreeC | BESS Site BOP Temperature | 644 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Humidity | PPC | PPC.bessStatus.ESS10_humidity_percent | BESS Site BOP Humidity | 645 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Reactive Power | PPC | PPC.bessStatus.ESS10_q3_kvar | BESS Site ESS Unit AC Reactive Power | 646 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Effective SOC | PPC | PPC.bessStatus.ESS10_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 647 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Charge Power Limit | PPC | PPC.bessStatus.ESS10_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 648 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Discharge Power Lim | PPC | PPC.bessStatus.ESS10_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 649 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Chargable Energy | PPC | PPC.bessStatus.ESS10_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 650 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Dischargable Energy | PPC | PPC.bessStatus.ESS10_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 651 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Op Code Indicator | PPC | PPC.bessStatus.ESS10_operationCode | BESS Site ESS Unit Operation Code Indicator | 652 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Num Of Strings OL | PPC | PPC.bessStatus.ESS10_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 653 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Voltage-DC | PPC | PPC.bessStatus.ESS11_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 654 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Real Power-DC | PPC | PPC.bessStatus.ESS11_p3_kw | BESS Site ESS Unit AC Real Power | 655 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Current-DC | PPC | PPC.bessStatus.ESS11_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 656 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 State Of Charge | PPC | PPC.bessStatus.ESS11_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 657 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Temperature-Avg | PPC | PPC.bessStatus.ESS11_temp_degreeC | BESS Site BOP Temperature | 658 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Humidity | PPC | PPC.bessStatus.ESS11_humidity_percent | BESS Site BOP Humidity | 659 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Reactive Power | PPC | PPC.bessStatus.ESS11_q3_kvar | BESS Site ESS Unit AC Reactive Power | 660 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Effective SOC | PPC | PPC.bessStatus.ESS11_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 661 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Charge Power Limit | PPC | PPC.bessStatus.ESS11_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 662 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Discharge Power Lim | PPC | PPC.bessStatus.ESS11_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 663 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Chargable Energy | PPC | PPC.bessStatus.ESS11_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 664 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Dischargable Energy | PPC | PPC.bessStatus.ESS11_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 665 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Op Code Indicator | PPC | PPC.bessStatus.ESS11_operationCode | BESS Site ESS Unit Operation Code Indicator | 666 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Num Of Strings OL | PPC | PPC.bessStatus.ESS11_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 667 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Voltage-DC | PPC | PPC.bessStatus.ESS12_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 668 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Real Power-DC | PPC | PPC.bessStatus.ESS12_p3_kw | BESS Site ESS Unit AC Real Power | 669 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Current-DC | PPC | PPC.bessStatus.ESS12_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 670 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 State Of Charge | PPC | PPC.bessStatus.ESS12_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 671 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Temperature-Avg | PPC | PPC.bessStatus.ESS12_temp_degreeC | BESS Site BOP Temperature | 672 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Humidity | PPC | PPC.bessStatus.ESS12_humidity_percent | BESS Site BOP Humidity | 673 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Reactive Power | PPC | PPC.bessStatus.ESS12_q3_kvar | BESS Site ESS Unit AC Reactive Power | 674 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Effective SOC | PPC | PPC.bessStatus.ESS12_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 675 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Charge Power Limit | PPC | PPC.bessStatus.ESS12_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 676 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Discharge Power Lim | PPC | PPC.bessStatus.ESS12_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 677 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Chargable Energy | PPC | PPC.bessStatus.ESS12_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 678 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Dischargable Energy | PPC | PPC.bessStatus.ESS12_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 679 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Op Code Indicator | PPC | PPC.bessStatus.ESS12_operationCode | BESS Site ESS Unit Operation Code Indicator | 680 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Num Of Strings OL | PPC | PPC.bessStatus.ESS12_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 681 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Voltage-DC | PPC | PPC.bessStatus.ESS13_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 682 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Real Power-DC | PPC | PPC.bessStatus.ESS13_p3_kw | BESS Site ESS Unit AC Real Power | 683 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Current-DC | PPC | PPC.bessStatus.ESS13_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 684 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 State Of Charge | PPC | PPC.bessStatus.ESS13_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 685 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Temperature-Avg | PPC | PPC.bessStatus.ESS13_temp_degreeC | BESS Site BOP Temperature | 686 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Humidity | PPC | PPC.bessStatus.ESS13_humidity_percent | BESS Site BOP Humidity | 687 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Reactive Power | PPC | PPC.bessStatus.ESS13_q3_kvar | BESS Site ESS Unit AC Reactive Power | 688 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Effective SOC | PPC | PPC.bessStatus.ESS13_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 689 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Charge Power Limit | PPC | PPC.bessStatus.ESS13_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 690 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Discharge Power Lim | PPC | PPC.bessStatus.ESS13_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 691 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Chargable Energy | PPC | PPC.bessStatus.ESS13_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 692 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Dischargable Energy | PPC | PPC.bessStatus.ESS13_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 693 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Op Code Indicator | PPC | PPC.bessStatus.ESS13_operationCode | BESS Site ESS Unit Operation Code Indicator | 694 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Num Of Strings OL | PPC | PPC.bessStatus.ESS13_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 695 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Voltage-DC | PPC | PPC.bessStatus.ESS14_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 696 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Real Power-DC | PPC | PPC.bessStatus.ESS14_p3_kw | BESS Site ESS Unit AC Real Power | 697 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Current-DC | PPC | PPC.bessStatus.ESS14_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 698 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 State Of Charge | PPC | PPC.bessStatus.ESS14_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 699 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Temperature-Avg | PPC | PPC.bessStatus.ESS14_temp_degreeC | BESS Site BOP Temperature | 700 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Humidity | PPC | PPC.bessStatus.ESS14_humidity_percent | BESS Site BOP Humidity | 701 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Reactive Power | PPC | PPC.bessStatus.ESS14_q3_kvar | BESS Site ESS Unit AC Reactive Power | 702 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Effective SOC | PPC | PPC.bessStatus.ESS14_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 703 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Charge Power Limit | PPC | PPC.bessStatus.ESS14_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 704 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Discharge Power Lim | PPC | PPC.bessStatus.ESS14_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 705 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Chargable Energy | PPC | PPC.bessStatus.ESS14_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 706 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Dischargable Energy | PPC | PPC.bessStatus.ESS14_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 707 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Op Code Indicator | PPC | PPC.bessStatus.ESS14_operationCode | BESS Site ESS Unit Operation Code Indicator | 708 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Num Of Strings OL | PPC | PPC.bessStatus.ESS14_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 709 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Voltage-DC | PPC | PPC.bessStatus.ESS15_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 710 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Real Power-DC | PPC | PPC.bessStatus.ESS15_p3_kw | BESS Site ESS Unit AC Real Power | 711 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Current-DC | PPC | PPC.bessStatus.ESS15_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 712 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 State Of Charge | PPC | PPC.bessStatus.ESS15_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 713 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Temperature-Avg | PPC | PPC.bessStatus.ESS15_temp_degreeC | BESS Site BOP Temperature | 714 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Humidity | PPC | PPC.bessStatus.ESS15_humidity_percent | BESS Site BOP Humidity | 715 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Reactive Power | PPC | PPC.bessStatus.ESS15_q3_kvar | BESS Site ESS Unit AC Reactive Power | 716 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Effective SOC | PPC | PPC.bessStatus.ESS15_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 717 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Charge Power Limit | PPC | PPC.bessStatus.ESS15_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 718 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Discharge Power Lim | PPC | PPC.bessStatus.ESS15_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 719 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Chargable Energy | PPC | PPC.bessStatus.ESS15_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 720 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Dischargable Energy | PPC | PPC.bessStatus.ESS15_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 721 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Op Code Indicator | PPC | PPC.bessStatus.ESS15_operationCode | BESS Site ESS Unit Operation Code Indicator | 722 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Num Of Strings OL | PPC | PPC.bessStatus.ESS15_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 723 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Voltage-DC | PPC | PPC.bessStatus.ESS16_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 724 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Real Power-DC | PPC | PPC.bessStatus.ESS16_p3_kw | BESS Site ESS Unit AC Real Power | 725 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Current-DC | PPC | PPC.bessStatus.ESS16_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 726 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 State Of Charge | PPC | PPC.bessStatus.ESS16_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 727 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Temperature-Avg | PPC | PPC.bessStatus.ESS16_temp_degreeC | BESS Site BOP Temperature | 728 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Humidity | PPC | PPC.bessStatus.ESS16_humidity_percent | BESS Site BOP Humidity | 729 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Reactive Power | PPC | PPC.bessStatus.ESS16_q3_kvar | BESS Site ESS Unit AC Reactive Power | 730 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Effective SOC | PPC | PPC.bessStatus.ESS16_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 731 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Charge Power Limit | PPC | PPC.bessStatus.ESS16_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 732 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Discharge Power Lim | PPC | PPC.bessStatus.ESS16_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 733 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Chargable Energy | PPC | PPC.bessStatus.ESS16_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 734 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Dischargable Energy | PPC | PPC.bessStatus.ESS16_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 735 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Op Code Indicator | PPC | PPC.bessStatus.ESS16_operationCode | BESS Site ESS Unit Operation Code Indicator | 736 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Num Of Strings OL | PPC | PPC.bessStatus.ESS16_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 737 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Voltage-DC | PPC | PPC.bessStatus.ESS17_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 738 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Real Power-DC | PPC | PPC.bessStatus.ESS17_p3_kw | BESS Site ESS Unit AC Real Power | 739 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Current-DC | PPC | PPC.bessStatus.ESS17_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 740 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 State Of Charge | PPC | PPC.bessStatus.ESS17_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 741 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Temperature-Avg | PPC | PPC.bessStatus.ESS17_temp_degreeC | BESS Site BOP Temperature | 742 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Humidity | PPC | PPC.bessStatus.ESS17_humidity_percent | BESS Site BOP Humidity | 743 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Reactive Power | PPC | PPC.bessStatus.ESS17_q3_kvar | BESS Site ESS Unit AC Reactive Power | 744 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Effective SOC | PPC | PPC.bessStatus.ESS17_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 745 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Charge Power Limit | PPC | PPC.bessStatus.ESS17_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 746 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Discharge Power Lim | PPC | PPC.bessStatus.ESS17_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 747 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Chargable Energy | PPC | PPC.bessStatus.ESS17_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 748 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Dischargable Energy | PPC | PPC.bessStatus.ESS17_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 749 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Op Code Indicator | PPC | PPC.bessStatus.ESS17_operationCode | BESS Site ESS Unit Operation Code Indicator | 750 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Num Of Strings OL | PPC | PPC.bessStatus.ESS17_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 751 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Voltage-DC | PPC | PPC.bessStatus.ESS18_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 752 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Real Power-DC | PPC | PPC.bessStatus.ESS18_p3_kw | BESS Site ESS Unit AC Real Power | 753 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Current-DC | PPC | PPC.bessStatus.ESS18_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 754 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 State Of Charge | PPC | PPC.bessStatus.ESS18_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 755 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Temperature-Avg | PPC | PPC.bessStatus.ESS18_temp_degreeC | BESS Site BOP Temperature | 756 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Humidity | PPC | PPC.bessStatus.ESS18_humidity_percent | BESS Site BOP Humidity | 757 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Reactive Power | PPC | PPC.bessStatus.ESS18_q3_kvar | BESS Site ESS Unit AC Reactive Power | 758 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Effective SOC | PPC | PPC.bessStatus.ESS18_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 759 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Charge Power Limit | PPC | PPC.bessStatus.ESS18_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 760 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Discharge Power Lim | PPC | PPC.bessStatus.ESS18_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 761 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Chargable Energy | PPC | PPC.bessStatus.ESS18_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 762 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Dischargable Energy | PPC | PPC.bessStatus.ESS18_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 763 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Op Code Indicator | PPC | PPC.bessStatus.ESS18_operationCode | BESS Site ESS Unit Operation Code Indicator | 764 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Num Of Strings OL | PPC | PPC.bessStatus.ESS18_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 765 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Voltage-DC | PPC | PPC.bessStatus.ESS19_vdcBus_v | BESS Site ESS Unit Battery DC Bus Voltage | 766 | kV | Requested-Available | 0 | 250 | 1000
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Real Power-DC | PPC | PPC.bessStatus.ESS19_p3_kw | BESS Site ESS Unit AC Real Power | 767 | kW | Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Current-DC | PPC | PPC.bessStatus.ESS19_idcBUs_a | BESS Site ESS Unit Battery DC Bus Current | 768 | A | Requested-Available | -32768 | 32767 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 State Of Charge | PPC | PPC.bessStatus.ESS19_socAvg_percent | BESS Site ESS Unit Battery Average SOC | 769 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Stored Energy | PPC |  | Stored Energy |  | kWh | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Temperature-Max | PPC |  | Temperature-Max |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Temperature-Min | PPC |  | Temperature-Min |  | °C | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Temperature-Avg | PPC | PPC.bessStatus.ESS19_temp_degreeC | BESS Site BOP Temperature | 770 | °C | Requested-Available | -40 | 80 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Zone Available | PPC |  | Zone Available |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Racks Online | PPC |  | Racks Online |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Racks Offline | PPC |  | Racks Offline |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Connection Status | PPC |  | Connection Status |  |  | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Voltage-Max | PPC |  | Voltage-Max |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Voltage-Min | PPC |  | Voltage-Min |  | kV | Requested-Not Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Humidity | PPC | PPC.bessStatus.ESS19_humidity_percent | BESS Site BOP Humidity | 771 | % | Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Reactive Power | PPC | PPC.bessStatus.ESS19_q3_kvar | BESS Site ESS Unit AC Reactive Power | 772 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Effective SOC | PPC | PPC.bessStatus.ESS19_socEffective_percent | BESS Site ESS Unit Battery Effective SOC | 773 | % | Not Requested-Available | 0 | 100 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Charge Power Limit | PPC | PPC.bessStatus.ESS19_pLimitChg_kw | BESS Site ESS Unit Charge Power Limit | 774 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Discharge Power Lim | PPC | PPC.bessStatus.ESS19_pLimitDischg_kw | BESS Site ESS Unit Discharge Power Limit | 775 | KW | Not Requested-Available | 0 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Chargable Energy | PPC | PPC.bessStatus.ESS19_energyChargable_kwh | BESS Site ESS Unit Chargeable Energy | 776 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Dischargable Energy | PPC | PPC.bessStatus.ESS19_energyDischargable_kwh | BESS Site ESS Unit Discharable Energy | 777 | KWh | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Op Code Indicator | PPC | PPC.bessStatus.ESS19_operationCode | BESS Site ESS Unit Operation Code Indicator | 778 | ENUM | Not Requested-Available | 0 | 3 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Num Of Strings OL | PPC | PPC.bessStatus.ESS19_numStringConnected | BESS Site ESS Unit Number of Battery String Connected to DC Bus | 779 | # | Not Requested-Available | 0 | 1000 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Battery Voltage | MET Station | MET94_MODBUS.BatteryVoltage | Battery Voltage | 780 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Humidity | MET Station | MET94_MODBUS.Humidity | Humidity | 781 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Pressure | MET Station | MET94_MODBUS.Pressure | Pressure | 782 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Temperature | MET Station | MET94_MODBUS.Temperature | Temperature | 783 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Wind Direction | MET Station | MET94_MODBUS.WindDirection | Wind Direction | 784 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Wind Speed | MET Station | MET94_MODBUS.WindSpeed | Wind Speed | 785 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Wind Speed-10 minute average | MET Station | MET94_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 786 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Wind Direction Average | MET Station | MET94_MODBUS.AvgWindDirection | Wind Direction Average | 787 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Humidity Average | MET Station | MET94_MODBUS.AvgHumidity | Humidity Average | 788 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Pressure Average | MET Station | MET94_MODBUS.AvgPressure | Pressure Average | 789 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Temperature Average | MET Station | MET94_MODBUS.AvgTemperature | Temperature Average | 790 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Rain-10 Minute | MET Station | MET94_MODBUS.10MinRain | Rain-10 Minute | 791 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET094 | Daggett 3_SUB1_MET094_Panel Temperature | MET Station | MET94_MODBUS.PanelTemperature | Panel Temperature | 792 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Heartbeat | MET Station | MET94_MODBUS.HeartBeat | Heartbeat | 793 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_FPOA Solar Irradiance | MET Station | MET94_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 794 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_RPOA Solar Irradiance | MET Station | MET94_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 795 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_GHI Solar Irradiance | MET Station | MET94_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 796 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_Albedo down Solar Irradiance | MET Station | MET94_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 797 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_BOM Temperature 1 | MET Station | MET94_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 798 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_BOM Temperature 2 | MET Station | MET94_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 799 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_BOM Temperature 3 | MET Station | MET94_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 800 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_BOM Temperature 4 | MET Station | MET94_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 801 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_BOM Temperature 5 | MET Station | MET94_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 802 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET94_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 803 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET094 | Daggett 3_SUB1_MET094_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET94_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 804 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Device Type | Soiling Station | MET94_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 805 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Datamodel Version | Soiling Station | MET94_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 806 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Software Version | Soiling Station | MET94_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 807 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Batch Num | Soiling Station | MET94_MODBUS.DUST IQ Batch Num | Production year in yy format | 808 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ SN | Soiling Station | MET94_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 809 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Hardware Version | Soiling Station | MET94_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 810 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Calibration Year | Soiling Station | MET94_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 811 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Calibration Month | Soiling Station | MET94_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 812 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Calibration Day | Soiling Station | MET94_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 813 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Tilt X | Soiling Station | MET94_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 814 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Tilt Y | Soiling Station | MET94_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 815 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Backpanel Temp | Soiling Station | MET94_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 816 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Device Voltage | Soiling Station | MET94_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 817 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Operational Mode | Soiling Station | MET94_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 818 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Status Flags | Soiling Station | MET94_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 819 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Internal Error Code | Soiling Station | MET94_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 820 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Calibration Flags | Soiling Station | MET94_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 821 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_DUST IQ Calibration Context Flags | Soiling Station | MET94_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 822 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Battery Voltage | MET Station | MET87_MODBUS.BatteryVoltage | Battery Voltage | 823 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Humidity | MET Station | MET87_MODBUS.Humidity | Humidity | 824 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Pressure | MET Station | MET87_MODBUS.Pressure | Pressure | 825 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Temperature | MET Station | MET87_MODBUS.Temperature | Temperature | 826 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Wind Direction | MET Station | MET87_MODBUS.WindDirection | Wind Direction | 827 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Wind Speed | MET Station | MET87_MODBUS.WindSpeed | Wind Speed | 828 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Wind Speed-10 minute average | MET Station | MET87_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 829 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Wind Direction Average | MET Station | MET87_MODBUS.AvgWindDirection | Wind Direction Average | 830 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Humidity Average | MET Station | MET87_MODBUS.AvgHumidity | Humidity Average | 831 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Pressure Average | MET Station | MET87_MODBUS.AvgPressure | Pressure Average | 832 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Temperature Average | MET Station | MET87_MODBUS.AvgTemperature | Temperature Average | 833 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Rain-10 Minute | MET Station | MET87_MODBUS.10MinRain | Rain-10 Minute | 834 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET087 | Daggett 3_SUB1_MET087_Panel Temperature | MET Station | MET87_MODBUS.PanelTemperature | Panel Temperature | 835 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Heartbeat | MET Station | MET87_MODBUS.HeartBeat | Heartbeat | 836 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_FPOA Solar Irradiance | MET Station | MET87_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 837 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_RPOA Solar Irradiance | MET Station | MET87_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 838 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_GHI Solar Irradiance | MET Station | MET87_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 839 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_Albedo down Solar Irradiance | MET Station | MET87_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 840 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_BOM Temperature 1 | MET Station | MET87_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 841 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_BOM Temperature 2 | MET Station | MET87_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 842 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_BOM Temperature 3 | MET Station | MET87_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 843 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_BOM Temperature 4 | MET Station | MET87_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 844 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_BOM Temperature 5 | MET Station | MET87_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 845 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET87_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 846 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET087 | Daggett 3_SUB1_MET087_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET87_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 847 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Device Type | Soiling Station | MET87_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 848 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Datamodel Version | Soiling Station | MET87_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 849 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Software Version | Soiling Station | MET87_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 850 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Batch Num | Soiling Station | MET87_MODBUS.DUST IQ Batch Num | Production year in yy format | 851 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ SN | Soiling Station | MET87_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 852 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Hardware Version | Soiling Station | MET87_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 853 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Calibration Year | Soiling Station | MET87_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 854 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Calibration Month | Soiling Station | MET87_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 855 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Calibration Day | Soiling Station | MET87_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 856 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Tilt X | Soiling Station | MET87_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 857 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Tilt Y | Soiling Station | MET87_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 858 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Backpanel Temp | Soiling Station | MET87_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 859 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Device Voltage | Soiling Station | MET87_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 860 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Operational Mode | Soiling Station | MET87_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 861 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Status Flags | Soiling Station | MET87_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 862 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Internal Error Code | Soiling Station | MET87_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 863 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Calibration Flags | Soiling Station | MET87_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 864 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_DUST IQ Calibration Context Flags | Soiling Station | MET87_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 865 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Battery Voltage | MET Station | MET83_MODBUS.BatteryVoltage | Battery Voltage | 866 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Humidity | MET Station | MET83_MODBUS.Humidity | Humidity | 867 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Pressure | MET Station | MET83_MODBUS.Pressure | Pressure | 868 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Temperature | MET Station | MET83_MODBUS.Temperature | Temperature | 869 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Wind Direction | MET Station | MET83_MODBUS.WindDirection | Wind Direction | 870 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Wind Speed | MET Station | MET83_MODBUS.WindSpeed | Wind Speed | 871 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Wind Speed-10 minute average | MET Station | MET83_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 872 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Wind Direction Average | MET Station | MET83_MODBUS.AvgWindDirection | Wind Direction Average | 873 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Humidity Average | MET Station | MET83_MODBUS.AvgHumidity | Humidity Average | 874 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Pressure Average | MET Station | MET83_MODBUS.AvgPressure | Pressure Average | 875 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Temperature Average | MET Station | MET83_MODBUS.AvgTemperature | Temperature Average | 876 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Rain-10 Minute | MET Station | MET83_MODBUS.10MinRain | Rain-10 Minute | 877 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET083 | Daggett 3_SUB1_MET083_Panel Temperature | MET Station | MET83_MODBUS.PanelTemperature | Panel Temperature | 878 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Heartbeat | MET Station | MET83_MODBUS.HeartBeat | Heartbeat | 879 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_FPOA Solar Irradiance | MET Station | MET83_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 880 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_RPOA Solar Irradiance | MET Station | MET83_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 881 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_GHI Solar Irradiance | MET Station | MET83_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 882 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_Albedo down Solar Irradiance | MET Station | MET83_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 883 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_BOM Temperature 1 | MET Station | MET83_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 884 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_BOM Temperature 2 | MET Station | MET83_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 885 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_BOM Temperature 3 | MET Station | MET83_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 886 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_BOM Temperature 4 | MET Station | MET83_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 887 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_BOM Temperature 5 | MET Station | MET83_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 888 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET83_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 889 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET083 | Daggett 3_SUB1_MET083_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET83_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 890 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Device Type | Soiling Station | MET83_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 891 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Datamodel Version | Soiling Station | MET83_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 892 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Software Version | Soiling Station | MET83_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 893 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Batch Num | Soiling Station | MET83_MODBUS.DUST IQ Batch Num | Production year in yy format | 894 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ SN | Soiling Station | MET83_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 895 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Hardware Version | Soiling Station | MET83_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 896 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Calibration Year | Soiling Station | MET83_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 897 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Calibration Month | Soiling Station | MET83_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 898 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Calibration Day | Soiling Station | MET83_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 899 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Tilt X | Soiling Station | MET83_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 900 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Tilt Y | Soiling Station | MET83_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 901 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Backpanel Temp | Soiling Station | MET83_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 902 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Device Voltage | Soiling Station | MET83_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 903 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Operational Mode | Soiling Station | MET83_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 904 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Status Flags | Soiling Station | MET83_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 905 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Internal Error Code | Soiling Station | MET83_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 906 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Calibration Flags | Soiling Station | MET83_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 907 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_DUST IQ Calibration Context Flags | Soiling Station | MET83_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 908 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Battery Voltage | MET Station | MET75_MODBUS.BatteryVoltage | Battery Voltage | 909 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Humidity | MET Station | MET75_MODBUS.Humidity | Humidity | 910 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Pressure | MET Station | MET75_MODBUS.Pressure | Pressure | 911 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Temperature | MET Station | MET75_MODBUS.Temperature | Temperature | 912 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Wind Direction | MET Station | MET75_MODBUS.WindDirection | Wind Direction | 913 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Wind Speed | MET Station | MET75_MODBUS.WindSpeed | Wind Speed | 914 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Wind Speed-10 minute average | MET Station | MET75_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 915 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Wind Direction Average | MET Station | MET75_MODBUS.AvgWindDirection | Wind Direction Average | 916 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Humidity Average | MET Station | MET75_MODBUS.AvgHumidity | Humidity Average | 917 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Pressure Average | MET Station | MET75_MODBUS.AvgPressure | Pressure Average | 918 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Temperature Average | MET Station | MET75_MODBUS.AvgTemperature | Temperature Average | 919 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Rain-10 Minute | MET Station | MET75_MODBUS.10MinRain | Rain-10 Minute | 920 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET075 | Daggett 3_SUB1_MET075_Panel Temperature | MET Station | MET75_MODBUS.PanelTemperature | Panel Temperature | 921 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Heartbeat | MET Station | MET75_MODBUS.HeartBeat | Heartbeat | 922 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_FPOA Solar Irradiance | MET Station | MET75_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 923 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_RPOA Solar Irradiance | MET Station | MET75_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 924 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_GHI Solar Irradiance | MET Station | MET75_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 925 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_Albedo down Solar Irradiance | MET Station | MET75_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 926 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_BOM Temperature 1 | MET Station | MET75_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 927 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_BOM Temperature 2 | MET Station | MET75_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 928 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_BOM Temperature 3 | MET Station | MET75_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 929 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_BOM Temperature 4 | MET Station | MET75_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 930 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_BOM Temperature 5 | MET Station | MET75_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 931 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET75_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 932 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET075 | Daggett 3_SUB1_MET075_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET75_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 933 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Device Type | Soiling Station | MET75_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 934 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Datamodel Version | Soiling Station | MET75_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 935 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Software Version | Soiling Station | MET75_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 936 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Batch Num | Soiling Station | MET75_MODBUS.DUST IQ Batch Num | Production year in yy format | 937 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ SN | Soiling Station | MET75_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 938 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Hardware Version | Soiling Station | MET75_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 939 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Calibration Year | Soiling Station | MET75_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 940 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Calibration Month | Soiling Station | MET75_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 941 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Calibration Day | Soiling Station | MET75_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 942 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Tilt X | Soiling Station | MET75_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 943 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Tilt Y | Soiling Station | MET75_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 944 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Backpanel Temp | Soiling Station | MET75_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 945 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Device Voltage | Soiling Station | MET75_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 946 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Operational Mode | Soiling Station | MET75_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 947 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Status Flags | Soiling Station | MET75_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 948 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Internal Error Code | Soiling Station | MET75_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 949 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Calibration Flags | Soiling Station | MET75_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 950 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_DUST IQ Calibration Context Flags | Soiling Station | MET75_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 951 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Battery Voltage | MET Station | MET68_MODBUS.BatteryVoltage | Battery Voltage | 952 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Humidity | MET Station | MET68_MODBUS.Humidity | Humidity | 953 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Pressure | MET Station | MET68_MODBUS.Pressure | Pressure | 954 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Temperature | MET Station | MET68_MODBUS.Temperature | Temperature | 955 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Wind Direction | MET Station | MET68_MODBUS.WindDirection | Wind Direction | 956 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Wind Speed | MET Station | MET68_MODBUS.WindSpeed | Wind Speed | 957 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Wind Speed-10 minute average | MET Station | MET68_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 958 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Wind Direction Average | MET Station | MET68_MODBUS.AvgWindDirection | Wind Direction Average | 959 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Humidity Average | MET Station | MET68_MODBUS.AvgHumidity | Humidity Average | 960 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Pressure Average | MET Station | MET68_MODBUS.AvgPressure | Pressure Average | 961 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Temperature Average | MET Station | MET68_MODBUS.AvgTemperature | Temperature Average | 962 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Rain-10 Minute | MET Station | MET68_MODBUS.10MinRain | Rain-10 Minute | 963 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET068 | Daggett 3_SUB1_MET068_Panel Temperature | MET Station | MET68_MODBUS.PanelTemperature | Panel Temperature | 964 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Heartbeat | MET Station | MET68_MODBUS.HeartBeat | Heartbeat | 965 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_FPOA Solar Irradiance | MET Station | MET68_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 966 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_RPOA Solar Irradiance | MET Station | MET68_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 967 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_GHI Solar Irradiance | MET Station | MET68_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 968 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_Albedo down Solar Irradiance | MET Station | MET68_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 969 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_BOM Temperature 1 | MET Station | MET68_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 970 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_BOM Temperature 2 | MET Station | MET68_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 971 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_BOM Temperature 3 | MET Station | MET68_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 972 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_BOM Temperature 4 | MET Station | MET68_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 973 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_BOM Temperature 5 | MET Station | MET68_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 974 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET68_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 975 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET068 | Daggett 3_SUB1_MET068_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET68_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 976 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Device Type | Soiling Station | MET68_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 977 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Datamodel Version | Soiling Station | MET68_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 978 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Software Version | Soiling Station | MET68_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 979 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Batch Num | Soiling Station | MET68_MODBUS.DUST IQ Batch Num | Production year in yy format | 980 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ SN | Soiling Station | MET68_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 981 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Hardware Version | Soiling Station | MET68_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 982 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Calibration Year | Soiling Station | MET68_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 983 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Calibration Month | Soiling Station | MET68_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 984 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Calibration Day | Soiling Station | MET68_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 985 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Tilt X | Soiling Station | MET68_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 986 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Tilt Y | Soiling Station | MET68_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 987 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Backpanel Temp | Soiling Station | MET68_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 988 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Device Voltage | Soiling Station | MET68_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 989 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Operational Mode | Soiling Station | MET68_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 990 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Status Flags | Soiling Station | MET68_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 991 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Internal Error Code | Soiling Station | MET68_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 992 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Calibration Flags | Soiling Station | MET68_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 993 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_DUST IQ Calibration Context Flags | Soiling Station | MET68_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 994 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Battery Voltage | MET Station | MET52_MODBUS.BatteryVoltage | Battery Voltage | 995 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Humidity | MET Station | MET52_MODBUS.Humidity | Humidity | 996 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Pressure | MET Station | MET52_MODBUS.Pressure | Pressure | 997 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Temperature | MET Station | MET52_MODBUS.Temperature | Temperature | 998 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Wind Direction | MET Station | MET52_MODBUS.WindDirection | Wind Direction | 999 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Wind Speed | MET Station | MET52_MODBUS.WindSpeed | Wind Speed | 1000 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Wind Speed-10 minute average | MET Station | MET52_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1001 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Wind Direction Average | MET Station | MET52_MODBUS.AvgWindDirection | Wind Direction Average | 1002 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Humidity Average | MET Station | MET52_MODBUS.AvgHumidity | Humidity Average | 1003 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Pressure Average | MET Station | MET52_MODBUS.AvgPressure | Pressure Average | 1004 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Temperature Average | MET Station | MET52_MODBUS.AvgTemperature | Temperature Average | 1005 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Rain-10 Minute | MET Station | MET52_MODBUS.10MinRain | Rain-10 Minute | 1006 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET052 | Daggett 3_SUB1_MET052_Panel Temperature | MET Station | MET52_MODBUS.PanelTemperature | Panel Temperature | 1007 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Heartbeat | MET Station | MET52_MODBUS.HeartBeat | Heartbeat | 1008 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_FPOA Solar Irradiance | MET Station | MET52_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1009 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_RPOA Solar Irradiance | MET Station | MET52_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1010 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_GHI Solar Irradiance | MET Station | MET52_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1011 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_Albedo down Solar Irradiance | MET Station | MET52_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1012 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_BOM Temperature 1 | MET Station | MET52_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1013 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_BOM Temperature 2 | MET Station | MET52_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1014 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_BOM Temperature 3 | MET Station | MET52_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1015 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_BOM Temperature 4 | MET Station | MET52_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1016 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_BOM Temperature 5 | MET Station | MET52_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1017 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET52_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1018 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET052 | Daggett 3_SUB1_MET052_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET52_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1019 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Device Type | Soiling Station | MET52_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1020 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Datamodel Version | Soiling Station | MET52_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1021 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Software Version | Soiling Station | MET52_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 1022 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Batch Num | Soiling Station | MET52_MODBUS.DUST IQ Batch Num | Production year in yy format | 1023 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ SN | Soiling Station | MET52_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1024 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Hardware Version | Soiling Station | MET52_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1025 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Calibration Year | Soiling Station | MET52_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1026 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Calibration Month | Soiling Station | MET52_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 1027 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Calibration Day | Soiling Station | MET52_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1028 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Tilt X | Soiling Station | MET52_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1029 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Tilt Y | Soiling Station | MET52_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1030 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Backpanel Temp | Soiling Station | MET52_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1031 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Device Voltage | Soiling Station | MET52_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1032 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Operational Mode | Soiling Station | MET52_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1033 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Status Flags | Soiling Station | MET52_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1034 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Internal Error Code | Soiling Station | MET52_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1035 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Calibration Flags | Soiling Station | MET52_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1036 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_DUST IQ Calibration Context Flags | Soiling Station | MET52_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1037 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Battery Voltage | MET Station | MET12_MODBUS.BatteryVoltage | Battery Voltage | 1038 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Humidity | MET Station | MET12_MODBUS.Humidity | Humidity | 1039 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Pressure | MET Station | MET12_MODBUS.Pressure | Pressure | 1040 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Temperature | MET Station | MET12_MODBUS.Temperature | Temperature | 1041 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Wind Direction | MET Station | MET12_MODBUS.WindDirection | Wind Direction | 1042 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Wind Speed | MET Station | MET12_MODBUS.WindSpeed | Wind Speed | 1043 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Wind Speed-10 minute average | MET Station | MET12_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1044 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Wind Direction Average | MET Station | MET12_MODBUS.AvgWindDirection | Wind Direction Average | 1045 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Humidity Average | MET Station | MET12_MODBUS.AvgHumidity | Humidity Average | 1046 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Pressure Average | MET Station | MET12_MODBUS.AvgPressure | Pressure Average | 1047 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Temperature Average | MET Station | MET12_MODBUS.AvgTemperature | Temperature Average | 1048 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Rain-10 Minute | MET Station | MET12_MODBUS.10MinRain | Rain-10 Minute | 1049 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET012 | Daggett 3_SUB1_MET012_Panel Temperature | MET Station | MET12_MODBUS.PanelTemperature | Panel Temperature | 1050 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Heartbeat | MET Station | MET12_MODBUS.HeartBeat | Heartbeat | 1051 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_FPOA Solar Irradiance | MET Station | MET12_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1052 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_RPOA Solar Irradiance | MET Station | MET12_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1053 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_GHI Solar Irradiance | MET Station | MET12_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1054 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_Albedo down Solar Irradiance | MET Station | MET12_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1055 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_BOM Temperature 1 | MET Station | MET12_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1056 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_BOM Temperature 2 | MET Station | MET12_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1057 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_BOM Temperature 3 | MET Station | MET12_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1058 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_BOM Temperature 4 | MET Station | MET12_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1059 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_BOM Temperature 5 | MET Station | MET12_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1060 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET12_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1061 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET012 | Daggett 3_SUB1_MET012_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET12_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1062 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Device Type | Soiling Station | MET12_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1063 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Datamodel Version | Soiling Station | MET12_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1064 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Software Version | Soiling Station | MET12_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111238 or higher) | 1065 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Batch Num | Soiling Station | MET12_MODBUS.DUST IQ Batch Num | Production year in yy format | 1066 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ SN | Soiling Station | MET12_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1067 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Hardware Version | Soiling Station | MET12_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1068 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Calibration Year | Soiling Station | MET12_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1069 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Calibration Month | Soiling Station | MET12_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 12 | 1070 |  | Not Requested-Available | 1 | 12 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Calibration Day | Soiling Station | MET12_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1071 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Tilt X | Soiling Station | MET12_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1072 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Tilt Y | Soiling Station | MET12_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1073 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Backpanel Temp | Soiling Station | MET12_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1074 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Device Voltage | Soiling Station | MET12_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1075 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Operational Mode | Soiling Station | MET12_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1076 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Status Flags | Soiling Station | MET12_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1077 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Internal Error Code | Soiling Station | MET12_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1078 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Calibration Flags | Soiling Station | MET12_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1079 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_DUST IQ Calibration Context Flags | Soiling Station | MET12_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1080 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Battery Voltage | MET Station | MET11_MODBUS.BatteryVoltage | Battery Voltage | 1081 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Humidity | MET Station | MET11_MODBUS.Humidity | Humidity | 1082 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Pressure | MET Station | MET11_MODBUS.Pressure | Pressure | 1083 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Temperature | MET Station | MET11_MODBUS.Temperature | Temperature | 1084 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Wind Direction | MET Station | MET11_MODBUS.WindDirection | Wind Direction | 1085 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Wind Speed | MET Station | MET11_MODBUS.WindSpeed | Wind Speed | 1086 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Wind Speed-10 minute average | MET Station | MET11_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1087 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Wind Direction Average | MET Station | MET11_MODBUS.AvgWindDirection | Wind Direction Average | 1088 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Humidity Average | MET Station | MET11_MODBUS.AvgHumidity | Humidity Average | 1089 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Pressure Average | MET Station | MET11_MODBUS.AvgPressure | Pressure Average | 1090 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Temperature Average | MET Station | MET11_MODBUS.AvgTemperature | Temperature Average | 1091 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Rain-10 Minute | MET Station | MET11_MODBUS.10MinRain | Rain-10 Minute | 1092 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET011 | Daggett 3_SUB1_MET011_Panel Temperature | MET Station | MET11_MODBUS.PanelTemperature | Panel Temperature | 1093 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Heartbeat | MET Station | MET11_MODBUS.HeartBeat | Heartbeat | 1094 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_FPOA Solar Irradiance | MET Station | MET11_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1095 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_RPOA Solar Irradiance | MET Station | MET11_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1096 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_GHI Solar Irradiance | MET Station | MET11_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1097 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_Albedo down Solar Irradiance | MET Station | MET11_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1098 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_BOM Temperature 1 | MET Station | MET11_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1099 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_BOM Temperature 2 | MET Station | MET11_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1100 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_BOM Temperature 3 | MET Station | MET11_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1101 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_BOM Temperature 4 | MET Station | MET11_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1102 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_BOM Temperature 5 | MET Station | MET11_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1103 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET11_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1104 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET011 | Daggett 3_SUB1_MET011_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET11_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1105 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Device Type | Soiling Station | MET11_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1106 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Datamodel Version | Soiling Station | MET11_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1107 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Software Version | Soiling Station | MET11_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1108 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Batch Num | Soiling Station | MET11_MODBUS.DUST IQ Batch Num | Production year in yy format | 1109 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ SN | Soiling Station | MET11_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1110 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Hardware Version | Soiling Station | MET11_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1111 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Calibration Year | Soiling Station | MET11_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1112 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Calibration Month | Soiling Station | MET11_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1113 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Calibration Day | Soiling Station | MET11_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1114 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Tilt X | Soiling Station | MET11_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1115 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Tilt Y | Soiling Station | MET11_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1116 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Backpanel Temp | Soiling Station | MET11_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1117 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Device Voltage | Soiling Station | MET11_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1118 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Operational Mode | Soiling Station | MET11_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1119 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Status Flags | Soiling Station | MET11_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1120 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Internal Error Code | Soiling Station | MET11_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1121 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Calibration Flags | Soiling Station | MET11_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1122 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_DUST IQ Calibration Context Flags | Soiling Station | MET11_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1123 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Battery Voltage | MET Station | MET65_MODBUS.BatteryVoltage | Battery Voltage | 1124 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Humidity | MET Station | MET65_MODBUS.Humidity | Humidity | 1125 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Pressure | MET Station | MET65_MODBUS.Pressure | Pressure | 1126 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Temperature | MET Station | MET65_MODBUS.Temperature | Temperature | 1127 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Wind Direction | MET Station | MET65_MODBUS.WindDirection | Wind Direction | 1128 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Wind Speed | MET Station | MET65_MODBUS.WindSpeed | Wind Speed | 1129 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Wind Speed-10 minute average | MET Station | MET65_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1130 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Wind Direction Average | MET Station | MET65_MODBUS.AvgWindDirection | Wind Direction Average | 1131 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Humidity Average | MET Station | MET65_MODBUS.AvgHumidity | Humidity Average | 1132 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Pressure Average | MET Station | MET65_MODBUS.AvgPressure | Pressure Average | 1133 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Temperature Average | MET Station | MET65_MODBUS.AvgTemperature | Temperature Average | 1134 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Rain-10 Minute | MET Station | MET65_MODBUS.10MinRain | Rain-10 Minute | 1135 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET065 | Daggett 3_SUB1_MET065_Panel Temperature | MET Station | MET65_MODBUS.PanelTemperature | Panel Temperature | 1136 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Heartbeat | MET Station | MET65_MODBUS.HeartBeat | Heartbeat | 1137 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_FPOA Solar Irradiance | MET Station | MET65_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1138 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_RPOA Solar Irradiance | MET Station | MET65_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1139 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_GHI Solar Irradiance | MET Station | MET65_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1140 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_Albedo down Solar Irradiance | MET Station | MET65_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1141 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_BOM Temperature 1 | MET Station | MET65_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1142 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_BOM Temperature 2 | MET Station | MET65_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1143 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_BOM Temperature 3 | MET Station | MET65_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1144 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_BOM Temperature 4 | MET Station | MET65_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1145 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_BOM Temperature 5 | MET Station | MET65_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1146 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET65_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1147 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET065 | Daggett 3_SUB1_MET065_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET65_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1148 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Device Type | Soiling Station | MET65_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1149 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Datamodel Version | Soiling Station | MET65_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1150 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Software Version | Soiling Station | MET65_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1151 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Batch Num | Soiling Station | MET65_MODBUS.DUST IQ Batch Num | Production year in yy format | 1152 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ SN | Soiling Station | MET65_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1153 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Hardware Version | Soiling Station | MET65_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1154 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Calibration Year | Soiling Station | MET65_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1155 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Calibration Month | Soiling Station | MET65_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1156 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Calibration Day | Soiling Station | MET65_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1157 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Tilt X | Soiling Station | MET65_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1158 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Tilt Y | Soiling Station | MET65_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1159 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Backpanel Temp | Soiling Station | MET65_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1160 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Device Voltage | Soiling Station | MET65_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1161 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Operational Mode | Soiling Station | MET65_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1162 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Status Flags | Soiling Station | MET65_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1163 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Internal Error Code | Soiling Station | MET65_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1164 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Calibration Flags | Soiling Station | MET65_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1165 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_DUST IQ Calibration Context Flags | Soiling Station | MET65_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1166 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Battery Voltage | MET Station | MET44_MODBUS.BatteryVoltage | Battery Voltage | 1167 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Humidity | MET Station | MET44_MODBUS.Humidity | Humidity | 1168 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Pressure | MET Station | MET44_MODBUS.Pressure | Pressure | 1169 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Temperature | MET Station | MET44_MODBUS.Temperature | Temperature | 1170 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Wind Direction | MET Station | MET44_MODBUS.WindDirection | Wind Direction | 1171 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Wind Speed | MET Station | MET44_MODBUS.WindSpeed | Wind Speed | 1172 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Wind Speed-10 minute average | MET Station | MET44_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1173 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Wind Direction Average | MET Station | MET44_MODBUS.AvgWindDirection | Wind Direction Average | 1174 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Humidity Average | MET Station | MET44_MODBUS.AvgHumidity | Humidity Average | 1175 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Pressure Average | MET Station | MET44_MODBUS.AvgPressure | Pressure Average | 1176 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Temperature Average | MET Station | MET44_MODBUS.AvgTemperature | Temperature Average | 1177 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Rain-10 Minute | MET Station | MET44_MODBUS.10MinRain | Rain-10 Minute | 1178 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET044 | Daggett 3_SUB1_MET044_Panel Temperature | MET Station | MET44_MODBUS.PanelTemperature | Panel Temperature | 1179 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Heartbeat | MET Station | MET44_MODBUS.HeartBeat | Heartbeat | 1180 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_FPOA Solar Irradiance | MET Station | MET44_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1181 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_RPOA Solar Irradiance | MET Station | MET44_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1182 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_GHI Solar Irradiance | MET Station | MET44_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1183 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_Albedo down Solar Irradiance | MET Station | MET44_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1184 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_BOM Temperature 1 | MET Station | MET44_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1185 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_BOM Temperature 2 | MET Station | MET44_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1186 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_BOM Temperature 3 | MET Station | MET44_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1187 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_BOM Temperature 4 | MET Station | MET44_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1188 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_BOM Temperature 5 | MET Station | MET44_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1189 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET44_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1190 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET044 | Daggett 3_SUB1_MET044_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET44_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1191 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Device Type | Soiling Station | MET44_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1192 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Datamodel Version | Soiling Station | MET44_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1193 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Software Version | Soiling Station | MET44_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1194 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Batch Num | Soiling Station | MET44_MODBUS.DUST IQ Batch Num | Production year in yy format | 1195 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ SN | Soiling Station | MET44_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1196 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Hardware Version | Soiling Station | MET44_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1197 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Calibration Year | Soiling Station | MET44_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1198 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Calibration Month | Soiling Station | MET44_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1199 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Calibration Day | Soiling Station | MET44_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1200 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Tilt X | Soiling Station | MET44_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1201 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Tilt Y | Soiling Station | MET44_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1202 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Backpanel Temp | Soiling Station | MET44_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1203 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Device Voltage | Soiling Station | MET44_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1204 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Operational Mode | Soiling Station | MET44_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1205 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Status Flags | Soiling Station | MET44_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1206 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Internal Error Code | Soiling Station | MET44_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1207 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Calibration Flags | Soiling Station | MET44_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1208 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_DUST IQ Calibration Context Flags | Soiling Station | MET44_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1209 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Battery Voltage | MET Station | MET50_MODBUS.BatteryVoltage | Battery Voltage | 1210 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Humidity | MET Station | MET50_MODBUS.Humidity | Humidity | 1211 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Pressure | MET Station | MET50_MODBUS.Pressure | Pressure | 1212 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Temperature | MET Station | MET50_MODBUS.Temperature | Temperature | 1213 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Wind Direction | MET Station | MET50_MODBUS.WindDirection | Wind Direction | 1214 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Wind Speed | MET Station | MET50_MODBUS.WindSpeed | Wind Speed | 1215 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Wind Speed-10 minute average | MET Station | MET50_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1216 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Wind Direction Average | MET Station | MET50_MODBUS.AvgWindDirection | Wind Direction Average | 1217 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Humidity Average | MET Station | MET50_MODBUS.AvgHumidity | Humidity Average | 1218 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Pressure Average | MET Station | MET50_MODBUS.AvgPressure | Pressure Average | 1219 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Temperature Average | MET Station | MET50_MODBUS.AvgTemperature | Temperature Average | 1220 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Rain-10 Minute | MET Station | MET50_MODBUS.10MinRain | Rain-10 Minute | 1221 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET050 | Daggett 3_SUB1_MET050_Panel Temperature | MET Station | MET50_MODBUS.PanelTemperature | Panel Temperature | 1222 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Heartbeat | MET Station | MET50_MODBUS.HeartBeat | Heartbeat | 1223 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_FPOA Solar Irradiance | MET Station | MET50_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1224 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_RPOA Solar Irradiance | MET Station | MET50_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1225 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_GHI Solar Irradiance | MET Station | MET50_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1226 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_Albedo down Solar Irradiance | MET Station | MET50_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1227 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_BOM Temperature 1 | MET Station | MET50_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1228 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_BOM Temperature 2 | MET Station | MET50_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1229 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_BOM Temperature 3 | MET Station | MET50_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1230 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_BOM Temperature 4 | MET Station | MET50_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1231 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_BOM Temperature 5 | MET Station | MET50_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1232 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET50_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1233 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET050 | Daggett 3_SUB1_MET050_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET50_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1234 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Device Type | Soiling Station | MET50_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1235 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Datamodel Version | Soiling Station | MET50_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1236 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Software Version | Soiling Station | MET50_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1237 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Batch Num | Soiling Station | MET50_MODBUS.DUST IQ Batch Num | Production year in yy format | 1238 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ SN | Soiling Station | MET50_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1239 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Hardware Version | Soiling Station | MET50_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1240 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Calibration Year | Soiling Station | MET50_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1241 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Calibration Month | Soiling Station | MET50_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1242 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Calibration Day | Soiling Station | MET50_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1243 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Tilt X | Soiling Station | MET50_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1244 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Tilt Y | Soiling Station | MET50_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1245 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Backpanel Temp | Soiling Station | MET50_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1246 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Device Voltage | Soiling Station | MET50_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1247 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Operational Mode | Soiling Station | MET50_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1248 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Status Flags | Soiling Station | MET50_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1249 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Internal Error Code | Soiling Station | MET50_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1250 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Calibration Flags | Soiling Station | MET50_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1251 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_DUST IQ Calibration Context Flags | Soiling Station | MET50_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1252 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Battery Voltage | MET Station | MET19_MODBUS.BatteryVoltage | Battery Voltage | 1253 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Humidity | MET Station | MET19_MODBUS.Humidity | Humidity | 1254 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Pressure | MET Station | MET19_MODBUS.Pressure | Pressure | 1255 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Temperature | MET Station | MET19_MODBUS.Temperature | Temperature | 1256 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Wind Direction | MET Station | MET19_MODBUS.WindDirection | Wind Direction | 1257 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Wind Speed | MET Station | MET19_MODBUS.WindSpeed | Wind Speed | 1258 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Wind Speed-10 minute average | MET Station | MET19_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1259 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Wind Direction Average | MET Station | MET19_MODBUS.AvgWindDirection | Wind Direction Average | 1260 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Humidity Average | MET Station | MET19_MODBUS.AvgHumidity | Humidity Average | 1261 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Pressure Average | MET Station | MET19_MODBUS.AvgPressure | Pressure Average | 1262 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Temperature Average | MET Station | MET19_MODBUS.AvgTemperature | Temperature Average | 1263 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Rain-10 Minute | MET Station | MET19_MODBUS.10MinRain | Rain-10 Minute | 1264 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET019 | Daggett 3_SUB1_MET019_Panel Temperature | MET Station | MET19_MODBUS.PanelTemperature | Panel Temperature | 1265 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Heartbeat | MET Station | MET19_MODBUS.HeartBeat | Heartbeat | 1266 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_FPOA Solar Irradiance | MET Station | MET19_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1267 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_RPOA Solar Irradiance | MET Station | MET19_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1268 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_GHI Solar Irradiance | MET Station | MET19_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1269 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_Albedo down Solar Irradiance | MET Station | MET19_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1270 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_BOM Temperature 1 | MET Station | MET19_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1271 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_BOM Temperature 2 | MET Station | MET19_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1272 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_BOM Temperature 3 | MET Station | MET19_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1273 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_BOM Temperature 4 | MET Station | MET19_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1274 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_BOM Temperature 5 | MET Station | MET19_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1275 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET19_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1276 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET019 | Daggett 3_SUB1_MET019_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET19_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1277 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Device Type | Soiling Station | MET19_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1278 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Datamodel Version | Soiling Station | MET19_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1279 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Software Version | Soiling Station | MET19_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1280 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Batch Num | Soiling Station | MET19_MODBUS.DUST IQ Batch Num | Production year in yy format | 1281 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ SN | Soiling Station | MET19_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1282 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Hardware Version | Soiling Station | MET19_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1283 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Calibration Year | Soiling Station | MET19_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1284 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Calibration Month | Soiling Station | MET19_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1285 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Calibration Day | Soiling Station | MET19_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1286 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Tilt X | Soiling Station | MET19_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1287 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Tilt Y | Soiling Station | MET19_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1288 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Backpanel Temp | Soiling Station | MET19_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1289 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Device Voltage | Soiling Station | MET19_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1290 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Operational Mode | Soiling Station | MET19_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1291 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Status Flags | Soiling Station | MET19_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1292 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Internal Error Code | Soiling Station | MET19_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1293 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Calibration Flags | Soiling Station | MET19_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1294 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_DUST IQ Calibration Context Flags | Soiling Station | MET19_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1295 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Battery Voltage | MET Station | MET08_MODBUS.BatteryVoltage | Battery Voltage | 1296 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Humidity | MET Station | MET08_MODBUS.Humidity | Humidity | 1297 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Pressure | MET Station | MET08_MODBUS.Pressure | Pressure | 1298 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Temperature | MET Station | MET08_MODBUS.Temperature | Temperature | 1299 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Wind Direction | MET Station | MET08_MODBUS.WindDirection | Wind Direction | 1300 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Wind Speed | MET Station | MET08_MODBUS.WindSpeed | Wind Speed | 1301 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Wind Speed-10 minute average | MET Station | MET08_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1302 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Wind Direction Average | MET Station | MET08_MODBUS.AvgWindDirection | Wind Direction Average | 1303 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Humidity Average | MET Station | MET08_MODBUS.AvgHumidity | Humidity Average | 1304 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Pressure Average | MET Station | MET08_MODBUS.AvgPressure | Pressure Average | 1305 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Temperature Average | MET Station | MET08_MODBUS.AvgTemperature | Temperature Average | 1306 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Rain-10 Minute | MET Station | MET08_MODBUS.10MinRain | Rain-10 Minute | 1307 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET008 | Daggett 3_SUB1_MET008_Panel Temperature | MET Station | MET08_MODBUS.PanelTemperature | Panel Temperature | 1308 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Heartbeat | MET Station | MET08_MODBUS.HeartBeat | Heartbeat | 1309 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_FPOA Solar Irradiance | MET Station | MET08_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1310 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_RPOA Solar Irradiance | MET Station | MET08_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1311 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_GHI Solar Irradiance | MET Station | MET08_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1312 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_Albedo down Solar Irradiance | MET Station | MET08_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1313 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_BOM Temperature 1 | MET Station | MET08_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1314 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_BOM Temperature 2 | MET Station | MET08_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1315 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_BOM Temperature 3 | MET Station | MET08_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1316 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_BOM Temperature 4 | MET Station | MET08_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1317 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_BOM Temperature 5 | MET Station | MET08_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1318 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET08_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1319 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET008 | Daggett 3_SUB1_MET008_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET08_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1320 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Device Type | Soiling Station | MET08_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1321 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Datamodel Version | Soiling Station | MET08_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1322 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Software Version | Soiling Station | MET08_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1323 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Batch Num | Soiling Station | MET08_MODBUS.DUST IQ Batch Num | Production year in yy format | 1324 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ SN | Soiling Station | MET08_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1325 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Hardware Version | Soiling Station | MET08_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1326 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Calibration Year | Soiling Station | MET08_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1327 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Calibration Month | Soiling Station | MET08_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1328 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Calibration Day | Soiling Station | MET08_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1329 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Tilt X | Soiling Station | MET08_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1330 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Tilt Y | Soiling Station | MET08_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1331 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Backpanel Temp | Soiling Station | MET08_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1332 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Device Voltage | Soiling Station | MET08_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1333 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Operational Mode | Soiling Station | MET08_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1334 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Status Flags | Soiling Station | MET08_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1335 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Internal Error Code | Soiling Station | MET08_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1336 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Calibration Flags | Soiling Station | MET08_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1337 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_DUST IQ Calibration Context Flags | Soiling Station | MET08_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1338 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Battery Voltage | MET Station | MET23_MODBUS.BatteryVoltage | Battery Voltage | 1339 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Humidity | MET Station | MET23_MODBUS.Humidity | Humidity | 1340 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Pressure | MET Station | MET23_MODBUS.Pressure | Pressure | 1341 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Temperature | MET Station | MET23_MODBUS.Temperature | Temperature | 1342 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Wind Direction | MET Station | MET23_MODBUS.WindDirection | Wind Direction | 1343 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Wind Speed | MET Station | MET23_MODBUS.WindSpeed | Wind Speed | 1344 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Wind Speed-10 minute average | MET Station | MET23_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1345 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Wind Direction Average | MET Station | MET23_MODBUS.AvgWindDirection | Wind Direction Average | 1346 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Humidity Average | MET Station | MET23_MODBUS.AvgHumidity | Humidity Average | 1347 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Pressure Average | MET Station | MET23_MODBUS.AvgPressure | Pressure Average | 1348 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Temperature Average | MET Station | MET23_MODBUS.AvgTemperature | Temperature Average | 1349 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Rain-10 Minute | MET Station | MET23_MODBUS.10MinRain | Rain-10 Minute | 1350 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET023 | Daggett 3_SUB1_MET023_Panel Temperature | MET Station | MET23_MODBUS.PanelTemperature | Panel Temperature | 1351 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Heartbeat | MET Station | MET23_MODBUS.HeartBeat | Heartbeat | 1352 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_FPOA Solar Irradiance | MET Station | MET23_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1353 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_RPOA Solar Irradiance | MET Station | MET23_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1354 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_GHI Solar Irradiance | MET Station | MET23_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1355 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_Albedo down Solar Irradiance | MET Station | MET23_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1356 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_BOM Temperature 1 | MET Station | MET23_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1357 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_BOM Temperature 2 | MET Station | MET23_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1358 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_BOM Temperature 3 | MET Station | MET23_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1359 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_BOM Temperature 4 | MET Station | MET23_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1360 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_BOM Temperature 5 | MET Station | MET23_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1361 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET23_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1362 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET023 | Daggett 3_SUB1_MET023_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET23_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1363 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Device Type | Soiling Station | MET23_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1364 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Datamodel Version | Soiling Station | MET23_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1365 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Software Version | Soiling Station | MET23_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1366 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Batch Num | Soiling Station | MET23_MODBUS.DUST IQ Batch Num | Production year in yy format | 1367 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ SN | Soiling Station | MET23_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1368 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Hardware Version | Soiling Station | MET23_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1369 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Calibration Year | Soiling Station | MET23_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1370 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Calibration Month | Soiling Station | MET23_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1371 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Calibration Day | Soiling Station | MET23_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1372 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Tilt X | Soiling Station | MET23_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1373 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Tilt Y | Soiling Station | MET23_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1374 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Backpanel Temp | Soiling Station | MET23_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1375 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Device Voltage | Soiling Station | MET23_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1376 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Operational Mode | Soiling Station | MET23_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1377 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Status Flags | Soiling Station | MET23_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1378 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Internal Error Code | Soiling Station | MET23_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1379 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Calibration Flags | Soiling Station | MET23_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1380 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_DUST IQ Calibration Context Flags | Soiling Station | MET23_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1381 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Battery Voltage | MET Station | MET34_MODBUS.BatteryVoltage | Battery Voltage | 1382 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Humidity | MET Station | MET34_MODBUS.Humidity | Humidity | 1383 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Pressure | MET Station | MET34_MODBUS.Pressure | Pressure | 1384 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Temperature | MET Station | MET34_MODBUS.Temperature | Temperature | 1385 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Wind Direction | MET Station | MET34_MODBUS.WindDirection | Wind Direction | 1386 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Wind Speed | MET Station | MET34_MODBUS.WindSpeed | Wind Speed | 1387 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Wind Speed-10 minute average | MET Station | MET34_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1388 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Wind Direction Average | MET Station | MET34_MODBUS.AvgWindDirection | Wind Direction Average | 1389 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Humidity Average | MET Station | MET34_MODBUS.AvgHumidity | Humidity Average | 1390 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Pressure Average | MET Station | MET34_MODBUS.AvgPressure | Pressure Average | 1391 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Temperature Average | MET Station | MET34_MODBUS.AvgTemperature | Temperature Average | 1392 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Rain-10 Minute | MET Station | MET34_MODBUS.10MinRain | Rain-10 Minute | 1393 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET034 | Daggett 3_SUB1_MET034_Panel Temperature | MET Station | MET34_MODBUS.PanelTemperature | Panel Temperature | 1394 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Heartbeat | MET Station | MET34_MODBUS.HeartBeat | Heartbeat | 1395 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_FPOA Solar Irradiance | MET Station | MET34_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1396 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_RPOA Solar Irradiance | MET Station | MET34_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1397 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_GHI Solar Irradiance | MET Station | MET34_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1398 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_Albedo down Solar Irradiance | MET Station | MET34_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1399 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_BOM Temperature 1 | MET Station | MET34_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1400 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_BOM Temperature 2 | MET Station | MET34_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1401 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_BOM Temperature 3 | MET Station | MET34_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1402 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_BOM Temperature 4 | MET Station | MET34_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1403 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_BOM Temperature 5 | MET Station | MET34_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1404 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET34_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1405 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET034 | Daggett 3_SUB1_MET034_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET34_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1406 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Device Type | Soiling Station | MET34_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1407 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Datamodel Version | Soiling Station | MET34_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1408 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Software Version | Soiling Station | MET34_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1409 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Batch Num | Soiling Station | MET34_MODBUS.DUST IQ Batch Num | Production year in yy format | 1410 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ SN | Soiling Station | MET34_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1411 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Hardware Version | Soiling Station | MET34_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1412 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Calibration Year | Soiling Station | MET34_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1413 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Calibration Month | Soiling Station | MET34_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1414 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Calibration Day | Soiling Station | MET34_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1415 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Tilt X | Soiling Station | MET34_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1416 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Tilt Y | Soiling Station | MET34_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1417 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Backpanel Temp | Soiling Station | MET34_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1418 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Device Voltage | Soiling Station | MET34_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1419 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Operational Mode | Soiling Station | MET34_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1420 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Status Flags | Soiling Station | MET34_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1421 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Internal Error Code | Soiling Station | MET34_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1422 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Calibration Flags | Soiling Station | MET34_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1423 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_DUST IQ Calibration Context Flags | Soiling Station | MET34_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1424 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Battery Voltage | MET Station | MET31_MODBUS.BatteryVoltage | Battery Voltage | 1425 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Humidity | MET Station | MET31_MODBUS.Humidity | Humidity | 1426 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Pressure | MET Station | MET31_MODBUS.Pressure | Pressure | 1427 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Temperature | MET Station | MET31_MODBUS.Temperature | Temperature | 1428 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Wind Direction | MET Station | MET31_MODBUS.WindDirection | Wind Direction | 1429 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Wind Speed | MET Station | MET31_MODBUS.WindSpeed | Wind Speed | 1430 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Wind Speed-10 minute average | MET Station | MET31_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1431 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Wind Direction Average | MET Station | MET31_MODBUS.AvgWindDirection | Wind Direction Average | 1432 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Humidity Average | MET Station | MET31_MODBUS.AvgHumidity | Humidity Average | 1433 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Pressure Average | MET Station | MET31_MODBUS.AvgPressure | Pressure Average | 1434 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Temperature Average | MET Station | MET31_MODBUS.AvgTemperature | Temperature Average | 1435 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Rain-10 Minute | MET Station | MET31_MODBUS.10MinRain | Rain-10 Minute | 1436 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET031 | Daggett 3_SUB1_MET031_Panel Temperature | MET Station | MET31_MODBUS.PanelTemperature | Panel Temperature | 1437 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Heartbeat | MET Station | MET31_MODBUS.HeartBeat | Heartbeat | 1438 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_FPOA Solar Irradiance | MET Station | MET31_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1439 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_RPOA Solar Irradiance | MET Station | MET31_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1440 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_GHI Solar Irradiance | MET Station | MET31_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1441 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_Albedo down Solar Irradiance | MET Station | MET31_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1442 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_BOM Temperature 1 | MET Station | MET31_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1443 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_BOM Temperature 2 | MET Station | MET31_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1444 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_BOM Temperature 3 | MET Station | MET31_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1445 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_BOM Temperature 4 | MET Station | MET31_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1446 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_BOM Temperature 5 | MET Station | MET31_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1447 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET31_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1448 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET031 | Daggett 3_SUB1_MET031_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET31_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1449 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Device Type | Soiling Station | MET31_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1450 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Datamodel Version | Soiling Station | MET31_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1451 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Software Version | Soiling Station | MET31_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1452 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Batch Num | Soiling Station | MET31_MODBUS.DUST IQ Batch Num | Production year in yy format | 1453 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ SN | Soiling Station | MET31_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1454 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Hardware Version | Soiling Station | MET31_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1455 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Calibration Year | Soiling Station | MET31_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1456 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Calibration Month | Soiling Station | MET31_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1457 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Calibration Day | Soiling Station | MET31_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1458 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Tilt X | Soiling Station | MET31_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1459 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Tilt Y | Soiling Station | MET31_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1460 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Backpanel Temp | Soiling Station | MET31_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1461 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Device Voltage | Soiling Station | MET31_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1462 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Operational Mode | Soiling Station | MET31_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1463 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Status Flags | Soiling Station | MET31_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1464 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Internal Error Code | Soiling Station | MET31_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1465 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Calibration Flags | Soiling Station | MET31_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1466 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_DUST IQ Calibration Context Flags | Soiling Station | MET31_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1467 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Battery Voltage | MET Station | MET42_MODBUS.BatteryVoltage | Battery Voltage | 1468 | V | Requested-Available | 11.5 | 14 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Humidity | MET Station | MET42_MODBUS.Humidity | Humidity | 1469 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Pressure | MET Station | MET42_MODBUS.Pressure | Pressure | 1470 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Temperature | MET Station | MET42_MODBUS.Temperature | Temperature | 1471 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Wind Direction | MET Station | MET42_MODBUS.WindDirection | Wind Direction | 1472 | ° | Requested-Available | 0 | 359 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Wind Speed | MET Station | MET42_MODBUS.WindSpeed | Wind Speed | 1473 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Wind Speed-10 minute average | MET Station | MET42_MODBUS.AvgWindSpeed | Wind Speed-10 minute average | 1474 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Wind Direction Average | MET Station | MET42_MODBUS.AvgWindDirection | Wind Direction Average | 1475 | m/s | Requested-Available | 0 | 60 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Humidity Average | MET Station | MET42_MODBUS.AvgHumidity | Humidity Average | 1476 | % | Requested-Available | 0 | 100 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Pressure Average | MET Station | MET42_MODBUS.AvgPressure | Pressure Average | 1477 | hPa | Requested-Available | 0 | 1100 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Temperature Average | MET Station | MET42_MODBUS.AvgTemperature | Temperature Average | 1478 | °C | Requested-Available | -40 | 80 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Rain-10 Minute | MET Station | MET42_MODBUS.10MinRain | Rain-10 Minute | 1479 | in | Requested-Available | 0 | 10000 | 0.39
SUB1 | MET042 | Daggett 3_SUB1_MET042_Panel Temperature | MET Station | MET42_MODBUS.PanelTemperature | Panel Temperature | 1480 | °C | Requested-Available | 0 | 70 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Heartbeat | MET Station | MET42_MODBUS.HeartBeat | Heartbeat | 1481 | Counts | Requested-Available | 0 | 59 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_FPOA Solar Irradiance | MET Station | MET42_MODBUS.FPOA Solar Irradiance | FPOA Solar Irradiance | 1482 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_RPOA Solar Irradiance | MET Station | MET42_MODBUS.RPOA Solar Irradiance | RPOA Solar Irradiance | 1483 | W/m2 | Not Requested-Available | 0 | 1500 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_GHI Solar Irradiance | MET Station | MET42_MODBUS.GHI Solar Irradiance | GHI Solar Irradiance | 1484 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_Albedo down Solar Irradiance | MET Station | MET42_MODBUS.Albedo Solar Irradiance | Albedo Solar Irradiance | 1485 | W/m2 | Not Requested-Available | 1 | 1500 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_BOM Temperature 1 | MET Station | MET42_MODBUS.BOM Temperature 1 | BOM Temperature 1 | 1486 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_BOM Temperature 2 | MET Station | MET42_MODBUS.BOM Temperature 2 | BOM Temperature 2 | 1487 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_BOM Temperature 3 | MET Station | MET42_MODBUS.BOM Temperature 3 | BOM Temperature 3 | 1488 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_BOM Temperature 4 | MET Station | MET42_MODBUS.BOM Temperature 4 | BOM Temperature 4 | 1489 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_BOM Temperature 5 | MET Station | MET42_MODBUS.BOM Temperature 5 | BOM Temperature 5 | 1490 | °C | Not Requested-Available | -40 | 135 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_DUST IQ Soiling Ratio Sensor 1 | MET Station | MET42_MODBUS.DUST IQ Soiling Ratio Sensor 1 | DUST IQ Soiling Ratio Sensor 1 | 1491 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | MET042 | Daggett 3_SUB1_MET042_DUST IQ Soiling Ratio Sensor 2 | MET Station | MET42_MODBUS.DUST IQ Soiling Ratio Sensor 2 | DUST IQ Soiling Ratio Sensor 2 | 1492 | % | Not Requested-Available | 50 | 101 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Device Type | Soiling Station | MET42_MODBUS.DUST IQ Device Type | Device type of the DUST-IQ sensor 800 for DustIQ | 1493 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Datamodel Version | Soiling Station | MET42_MODBUS.DUST IQ Datamodel Version | Version of the data model (=302 for current version) | 1494 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Software Version | Soiling Station | MET42_MODBUS.DUST IQ Software Version | Software version of the firmware (= 111138 or higher) | 1495 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Batch Num | Soiling Station | MET42_MODBUS.DUST IQ Batch Num | Production year in yy format | 1496 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ SN | Soiling Station | MET42_MODBUS.DUST IQ Serial Number | Production serial number for the above mentioned year from 0000 to 9999 | 1497 |  | Not Requested-Available | 0 | 9999 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Hardware Version | Soiling Station | MET42_MODBUS.DUST IQ Hardware Version | Hardware version (= 5 for current hardware) | 1498 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Calibration Year | Soiling Station | MET42_MODBUS.DUST IQ Calibration Year | Factory calibration year 2000 to 2099 | 1499 |  | Not Requested-Available | 2000 | 2099 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Calibration Month | Soiling Station | MET42_MODBUS.DUST IQ Calibration Month | Factory calibration month 1 to 11 | 1500 |  | Not Requested-Available | 1 | 11 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Calibration Day | Soiling Station | MET42_MODBUS.DUST IQ Calibration Day | Factory calibration day 1 to 31 | 1501 |  | Not Requested-Available | 1 | 31 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Tilt X | Soiling Station | MET42_MODBUS.DUST IQ Tilt X | Tilt X direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1502 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Tilt Y | Soiling Station | MET42_MODBUS.DUST IQ Tilt Y | Tilt Y direction (long axis ) -179.9 to +180.0 in steps of 0.1 degree | 1503 | ° | Not Requested-Available | -180 | 180 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Backpanel Temp | Soiling Station | MET42_MODBUS.DUST IQ Backpanel Temp | Back panel temperature in 0.1 Kelvin | 1504 | K | Not Requested-Available | -274 | 500 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Device Voltage | Soiling Station | MET42_MODBUS.DUST IQ Device Voltage | Device voltage at the input connector in mV | 1505 | mV | Not Requested-Available | 0 | 1000000 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Operational Mode | Soiling Station | MET42_MODBUS.DUST IQ Operational Mode | Operational mode: normal =1, (service =2 , calibration = 3) | 1506 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Status Flags | Soiling Station | MET42_MODBUS.DUST IQ Status Flags | Device Status flags (0 = status OK) | 1507 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Internal Error Code | Soiling Station | MET42_MODBUS.DUST IQ Internal Error Code | Internal Values for Error Handling for identification and error handling | 1508 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Calibration Flags | Soiling Station | MET42_MODBUS.DUST IQ Calibration Flags | Calibration flags (0 = OK) | 1509 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_DUST IQ Calibration Context Flags | Soiling Station | MET42_MODBUS.DUST IQ Calibration Context Flags | Calibration context flags (0 = status OK) | 1510 |  | Not Requested-Available | 0 | 2147483647 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_Soiling Ratio | Soiling Station | MET94_MODBUS.SoilingRatio | Soiling Ratio | 1511 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_Soiling Ratio | Soiling Station | MET87_MODBUS.SoilingRatio | Soiling Ratio | 1512 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_Soiling Ratio | Soiling Station | MET83_MODBUS.SoilingRatio | Soiling Ratio | 1513 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_Soiling Ratio | Soiling Station | MET75_MODBUS.SoilingRatio | Soiling Ratio | 1514 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_Soiling Ratio | Soiling Station | MET68_MODBUS.SoilingRatio | Soiling Ratio | 1515 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_Soiling Ratio | Soiling Station | MET52_MODBUS.SoilingRatio | Soiling Ratio | 1516 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_Soiling Ratio | Soiling Station | MET12_MODBUS.SoilingRatio | Soiling Ratio | 1517 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_Soiling Ratio | Soiling Station | MET11_MODBUS.SoilingRatio | Soiling Ratio | 1518 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_Soiling Ratio | Soiling Station | MET65_MODBUS.SoilingRatio | Soiling Ratio | 1519 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_Soiling Ratio | Soiling Station | MET44_MODBUS.SoilingRatio | Soiling Ratio | 1520 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_Soiling Ratio | Soiling Station | MET50_MODBUS.SoilingRatio | Soiling Ratio | 1521 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_Soiling Ratio | Soiling Station | MET19_MODBUS.SoilingRatio | Soiling Ratio | 1522 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_Soiling Ratio | Soiling Station | MET08_MODBUS.SoilingRatio | Soiling Ratio | 1523 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_Soiling Ratio | Soiling Station | MET23_MODBUS.SoilingRatio | Soiling Ratio | 1524 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_Soiling Ratio | Soiling Station | MET34_MODBUS.SoilingRatio | Soiling Ratio | 1525 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_Soiling Ratio | Soiling Station | MET31_MODBUS.SoilingRatio | Soiling Ratio | 1526 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_Soiling Ratio | Soiling Station | MET42_MODBUS.SoilingRatio | Soiling Ratio | 1527 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_Transmission Loss | Soiling Station | MET94_MODBUS.TransmissionLoss | Transmission Loss | 1528 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_Transmission Loss | Soiling Station | MET87_MODBUS.TransmissionLoss | Transmission Loss | 1529 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_Transmission Loss | Soiling Station | MET83_MODBUS.TransmissionLoss | Transmission Loss | 1530 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_Transmission Loss | Soiling Station | MET75_MODBUS.TransmissionLoss | Transmission Loss | 1531 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_Transmission Loss | Soiling Station | MET68_MODBUS.TransmissionLoss | Transmission Loss | 1532 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_Transmission Loss | Soiling Station | MET52_MODBUS.TransmissionLoss | Transmission Loss | 1533 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_Transmission Loss | Soiling Station | MET12_MODBUS.TransmissionLoss | Transmission Loss | 1534 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_Transmission Loss | Soiling Station | MET11_MODBUS.TransmissionLoss | Transmission Loss | 1535 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_Transmission Loss | Soiling Station | MET65_MODBUS.TransmissionLoss | Transmission Loss | 1536 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_Transmission Loss | Soiling Station | MET44_MODBUS.TransmissionLoss | Transmission Loss | 1537 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_Transmission Loss | Soiling Station | MET50_MODBUS.TransmissionLoss | Transmission Loss | 1538 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_Transmission Loss | Soiling Station | MET19_MODBUS.TransmissionLoss | Transmission Loss | 1539 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_Transmission Loss | Soiling Station | MET08_MODBUS.TransmissionLoss | Transmission Loss | 1540 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_Transmission Loss | Soiling Station | MET23_MODBUS.TransmissionLoss | Transmission Loss | 1541 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_Transmission Loss | Soiling Station | MET34_MODBUS.TransmissionLoss | Transmission Loss | 1542 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_Transmission Loss | Soiling Station | MET31_MODBUS.TransmissionLoss | Transmission Loss | 1543 | % | Requested-Available | 0 | 100 | 1
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_Transmission Loss | Soiling Station | MET42_MODBUS.TransmissionLoss | Transmission Loss | 1544 | % | Requested-Available | 0 | 100 | 1
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Real Power-AC | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0000_Real_Power_AC | AC Real Power | 1545 | MW | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Reactive Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0001_Reactive_Power | AC Reactive Power | 1546 | MVAR | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0002_Power_Factor | Power Factor | 1547 | Unitless | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage A-B | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0003_Voltage_A_B | Phase-Phase Voltages | 1548 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage B-C | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0004_Voltage_B_C | Phase-Phase Voltages | 1549 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage C-A | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0005_Voltage_C_A | Phase-Phase Voltages | 1550 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Current | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0006_Current_A | Phase Currents | 1551 | A | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Current | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0007_Current_B | Phase Currents | 1552 | A | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Current | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0008_Current_C | Phase Currents | 1553 | A | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Frequency | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0009_Frequency | Frequency | 1554 | Hz | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0010_A_Phase_Power | Phase Power | 1555 | MW | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0011_B_Phase_Power | Phase Power | 1556 | MW | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0012_C_Phase_Power | Phase Power | 1557 | MW | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage A-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0013_Voltage_A_N | L-N Phase Voltages | 1558 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage B-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0014_Voltage_B_N | L-N Phase Voltages | 1559 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Voltage C-N | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0015_Voltage_C_N | L-N Phase Voltages | 1560 | kV | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0016_A_Phase_Apparent_Power | Phase Apparent Power | 1561 | MVA | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0017_B_Phase_Apparent_Power | Phase Apparent Power | 1562 | MVA | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Apparent Power | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0018_C_Phase_Apparent_Power | Phase Apparent Power | 1563 | MVA | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_A Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0019_A_Phase_Power_Factor | Phase Power Factor | 1564 | Unitless | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_B Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0020_B_Phase_Power_Factor | Phase Power Factor | 1565 | Unitless | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_C Phase Power Factor | Line Relay | GE_L90_87L1P_DNP.Analog_Input_0021_C_Phase_Power_Factor | Phase Power Factor | 1566 | Unitless | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Real Power-AC | Line Relay | SEL_411L_87L1S_SEL.F_METER2_P | AC Real Power | 1567 | MW | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Reactive Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_Q | AC Reactive Power | 1568 | MVAR | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PF | Power Factor | 1569 | Unitless | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage A-B | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VAB | Phase-Phase Voltages | 1570 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage B-C | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VBC | Phase-Phase Voltages | 1571 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage C-A | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VCA | Phase-Phase Voltages | 1572 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Current | Line Relay | SEL_411L_87L1S_SEL.FM_INST_IAB | Phase Currents | 1573 | A | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Current | Line Relay | SEL_411L_87L1S_SEL.FM_INST_IBC | Phase Currents | 1574 | A | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Current | Line Relay | SEL_411L_87L1S_SEL.FM_INST_ICA | Phase Currents | 1575 | A | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Frequency | Line Relay | SEL_411L_87L1S_SEL.FM_INST_FREQ | Frequency | 1576 | Hz | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PA | Phase Power | 1577 | MW | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PB | Phase Power | 1578 | MW | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PC | Phase Power | 1579 | MW | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage A-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VA | L-N Phase Voltages | 1580 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage B-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VB | L-N Phase Voltages | 1581 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Voltage C-N | Line Relay | SEL_411L_87L1S_SEL.FM_INST_VC | L-N Phase Voltages | 1582 | kV | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SA | Phase Apparent Power | 1583 | MVA | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SB | Phase Apparent Power | 1584 | MVA | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Apparent Power | Line Relay | SEL_411L_87L1S_SEL.F_METER2_SC | Phase Apparent Power | 1585 | MVA | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_A Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFA | Phase Power Factor | 1586 | Unitless | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_B Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFB | Phase Power Factor | 1587 | Unitless | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_C Phase Power Factor | Line Relay | SEL_411L_87L1S_SEL.F_METER2_PFC | Phase Power Factor | 1588 | Unitless | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Real Power-AC | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0000_Real_Power_AC | AC Real Power | 1589 | MW | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Reactive Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0001_Reactive_Power | AC Reactive Power | 1590 | MVAR | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0002_Power_Factor | Power Factor | 1591 | Unitless | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage A-B | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0003_Voltage_A_B | Phase-Phase Voltages | 1592 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage B-C | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0004_Voltage_B_C | Phase-Phase Voltages | 1593 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage C-A | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0005_Voltage_C_A | Phase-Phase Voltages | 1594 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Current | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0006_Current_A | Phase Currents | 1595 | A | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Current | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0007_Current_B | Phase Currents | 1596 | A | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Current | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0008_Current_C | Phase Currents | 1597 | A | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Frequency | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0009_Frequency | Frequency | 1598 | Hz | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0010_A_Phase_Power | Phase Power | 1599 | MW | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0011_B_Phase_Power | Phase Power | 1600 | MW | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0012_C_Phase_Power | Phase Power | 1601 | MW | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage A-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0013_Voltage_A_N | L-N Phase Voltages | 1602 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage B-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0014_Voltage_B_N | L-N Phase Voltages | 1603 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Voltage C-N | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0015_Voltage_C_N | L-N Phase Voltages | 1604 | kV | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0016_A_Phase_Apparent_Power | Phase Apparent Power | 1605 | MVA | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0017_B_Phase_Apparent_Power | Phase Apparent Power | 1606 | MVA | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Apparent Power | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0018_C_Phase_Apparent_Power | Phase Apparent Power | 1607 | MVA | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_A Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0019_A_Phase_Power_Factor | Phase Power Factor | 1608 | Unitless | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_B Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0020_B_Phase_Power_Factor | Phase Power Factor | 1609 | Unitless | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_C Phase Power Factor | Line Relay | GE_L90_87L2P_DNP.Analog_Input_0021_C_Phase_Power_Factor | Phase Power Factor | 1610 | Unitless | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Real Power-AC | Line Relay | SEL_411L_87L2S_SEL.F_METER2_P | AC Real Power | 1611 | MW | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Reactive Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_Q | AC Reactive Power | 1612 | MVAR | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PF | Power Factor | 1613 | Unitless | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage A-B | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VAB | Phase-Phase Voltages | 1614 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage B-C | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VBC | Phase-Phase Voltages | 1615 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage C-A | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VCA | Phase-Phase Voltages | 1616 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Current | Line Relay | SEL_411L_87L2S_SEL.FM_INST_IAB | Phase Currents | 1617 | A | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Current | Line Relay | SEL_411L_87L2S_SEL.FM_INST_IBC | Phase Currents | 1618 | A | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Current | Line Relay | SEL_411L_87L2S_SEL.FM_INST_ICA | Phase Currents | 1619 | A | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Frequency | Line Relay | SEL_411L_87L2S_SEL.FM_INST_FREQ | Frequency | 1620 | Hz | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PA | Phase Power | 1621 | MW | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PB | Phase Power | 1622 | MW | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PC | Phase Power | 1623 | MW | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage A-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VA | L-N Phase Voltages | 1624 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage B-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VB | L-N Phase Voltages | 1625 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Voltage C-N | Line Relay | SEL_411L_87L2S_SEL.FM_INST_VC | L-N Phase Voltages | 1626 | kV | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SA | Phase Apparent Power | 1627 | MVA | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SB | Phase Apparent Power | 1628 | MVA | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Apparent Power | Line Relay | SEL_411L_87L2S_SEL.F_METER2_SC | Phase Apparent Power | 1629 | MVA | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_A Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFA | Phase Power Factor | 1630 | Unitless | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_B Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFB | Phase Power Factor | 1631 | Unitless | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_C Phase Power Factor | Line Relay | SEL_411L_87L2S_SEL.F_METER2_PFC | Phase Power Factor | 1632 | Unitless | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Real Power-AC | Transformer Relay | SEL_487E_87T1P_SEL.FPP_3_004 | AC Real Power | 1633 | MW | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_4_004 | AC Reactive Power | 1634 | MVAR | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_004 | Power Factor | 1635 | Unitless | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage A-B | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1636 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage B-C | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1637 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage C-A | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1638 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Current | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY1 | Phase Currents | 1639 | A | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Current | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY2 | Phase Currents | 1640 | A | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Current | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_IY3 | Phase Currents | 1641 | A | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Frequency | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_FREQ | Frequency | 1642 | Hz | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_001_PA | Phase Power | 1643 | MW | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_002_PB | Phase Power | 1644 | MW | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_003_PC | Phase Power | 1645 | MW | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage A-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VAZ | L-N Phase Voltages | 1646 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage B-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VBZ | L-N Phase Voltages | 1647 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Voltage C-N | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_VCZ | L-N Phase Voltages | 1648 | kV | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_001_SA | Phase Apparent Power | 1649 | MVA | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_002_SB | Phase Apparent Power | 1650 | MVA | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Apparent Power | Transformer Relay | SEL_487E_87T1P_SEL.FPP_2_003_SC | Phase Apparent Power | 1651 | MVA | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_001_PA | Phase Power Factor | 1652 | Unitless | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_002_PB | Phase Power Factor | 1653 | Unitless | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Power Factor | Transformer Relay | SEL_487E_87T1P_SEL.FPP_1_003_PC | Phase Power Factor | 1654 | Unitless | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Real Power-AC | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_001_P3 | AC Real Power | 1655 | MW | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_002_Q3 | AC Reactive Power | 1656 | MVAR | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Power Factor | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_003_PF3 | Power Factor | 1657 | Unitless | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage A-B | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_001_VAB | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage B-C | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_002_VBC | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage C-A | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_003_VCA | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Current | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IA1 | Phase Currents | 1658 | A | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Current | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IB1 | Phase Currents | 1659 | A | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Current | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_IC1 | Phase Currents | 1660 | A | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Frequency | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_FREQ | Frequency | 1661 | Hz | Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_001_PA | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_002_PB | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_1_003_PC | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage A-N | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_001_VA | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage B-N | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_002_VB | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Voltage C-N | Transformer Relay | SEL_387A_87T1S_SEL.FPP_2_003_VC | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Apparent Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_3_001_SA | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Apparent Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_3_002_SB | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Apparent Power | Transformer Relay | SEL_387A_87T1S_SEL.FPP_3_003_SC | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Power Factor | Transformer Relay | SEL_387A_87T1S_SEL.FPP_4_001_PA | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Power Factor | Transformer Relay | SEL_387A_87T1S_SEL.FPP_4_002_PB | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Power Factor | Transformer Relay | SEL_387A_87T1S_SEL.FPP_4_003_PC | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Real Power-AC | Transformer Relay | SEL_487E_87T2P_SEL.FPP_3_004 | AC Real Power | 1662 | MW | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_4_004 | AC Reactive Power | 1663 | MVAR | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_004 | Power Factor | 1664 | Unitless | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage A-B | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VABZ | Phase-Phase Voltages | 1665 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage B-C | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VBCZ | Phase-Phase Voltages | 1666 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage C-A | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VCAZ | Phase-Phase Voltages | 1667 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Current | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY1 | Phase Currents | 1668 | A | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Current | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY2 | Phase Currents | 1669 | A | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Current | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_IY3 | Phase Currents | 1670 | A | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Frequency | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_FREQ | Frequency | 1671 | Hz | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_001_PA | Phase Power | 1672 | MW | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_002_PB | Phase Power | 1673 | MW | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_003_PC | Phase Power | 1674 | MW | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage A-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VAZ | L-N Phase Voltages | 1675 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage B-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VBZ | L-N Phase Voltages | 1676 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Voltage C-N | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_VCZ | L-N Phase Voltages | 1677 | kV | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_001_SA | Phase Apparent Power | 1678 | MVA | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_002_SB | Phase Apparent Power | 1679 | MVA | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Apparent Power | Transformer Relay | SEL_487E_87T2P_SEL.FPP_2_003_SC | Phase Apparent Power | 1680 | MVA | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_001_PA | Phase Power Factor | 1681 | Unitless | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_002_PB | Phase Power Factor | 1682 | Unitless | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Power Factor | Transformer Relay | SEL_487E_87T2P_SEL.FPP_1_003_PC | Phase Power Factor | 1683 | Unitless | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Real Power-AC | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_001_P3 | AC Real Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_002_Q3 | AC Reactive Power |  | MVAR | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Power Factor | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_003_PF3 | Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage A-B | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_001_VAB | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage B-C | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_002_VBC | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage C-A | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_003_VCA | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Current | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IA1 | Phase Currents | 1684 | A | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Current | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IB1 | Phase Currents | 1685 | A | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Current | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IC1 | Phase Currents | 1686 | A | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Frequency | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_FREQ | Frequency | 1687 | Hz | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_001_PA | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_002_PB | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_1_003_PC | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage A-N | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_001_VA | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage B-N | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_002_VB | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Voltage C-N | Transformer Relay | SEL_387A_87T2S_SEL.FPP_2_003_VC | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Apparent Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_3_001_SA | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Apparent Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_3_002_SB | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Apparent Power | Transformer Relay | SEL_387A_87T2S_SEL.FPP_3_003_SC | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Power Factor | Transformer Relay | SEL_387A_87T2S_SEL.FPP_4_001_PA | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Power Factor | Transformer Relay | SEL_387A_87T2S_SEL.FPP_4_002_PB | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Power Factor | Transformer Relay | SEL_387A_87T2S_SEL.FPP_4_003_PC | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Real Power-AC | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_P_WATTS | AC Real Power | 1688 | MW | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Reactive Power | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_Q_VARS | AC Reactive Power | 1689 | MVAR | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Power Factor | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_1_004_P3 | Power Factor | 1690 | Unitless | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage A-B | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VAB | Phase-Phase Voltages | 1691 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage B-C | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VBC | Phase-Phase Voltages | 1692 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage C-A | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VCA | Phase-Phase Voltages | 1693 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Current | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_IA | Phase Currents | 1694 | A | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Current | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_IB | Phase Currents | 1695 | A | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Current | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_IC | Phase Currents | 1696 | A | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Frequency | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_FREQ | Frequency | 1697 | Hz | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Power | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_PA_WATTS | Phase Power | 1698 | MW | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Power | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_PB_WATTS | Phase Power | 1699 | MW | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Power | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_PC_WATTS | Phase Power | 1700 | MW | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage A-N | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VA | L-N Phase Voltages | 1701 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage B-N | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VB | L-N Phase Voltages | 1702 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Voltage C-N | Breaker Relay | SEL_351S-50BFL1_SEL.FM_INST_VC | L-N Phase Voltages | 1703 | kV | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Apparent Power | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_2_001_SA | Phase Apparent Power | 1704 | MVA | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Apparent Power | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_2_002_SB | Phase Apparent Power | 1705 | MVA | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Apparent Power | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_2_003_SC | Phase Apparent Power | 1706 | MVA | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Power Factor | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_1_001_PFA | Phase Power Factor | 1707 | Unitless | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Power Factor | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_1_002_PFB | Phase Power Factor | 1708 | Unitless | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Power Factor | Breaker Relay | SEL_351S-50BFL1_SEL.FPP_1_003_PFC | Phase Power Factor | 1709 | Unitless | Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Real Power-AC | Breaker Relay |  | AC Real Power |  | MW | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Reactive Power | Breaker Relay |  | AC Reactive Power |  | MVAR | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Power Factor | Breaker Relay |  | Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage A-B | Breaker Relay |  | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage B-C | Breaker Relay |  | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage C-A | Breaker Relay |  | Phase-Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Current | Breaker Relay |  | Phase Currents |  | A | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Current | Breaker Relay |  | Phase Currents |  | A | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Current | Breaker Relay |  | Phase Currents |  | A | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Frequency | Breaker Relay |  | Frequency |  | Hz | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Power | Breaker Relay |  | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Power | Breaker Relay |  | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Power | Breaker Relay |  | Phase Power |  | MW | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage A-N | Breaker Relay |  | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage B-N | Breaker Relay |  | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Voltage C-N | Breaker Relay |  | L-N Phase Voltages |  | kV | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Apparent Power | Breaker Relay |  | Phase Apparent Power |  | MVA | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Power Factor | Breaker Relay |  | Phase Power Factor |  | Unitless | Requested-Not Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Real Power-AC | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_P_WATTS | AC Real Power | 1710 | MW | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Reactive Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_Q_VARS | AC Reactive Power | 1711 | MVAR | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Power Factor | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_004_P3 | Power Factor | 1712 | Unitless | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage A-B | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VAB | Phase-Phase Voltages | 1713 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage B-C | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VBC | Phase-Phase Voltages | 1714 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage C-A | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VCA | Phase-Phase Voltages | 1715 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Current | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IA | Phase Currents | 1716 | A | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Current | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IB | Phase Currents | 1717 | A | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Current | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IC | Phase Currents | 1718 | A | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Frequency | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_FREQ | Frequency | 1719 | Hz | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PA_WATTS | Phase Power | 1720 | MW | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PB_WATTS | Phase Power | 1721 | MW | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Power | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_PC_WATTS | Phase Power | 1722 | MW | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage A-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VA | L-N Phase Voltages | 1723 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage B-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VB | L-N Phase Voltages | 1724 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Voltage C-N | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_VC | L-N Phase Voltages | 1725 | kV | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Apparent Power | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_001_SA | Phase Apparent Power | 1726 | MVA | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Apparent Power | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_002_SB | Phase Apparent Power | 1727 | MVA | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Apparent Power | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_003_SC | Phase Apparent Power | 1728 | MVA | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Power Factor | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_001_PFA | Phase Power Factor | 1729 | Unitless | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Power Factor | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_002_PFB | Phase Power Factor | 1730 | Unitless | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Power Factor | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_003_PFC | Phase Power Factor | 1731 | Unitless | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Real Power-AC | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_P_WATTS | AC Real Power | 1732 | MW | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Reactive Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_Q_VARS | AC Reactive Power | 1733 | MVAR | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Power Factor | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_004_P3 | Power Factor | 1734 | Unitless | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage A-B | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VAB | Phase-Phase Voltages | 1735 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage B-C | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VBC | Phase-Phase Voltages | 1736 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage C-A | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VCA | Phase-Phase Voltages | 1737 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Current | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IA | Phase Currents | 1738 | A | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Current | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IB | Phase Currents | 1739 | A | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Current | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IC | Phase Currents | 1740 | A | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Frequency | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_FREQ | Frequency | 1741 | Hz | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PA_WATTS | Phase Power | 1742 | MW | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PB_WATTS | Phase Power | 1743 | MW | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Power | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_PC_WATTS | Phase Power | 1744 | MW | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage A-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VA | L-N Phase Voltages | 1745 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage B-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VB | L-N Phase Voltages | 1746 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Voltage C-N | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_VC | L-N Phase Voltages | 1747 | kV | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Apparent Power | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_001_SSA | Phase Apparent Power | 1748 | MVA | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Apparent Power | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_002_SSB | Phase Apparent Power | 1749 | MVA | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Apparent Power | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_003_SSC | Phase Apparent Power | 1750 | MVA | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Power Factor | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_001_PFA | Phase Power Factor | 1751 | Unitless | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Power Factor | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_002_PFB | Phase Power Factor | 1752 | Unitless | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Power Factor | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_003_PFC | Phase Power Factor | 1753 | Unitless | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Real Power-AC | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_P_WATTS | AC Real Power | 1754 | MW | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Reactive Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_Q_VARS | AC Reactive Power | 1755 | MVAR | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Power Factor | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_004_P3 | Power Factor | 1756 | Unitless | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage A-B | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VAB | Phase-Phase Voltages | 1757 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage B-C | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VBC | Phase-Phase Voltages | 1758 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage C-A | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VCA | Phase-Phase Voltages | 1759 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _A Phase Current | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IA | Phase Currents | 1760 | A | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _B Phase Current | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IB | Phase Currents | 1761 | A | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _C Phase Current | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IC | Phase Currents | 1762 | A | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Frequency | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_FREQ | Frequency | 1763 | Hz | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _A Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PA_WATTS | Phase Power | 1764 | MW | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _B Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PB_WATTS | Phase Power | 1765 | MW | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _C Phase Power | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_PC_WATTS | Phase Power | 1766 | MW | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage A-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VA | L-N Phase Voltages | 1767 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage B-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VB | L-N Phase Voltages | 1768 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _Voltage C-N | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_VC | L-N Phase Voltages | 1769 | kV | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _A Phase Apparent Power | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_001_SSA | Phase Apparent Power | 1770 | MVA | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _B Phase Apparent Power | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_002_SSB | Phase Apparent Power | 1771 | MVA | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _C Phase Apparent Power | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_003_SSC | Phase Apparent Power | 1772 | MVA | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _A Phase Power Factor | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_001_PFA | Phase Power Factor | 1773 | Unitless | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _B Phase Power Factor | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_002_PFB | Phase Power Factor | 1774 | Unitless | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3 _C Phase Power Factor | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_003_PFC | Phase Power Factor | 1775 | Unitless | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Real Power-AC | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_P_WATTS | AC Real Power | 1776 | MW | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Reactive Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_Q_VARS | AC Reactive Power | 1777 | MVAR | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Power Factor | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_004_P3 | Power Factor | 1778 | Unitless | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage A-B | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VAB | Phase-Phase Voltages | 1779 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage B-C | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VBC | Phase-Phase Voltages | 1780 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage C-A | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VCA | Phase-Phase Voltages | 1781 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Current | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IA | Phase Currents | 1782 | A | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Current | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IB | Phase Currents | 1783 | A | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Current | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IC | Phase Currents | 1784 | A | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Frequency | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_FREQ | Frequency | 1785 | Hz | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PA_WATTS | Phase Power | 1786 | MW | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PB_WATTS | Phase Power | 1787 | MW | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Power | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_PC_WATTS | Phase Power | 1788 | MW | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage A-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VA | L-N Phase Voltages | 1789 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage B-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VB | L-N Phase Voltages | 1790 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Voltage C-N | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_VC | L-N Phase Voltages | 1791 | kV | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Apparent Power | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_001_SSA | Phase Apparent Power | 1792 | MVA | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Apparent Power | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_002_SSB | Phase Apparent Power | 1793 | MVA | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Apparent Power | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_003_SSC | Phase Apparent Power | 1794 | MVA | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Power Factor | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_001_PFA | Phase Power Factor | 1795 | Unitless | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Power Factor | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_002_PFB | Phase Power Factor | 1796 | Unitless | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Power Factor | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_003_PFC | Phase Power Factor | 1797 | Unitless | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Real Power-AC | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_P_WATTS | AC Real Power | 1798 | MW | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Reactive Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_Q_VARS | AC Reactive Power | 1799 | MVAR | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Power Factor | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_004_P3 | Power Factor | 1800 | Unitless | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage A-B | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VAB | Phase-Phase Voltages | 1801 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage B-C | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VBC | Phase-Phase Voltages | 1802 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage C-A | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VCA | Phase-Phase Voltages | 1803 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _A Phase Current | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IA | Phase Currents | 1804 | A | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _B Phase Current | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IB | Phase Currents | 1805 | A | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _C Phase Current | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IC | Phase Currents | 1806 | A | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Frequency | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_FREQ | Frequency | 1807 | Hz | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _A Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PA_WATTS | Phase Power | 1808 | MW | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _B Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PB_WATTS | Phase Power | 1809 | MW | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _C Phase Power | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_PC_WATTS | Phase Power | 1810 | MW | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage A-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VA | L-N Phase Voltages | 1811 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage B-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VB | L-N Phase Voltages | 1812 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _Voltage C-N | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_VC | L-N Phase Voltages | 1813 | kV | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _A Phase Apparent Power | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_001_SSA | Phase Apparent Power | 1814 | MVA | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _B Phase Apparent Power | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_002_SSB | Phase Apparent Power | 1815 | MVA | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _C Phase Apparent Power | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_003_SSC | Phase Apparent Power | 1816 | MVA | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _A Phase Power Factor | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_001_PFA | Phase Power Factor | 1817 | Unitless | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _B Phase Power Factor | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_002_PFB | Phase Power Factor | 1818 | Unitless | Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5 _C Phase Power Factor | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_003_PFC | Phase Power Factor | 1819 | Unitless | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Real Power-AC | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_P_WATTS | AC Real Power | 1820 | MW | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Reactive Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_Q_VARS | AC Reactive Power | 1821 | MVAR | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Power Factor | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_004_P3 | Power Factor | 1822 | Unitless | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage A-B | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VAB | Phase-Phase Voltages | 1823 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage B-C | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VBC | Phase-Phase Voltages | 1824 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage C-A | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VCA | Phase-Phase Voltages | 1825 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _A Phase Current | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IA | Phase Currents | 1826 | A | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _B Phase Current | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IB | Phase Currents | 1827 | A | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _C Phase Current | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IC | Phase Currents | 1828 | A | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Frequency | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_FREQ | Frequency | 1829 | Hz | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _A Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PA_WATTS | Phase Power | 1830 | MW | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _B Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PB_WATTS | Phase Power | 1831 | MW | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _C Phase Power | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_PC_WATTS | Phase Power | 1832 | MW | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage A-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VA | L-N Phase Voltages | 1833 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage B-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VB | L-N Phase Voltages | 1834 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _Voltage C-N | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_VC | L-N Phase Voltages | 1835 | kV | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _A Phase Apparent Power | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_001_SSA | Phase Apparent Power | 1836 | MVA | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _B Phase Apparent Power | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_002_SSB | Phase Apparent Power | 1837 | MVA | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _C Phase Apparent Power | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_003_SSC | Phase Apparent Power | 1838 | MVA | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _A Phase Power Factor | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_001_PFA | Phase Power Factor | 1839 | Unitless | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _B Phase Power Factor | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_002_PFB | Phase Power Factor | 1840 | Unitless | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6 _C Phase Power Factor | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_003_PFC | Phase Power Factor | 1841 | Unitless | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Real Power-AC | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_P_WATTS | AC Real Power | 1842 | MW | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Reactive Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_Q_VARS | AC Reactive Power | 1843 | MVAR | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Power Factor | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_004_P3 | Power Factor | 1844 | Unitless | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage A-B | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VAB | Phase-Phase Voltages | 1845 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage B-C | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VBC | Phase-Phase Voltages | 1846 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage C-A | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VCA | Phase-Phase Voltages | 1847 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Current | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IA | Phase Currents | 1848 | A | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Current | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IB | Phase Currents | 1849 | A | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Current | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IC | Phase Currents | 1850 | A | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Frequency | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_FREQ | Frequency | 1851 | Hz | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PA_WATTS | Phase Power | 1852 | MW | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PB_WATTS | Phase Power | 1853 | MW | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Power | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_PC_WATTS | Phase Power | 1854 | MW | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage A-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VA | L-N Phase Voltages | 1855 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage B-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VB | L-N Phase Voltages | 1856 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Voltage C-N | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_VC | L-N Phase Voltages | 1857 | kV | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Apparent Power | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_001_SSA | Phase Apparent Power | 1858 | MVA | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Apparent Power | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_002_SSB | Phase Apparent Power | 1859 | MVA | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Apparent Power | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_003_SSC | Phase Apparent Power | 1860 | MVA | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Power Factor | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_001_PFA | Phase Power Factor | 1861 | Unitless | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Power Factor | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_002_PFB | Phase Power Factor | 1862 | Unitless | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Power Factor | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_003_PFC | Phase Power Factor | 1863 | Unitless | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Real Power-AC | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_P_WATTS | AC Real Power | 1864 | MW | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Reactive Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_Q_VARS | AC Reactive Power | 1865 | MVAR | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Power Factor | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_004_P3 | Power Factor | 1866 | Unitless | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage A-B | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VAB | Phase-Phase Voltages | 1867 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage B-C | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VBC | Phase-Phase Voltages | 1868 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage C-A | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VCA | Phase-Phase Voltages | 1869 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Current | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IA | Phase Currents | 1870 | A | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Current | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IB | Phase Currents | 1871 | A | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Current | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IC | Phase Currents | 1872 | A | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Frequency | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_FREQ | Frequency | 1873 | Hz | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PA_WATTS | Phase Power | 1874 | MW | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PB_WATTS | Phase Power | 1875 | MW | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Power | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_PC_WATTS | Phase Power | 1876 | MW | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage A-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VA | L-N Phase Voltages | 1877 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage B-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VB | L-N Phase Voltages | 1878 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Voltage C-N | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_VC | L-N Phase Voltages | 1879 | kV | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Apparent Power | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_001_SSA | Phase Apparent Power | 1880 | MVA | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Apparent Power | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_002_SSB | Phase Apparent Power | 1881 | MVA | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Apparent Power | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_003_SSC | Phase Apparent Power | 1882 | MVA | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Power Factor | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_001_PFA | Phase Power Factor | 1883 | Unitless | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Power Factor | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_002_PFB | Phase Power Factor | 1884 | Unitless | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Power Factor | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_003_PFC | Phase Power Factor | 1885 | Unitless | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Real Power-AC | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_P_WATTS | AC Real Power | 1886 | MW | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Reactive Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_Q_VARS | AC Reactive Power | 1887 | MVAR | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Power Factor | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_004_P3 | Power Factor | 1888 | Unitless | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage A-B | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VAB | Phase-Phase Voltages | 1889 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage B-C | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VBC | Phase-Phase Voltages | 1890 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage C-A | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VCA | Phase-Phase Voltages | 1891 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Current | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IA | Phase Currents | 1892 | A | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Current | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IB | Phase Currents | 1893 | A | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Current | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IC | Phase Currents | 1894 | A | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Frequency | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_FREQ | Frequency | 1895 | Hz | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PA_WATTS | Phase Power | 1896 | MW | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PB_WATTS | Phase Power | 1897 | MW | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Power | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_PC_WATTS | Phase Power | 1898 | MW | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage A-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VA | L-N Phase Voltages | 1899 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage B-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VB | L-N Phase Voltages | 1900 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Voltage C-N | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_VC | L-N Phase Voltages | 1901 | kV | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Apparent Power | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_001_SSA | Phase Apparent Power | 1902 | MVA | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Apparent Power | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_002_SSB | Phase Apparent Power | 1903 | MVA | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Apparent Power | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_003_SSC | Phase Apparent Power | 1904 | MVA | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Power Factor | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_001_PFA | Phase Power Factor | 1905 | Unitless | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Power Factor | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_002_PFB | Phase Power Factor | 1906 | Unitless | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Power Factor | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_003_PFC | Phase Power Factor | 1907 | Unitless | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Real Power-AC | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_P_WATTS | AC Real Power | 1908 | MW | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Reactive Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_Q_VARS | AC Reactive Power | 1909 | MVAR | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Power Factor | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_004_P3 | Power Factor | 1910 | Unitless | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage A-B | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VAB | Phase-Phase Voltages | 1911 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage B-C | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VBC | Phase-Phase Voltages | 1912 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage C-A | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VCA | Phase-Phase Voltages | 1913 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Current | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IA | Phase Currents | 1914 | A | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Current | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IB | Phase Currents | 1915 | A | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Current | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IC | Phase Currents | 1916 | A | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Frequency | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_FREQ | Frequency | 1917 | Hz | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PA_WATTS | Phase Power | 1918 | MW | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PB_WATTS | Phase Power | 1919 | MW | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Power | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_PC_WATTS | Phase Power | 1920 | MW | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage A-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VA | L-N Phase Voltages | 1921 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage B-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VB | L-N Phase Voltages | 1922 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Voltage C-N | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_VC | L-N Phase Voltages | 1923 | kV | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Apparent Power | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_001_SSA | Phase Apparent Power | 1924 | MVA | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Apparent Power | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_002_SSB | Phase Apparent Power | 1925 | MVA | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Apparent Power | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_003_SSC | Phase Apparent Power | 1926 | MVA | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Power Factor | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_001_PFA | Phase Power Factor | 1927 | Unitless | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Power Factor | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_002_PFB | Phase Power Factor | 1928 | Unitless | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Power Factor | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_003_PFC | Phase Power Factor | 1929 | Unitless | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Real Power-AC | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_P_WATTS | AC Real Power | 1930 | MW | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Reactive Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_Q_VARS | AC Reactive Power | 1931 | MVAR | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Power Factor | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_004_P3 | Power Factor | 1932 | Unitless | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage A-B | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VAB | Phase-Phase Voltages | 1933 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage B-C | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VBC | Phase-Phase Voltages | 1934 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage C-A | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VCA | Phase-Phase Voltages | 1935 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Current | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IA | Phase Currents | 1936 | A | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Current | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IB | Phase Currents | 1937 | A | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Current | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IC | Phase Currents | 1938 | A | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Frequency | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_FREQ | Frequency | 1939 | Hz | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PA_WATTS | Phase Power | 1940 | MW | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PB_WATTS | Phase Power | 1941 | MW | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Power | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_PC_WATTS | Phase Power | 1942 | MW | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage A-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VA | L-N Phase Voltages | 1943 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage B-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VB | L-N Phase Voltages | 1944 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Voltage C-N | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_VC | L-N Phase Voltages | 1945 | kV | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Apparent Power | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_001_SSA | Phase Apparent Power | 1946 | MVA | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Apparent Power | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_002_SSB | Phase Apparent Power | 1947 | MVA | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Apparent Power | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_003_SSC | Phase Apparent Power | 1948 | MVA | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Power Factor | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_001_PFA | Phase Power Factor | 1949 | Unitless | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Power Factor | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_002_PFB | Phase Power Factor | 1950 | Unitless | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Power Factor | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_003_PFC | Phase Power Factor | 1951 | Unitless | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Real Power-AC | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_P_WATTS | AC Real Power | 1952 | MW | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Reactive Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_Q_VARS | AC Reactive Power | 1953 | MVAR | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Power Factor | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_004_P3 | Power Factor | 1954 | Unitless | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage A-B | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VAB | Phase-Phase Voltages | 1955 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage B-C | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VBC | Phase-Phase Voltages | 1956 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage C-A | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VCA | Phase-Phase Voltages | 1957 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Current | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IA | Phase Currents | 1958 | A | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Current | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IB | Phase Currents | 1959 | A | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Current | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IC | Phase Currents | 1960 | A | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Frequency | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_FREQ | Frequency | 1961 | Hz | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PA_WATTS | Phase Power | 1962 | MW | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PB_WATTS | Phase Power | 1963 | MW | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Power | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_PC_WATTS | Phase Power | 1964 | MW | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage A-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VA | L-N Phase Voltages | 1965 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage B-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VB | L-N Phase Voltages | 1966 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Voltage C-N | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_VC | L-N Phase Voltages | 1967 | kV | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Apparent Power | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_001_SSA | Phase Apparent Power | 1968 | MVA | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Apparent Power | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_002_SSB | Phase Apparent Power | 1969 | MVA | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Apparent Power | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_003_SSC | Phase Apparent Power | 1970 | MVA | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Power Factor | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_001_PFA | Phase Power Factor | 1971 | Unitless | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Power Factor | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_002_PFB | Phase Power Factor | 1972 | Unitless | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Power Factor | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_003_PFC | Phase Power Factor | 1973 | Unitless | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Real Power-AC | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_P_WATTS | AC Real Power | 1974 | MW | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Reactive Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_Q_VARS | AC Reactive Power | 1975 | MVAR | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Power Factor | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_004_P3 | Power Factor | 1976 | Unitless | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage A-B | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VAB | Phase-Phase Voltages | 1977 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage B-C | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VBC | Phase-Phase Voltages | 1978 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage C-A | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VCA | Phase-Phase Voltages | 1979 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Current | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IA | Phase Currents | 1980 | A | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Current | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IB | Phase Currents | 1981 | A | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Current | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IC | Phase Currents | 1982 | A | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Frequency | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_FREQ | Frequency | 1983 | Hz | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PA_WATTS | Phase Power | 1984 | MW | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PB_WATTS | Phase Power | 1985 | MW | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Power | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_PC_WATTS | Phase Power | 1986 | MW | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage A-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VA | L-N Phase Voltages | 1987 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage B-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VB | L-N Phase Voltages | 1988 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Voltage C-N | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_VC | L-N Phase Voltages | 1989 | kV | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Apparent Power | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_001_SA | Phase Apparent Power | 1990 | MVA | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Apparent Power | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_002_SB | Phase Apparent Power | 1991 | MVA | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Apparent Power | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_003_SC | Phase Apparent Power | 1992 | MVA | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Power Factor | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_001_PFA | Phase Power Factor | 1993 | Unitless | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Power Factor | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_002_PFB | Phase Power Factor | 1994 | Unitless | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Power Factor | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_003_PFC | Phase Power Factor | 1995 | Unitless | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Real Power-AC | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_P_WATTS | AC Real Power | 1996 | MW | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Reactive Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_Q_VARS | AC Reactive Power | 1997 | MVAR | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Power Factor | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_004_P3 | Power Factor | 1998 | Unitless | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage A-B | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VAB | Phase-Phase Voltages | 1999 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage B-C | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VBC | Phase-Phase Voltages | 2000 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage C-A | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VCA | Phase-Phase Voltages | 2001 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Current | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IA | Phase Currents | 2002 | A | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Current | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IB | Phase Currents | 2003 | A | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Current | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IC | Phase Currents | 2004 | A | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Frequency | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_FREQ | Frequency | 2005 | Hz | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PA_WATTS | Phase Power | 2006 | MW | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PB_WATTS | Phase Power | 2007 | MW | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Power | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_PC_WATTS | Phase Power | 2008 | MW | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage A-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VA | L-N Phase Voltages | 2009 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage B-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VB | L-N Phase Voltages | 2010 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Voltage C-N | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_VC | L-N Phase Voltages | 2011 | kV | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Apparent Power | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_001_SA | Phase Apparent Power | 2012 | MVA | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Apparent Power | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_002_SB | Phase Apparent Power | 2013 | MVA | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Apparent Power | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_003_SC | Phase Apparent Power | 2014 | MVA | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Power Factor | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_001_PFA | Phase Power Factor | 2015 | Unitless | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Power Factor | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_002_PFB | Phase Power Factor | 2016 | Unitless | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Power Factor | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_003_PFC | Phase Power Factor | 2017 | Unitless | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Real Power-AC | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_P_WATTS | AC Real Power | 2018 | MW | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Reactive Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_Q_VARS | AC Reactive Power | 2019 | MVAR | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Power Factor | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_004_P3 | Power Factor | 2020 | Unitless | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage A-B | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VAB | Phase-Phase Voltages | 2021 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage B-C | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VBC | Phase-Phase Voltages | 2022 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage C-A | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VCA | Phase-Phase Voltages | 2023 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Current | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IA | Phase Currents | 2024 | A | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Current | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IB | Phase Currents | 2025 | A | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Current | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IC | Phase Currents | 2026 | A | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Frequency | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_FREQ | Frequency | 2027 | Hz | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PA_WATTS | Phase Power | 2028 | MW | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PB_WATTS | Phase Power | 2029 | MW | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Power | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_PC_WATTS | Phase Power | 2030 | MW | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage A-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VA | L-N Phase Voltages | 2031 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage B-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VB | L-N Phase Voltages | 2032 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Voltage C-N | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_VC | L-N Phase Voltages | 2033 | kV | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Apparent Power | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_001_SA | Phase Apparent Power | 2034 | MVA | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Apparent Power | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_002_SB | Phase Apparent Power | 2035 | MVA | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Apparent Power | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_003_SC | Phase Apparent Power | 2036 | MVA | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Power Factor | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_001_PFA | Phase Power Factor | 2037 | Unitless | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Power Factor | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_002_PFB | Phase Power Factor | 2038 | Unitless | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Power Factor | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_003_PFC | Phase Power Factor | 2039 | Unitless | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Real Power-AC | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_P_WATTS | AC Real Power | 2040 | MW | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Reactive Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_Q_VARS | AC Reactive Power | 2041 | MVAR | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Power Factor | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_004_P3 | Power Factor | 2042 | Unitless | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage A-B | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VAB | Phase-Phase Voltages | 2043 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage B-C | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VBC | Phase-Phase Voltages | 2044 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage C-A | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VCA | Phase-Phase Voltages | 2045 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Current | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IA | Phase Currents | 2046 | A | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Current | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IB | Phase Currents | 2047 | A | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Current | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IC | Phase Currents | 2048 | A | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Frequency | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_FREQ | Frequency | 2049 | Hz | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PA_WATTS | Phase Power | 2050 | MW | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PB_WATTS | Phase Power | 2051 | MW | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Power | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_PC_WATTS | Phase Power | 2052 | MW | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage A-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VA | L-N Phase Voltages | 2053 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage B-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VB | L-N Phase Voltages | 2054 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Voltage C-N | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_VC | L-N Phase Voltages | 2055 | kV | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Apparent Power | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_001_SA | Phase Apparent Power | 2056 | MVA | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Apparent Power | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_002_SB | Phase Apparent Power | 2057 | MVA | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Apparent Power | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_003_SC | Phase Apparent Power | 2058 | MVA | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Power Factor | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_001_PFA | Phase Power Factor | 2059 | Unitless | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Power Factor | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_002_PFB | Phase Power Factor | 2060 | Unitless | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Power Factor | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_003_PFC | Phase Power Factor | 2061 | Unitless | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_A Phase Current | Bus Relay | SEL_587Z_87BT1_SEL..FPP_1_001 | Phase Currents | 2062 | A | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_B Phase Current | Bus Relay | SEL_587Z_87BT1_SEL..FPP_1_002 | Phase Currents | 2063 | A | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_C Phase Current | Bus Relay | SEL_587Z_87BT1_SEL..FPP_1_003 | Phase Currents | 2064 | A | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_A Phase Current | Bus Relay | SEL_587Z_87BT2_SEL..FPP_1_001 | Phase Currents | 2065 | A | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_B Phase Current | Bus Relay | SEL_587Z_87BT2_SEL..FPP_1_002 | Phase Currents | 2066 | A | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_C Phase Current | Bus Relay | SEL_587Z_87BT2_SEL..FPP_1_003 | Phase Currents | 2067 | A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_ Real Power-AC | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2068 | MW | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2069 | MVAR | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2070 | N/A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage A-B | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2071 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage B-C | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2072 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage C-A | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2073 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2074 | A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2075 | A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2076 | A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Frequency | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2077 | Hz | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2078 | % | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Current THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2079 | % | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2080 | MW | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2081 | MW | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2082 | MW | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage A-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2083 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage B-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2084 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Voltage C-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2085 | kV | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2086 | MVA | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2087 | MVA | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2088 | MVA | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2089 | N/A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2090 | N/A | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2091 | N/A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_ Real Power-AC | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2092 | MW | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2093 | MVAR | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2094 | N/A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage A-B | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2095 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage B-C | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2096 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage C-A | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2097 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2098 | A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2099 | A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Current | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2100 | A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Frequency | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2101 | Hz | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2102 | % | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Current THD | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2103 | % | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2104 | MW | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2105 | MW | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2106 | MW | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage A-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2107 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage B-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2108 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Voltage C-N | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2109 | kV | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2110 | MVA | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2111 | MVA | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Apparent Power | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2112 | MVA | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2113 | N/A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2114 | N/A | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Power Factor | Meter | SEL_735_OCM1_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2115 | N/A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_ Real Power-AC | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2116 | MW | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2117 | MVAR | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2118 | N/A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage A-B | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2119 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage B-C | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2120 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage C-A | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2121 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2122 | A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2123 | A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Current | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2124 | A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Frequency | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2125 | Hz | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage THD | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2126 | % | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Current THD | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2127 | % | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2128 | MW | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2129 | MW | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2130 | MW | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage A-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2131 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage B-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2132 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Voltage C-N | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2133 | kV | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2134 | MVA | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2135 | MVA | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Apparent Power | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2136 | MVA | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2137 | N/A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2138 | N/A | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Power Factor | Meter | SEL_735_OCM3_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2139 | N/A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_ Real Power-AC | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2140 | MW | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2141 | MVAR | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2142 | N/A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage A-B | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2143 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage B-C | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2144 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage C-A | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2145 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2146 | A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2147 | A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Current | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2148 | A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Frequency | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2149 | Hz | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage THD | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2150 | % | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Current THD | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2151 | % | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2152 | MW | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2153 | MW | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2154 | MW | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage A-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2155 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage B-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2156 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Voltage C-N | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2157 | kV | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2158 | MVA | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2159 | MVA | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Apparent Power | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2160 | MVA | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2161 | N/A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2162 | N/A | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Power Factor | Meter | SEL_735_OCM4_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2163 | N/A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_ Real Power-AC | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2164 | MW | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2165 | MVAR | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2166 | N/A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage A-B | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2167 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage B-C | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2168 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage C-A | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2169 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2170 | A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2171 | A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Current | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2172 | A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Frequency | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2173 | Hz | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage THD | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2174 | % | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Current THD | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2175 | % | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2176 | MW | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2177 | MW | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2178 | MW | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage A-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2179 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage B-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2180 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Voltage C-N | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2181 | kV | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2182 | MVA | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2183 | MVA | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Apparent Power | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2184 | MVA | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2185 | N/A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2186 | N/A | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Power Factor | Meter | SEL_735_OCM5_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2187 | N/A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_ Real Power-AC | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2188 | MW | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2189 | MVAR | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2190 | N/A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage A-B | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2191 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage B-C | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2192 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage C-A | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2193 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2194 | A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2195 | A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Current | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2196 | A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Frequency | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2197 | Hz | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage THD | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2198 | % | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Current THD | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2199 | % | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2200 | MW | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2201 | MW | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2202 | MW | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage A-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2203 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage B-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2204 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Voltage C-N | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2205 | kV | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2206 | MVA | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2207 | MVA | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Apparent Power | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2208 | MVA | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2209 | N/A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2210 | N/A | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Power Factor | Meter | SEL_735_OCM6_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2211 | N/A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_ Real Power-AC | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2212 | MW | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2213 | MVAR | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2214 | N/A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage A-B | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2215 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage B-C | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2216 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage C-A | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2217 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2218 | A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2219 | A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Current | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2220 | A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Frequency | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2221 | Hz | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage THD | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2222 | % | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Current THD | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2223 | % | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2224 | MW | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2225 | MW | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2226 | MW | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage A-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2227 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage B-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2228 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Voltage C-N | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2229 | kV | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2230 | MVA | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2231 | MVA | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Apparent Power | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2232 | MVA | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2233 | N/A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2234 | N/A | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Power Factor | Meter | SEL_735_OCM7_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2235 | N/A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_ Real Power-AC | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2236 | MW | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2237 | MVAR | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2238 | N/A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage A-B | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2239 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage B-C | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2240 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage C-A | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2241 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2242 | A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2243 | A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Current | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2244 | A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Frequency | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2245 | Hz | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage THD | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2246 | % | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Current THD | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2247 | % | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2248 | MW | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2249 | MW | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2250 | MW | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage A-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2251 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage B-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2252 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Voltage C-N | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2253 | kV | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2254 | MVA | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2255 | MVA | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Apparent Power | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2256 | MVA | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2257 | N/A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2258 | N/A | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Power Factor | Meter | SEL_735_OCM8_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2259 | N/A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_ Real Power-AC | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2260 | MW | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2261 | MVAR | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2262 | N/A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage A-B | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2263 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage B-C | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2264 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage C-A | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2265 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2266 | A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2267 | A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Current | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2268 | A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Frequency | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2269 | Hz | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage THD | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2270 | % | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Current THD | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2271 | % | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2272 | MW | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2273 | MW | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2274 | MW | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage A-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2275 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage B-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2276 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Voltage C-N | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2277 | kV | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2278 | MVA | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2279 | MVA | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Apparent Power | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2280 | MVA | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2281 | N/A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2282 | N/A | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Power Factor | Meter | SEL_735_OCM9_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2283 | N/A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_ Real Power-AC | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2284 | MW | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2285 | MVAR | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2286 | N/A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage A-B | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2287 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage B-C | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2288 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage C-A | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2289 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2290 | A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2291 | A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Current | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2292 | A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Frequency | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2293 | Hz | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage THD | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2294 | % | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Current THD | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2295 | % | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2296 | MW | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2297 | MW | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2298 | MW | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage A-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2299 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage B-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2300 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Voltage C-N | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2301 | kV | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2302 | MVA | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2303 | MVA | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Apparent Power | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2304 | MVA | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2305 | N/A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2306 | N/A | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Power Factor | Meter | SEL_735_OCM10_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2307 | N/A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_ Real Power-AC | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2308 | MW | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2309 | MVAR | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2310 | N/A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage A-B | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2311 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage B-C | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2312 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage C-A | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2313 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2314 | A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2315 | A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Current | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2316 | A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Frequency | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2317 | Hz | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage THD | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2318 | % | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Current THD | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2319 | % | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2320 | MW | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2321 | MW | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2322 | MW | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage A-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2323 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage B-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2324 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Voltage C-N | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2325 | kV | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2326 | MVA | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2327 | MVA | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Apparent Power | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2328 | MVA | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2329 | N/A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2330 | N/A | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Power Factor | Meter | SEL_735_OCM11_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2331 | N/A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_ Real Power-AC | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2332 | MW | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2333 | MVAR | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2334 | N/A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage A-B | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2335 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage B-C | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2336 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage C-A | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2337 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2338 | A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2339 | A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Current | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2340 | A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Frequency | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2341 | Hz | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage THD | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2342 | % | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Current THD | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2343 | % | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2344 | MW | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2345 | MW | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2346 | MW | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage A-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2347 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage B-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2348 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Voltage C-N | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2349 | kV | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2350 | MVA | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2351 | MVA | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Apparent Power | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2352 | MVA | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2353 | N/A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2354 | N/A | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Power Factor | Meter | SEL_735_OCM12_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2355 | N/A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_ Real Power-AC | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2356 | MW | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2357 | MVAR | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2358 | N/A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage A-B | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2359 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage B-C | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2360 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage C-A | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2361 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2362 | A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2363 | A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Current | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2364 | A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Frequency | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2365 | Hz | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage THD | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2366 | % | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Current THD | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2367 | % | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2368 | MW | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2369 | MW | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2370 | MW | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage A-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2371 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage B-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2372 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Voltage C-N | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2373 | kV | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2374 | MVA | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2375 | MVA | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Apparent Power | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2376 | MVA | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2377 | N/A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2378 | N/A | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Power Factor | Meter | SEL_735_OCM13_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2379 | N/A | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_A Phase Apparent Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00000_A_Phase_Apparent_Power | Phase Apparent Power | 2380 | MVA | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_B Phase Apparent Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00001_B_Phase_Apparent_Power | Phase Apparent Power | 2381 | MVA | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_C Phase Apparent Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00002_C_Phase_Apparent_Power | Phase Apparent Power | 2382 | MVA | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_A Phase Current | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00003_A_Phase_Current | Phase Currents | 2383 | A | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_B Phase Current | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00004_B_Phase_Current | Phase Currents | 2384 | A | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_C Phase Current | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00005_C_Phase_Current | Phase Currents | 2385 | A | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_A Phase Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00006_A_Phase_Power | Phase Power | 2386 | MW | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_B Phase Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00007_B_Phase_Power | Phase Power | 2387 | MW | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_C Phase Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00008_C_Phase_Power | Phase Power | 2388 | MW | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_A Phase Power Factor | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00009_A_Phase_Power_Factor | Phase Power Factor | 2389 | Unitless | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_B Phase Power Factor | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00010_B_Phase_Power_Factor | Phase Power Factor | 2390 | Unitless | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_C Phase Power Factor | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00011_C_Phase_Power_Factor | Phase Power Factor | 2391 | Unitless | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Power Factor | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00012_Power_Factor | Power Factor | 2392 | Unitless | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Frequency | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00013_Frequency | Frequency | 2393 | Hz | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Reactive Power | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00014_Reactive_Power | AC Reactive Power | 2394 | MVAR | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Real Power-AC | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00015_Real_Power_AC | AC Real Power | 2395 | MW | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage A-B | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00016_Voltage_A_B | Phase-Phase Voltages | 2396 | kV | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage B-C | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00017_Voltage_B_C | Phase-Phase Voltages | 2397 | kV | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage C-A | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00018_Voltage_C_A | Phase-Phase Voltages | 2398 | kV | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage A-N | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00019_Voltage_A_N | L-N Phase Voltages | 2399 | kV | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage B-N | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00020_Voltage_B_N | L-N Phase Voltages | 2400 | kV | Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Voltage C-N | Line Relay | GE_N60_CRAS_1A_DNP.ANALOG_INPUT_00021_Voltage_C_N | L-N Phase Voltages | 2401 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_A Phase Apparent Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00000_A_Phase_Apparent_Power | Phase Apparent Power | 2402 | MVA | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_B Phase Apparent Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00001_B_Phase_Apparent_Power | Phase Apparent Power | 2403 | MVA | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_C Phase Apparent Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00002_C_Phase_Apparent_Power | Phase Apparent Power | 2404 | MVA | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_A Phase Current | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00003_A_Phase_Current | Phase Currents | 2405 | A | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_B Phase Current | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00004_B_Phase_Current | Phase Currents | 2406 | A | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_C Phase Current | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00005_C_Phase_Current | Phase Currents | 2407 | A | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_A Phase Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00006_A_Phase_Power | Phase Power | 2408 | MW | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_B Phase Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00007_B_Phase_Power | Phase Power | 2409 | MW | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_C Phase Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00008_C_Phase_Power | Phase Power | 2410 | MW | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_A Phase Power Factor | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00009_A_Phase_Power_Factor | Phase Power Factor | 2411 | Unitless | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_B Phase Power Factor | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00010_B_Phase_Power_Factor | Phase Power Factor | 2412 | Unitless | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_C Phase Power Factor | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00011_C_Phase_Power_Factor | Phase Power Factor | 2413 | Unitless | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Power Factor | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00012_Power_Factor | Power Factor | 2414 | Unitless | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Frequency | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00013_Frequency | Frequency | 2415 | Hz | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Reactive Power | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00014_Reactive_Power | AC Reactive Power | 2416 | MVAR | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Real Power-AC | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00015_Real_Power_AC | AC Real Power | 2417 | MW | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage A-B | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00016_Voltage_A_B | Phase-Phase Voltages | 2418 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage B-C | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00017_Voltage_B_C | Phase-Phase Voltages | 2419 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage C-A | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00018_Voltage_C_A | Phase-Phase Voltages | 2420 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage A-N | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00019_Voltage_A_N | L-N Phase Voltages | 2421 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage B-N | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00020_Voltage_B_N | L-N Phase Voltages | 2422 | kV | Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Voltage C-N | Line Relay | GE_N60_CRAS_1B_DNP.ANALOG_INPUT_00021_Voltage_C_N | L-N Phase Voltages | 2423 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_A Phase Apparent Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00000_A_Phase_Apparent_Power | Phase Apparent Power | 2424 | MVA | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_B Phase Apparent Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00001_B_Phase_Apparent_Power | Phase Apparent Power | 2425 | MVA | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_C Phase Apparent Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00002_C_Phase_Apparent_Power | Phase Apparent Power | 2426 | MVA | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_A Phase Current | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00003_A_Phase_Current | Phase Currents | 2427 | A | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_B Phase Current | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00004_B_Phase_Current | Phase Currents | 2428 | A | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_C Phase Current | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00005_C_Phase_Current | Phase Currents | 2429 | A | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_A Phase Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00006_A_Phase_Power | Phase Power | 2430 | MW | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_B Phase Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00007_B_Phase_Power | Phase Power | 2431 | MW | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_C Phase Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00008_C_Phase_Power | Phase Power | 2432 | MW | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_A Phase Power Factor | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00009_A_Phase_Power_Factor | Phase Power Factor | 2433 | Unitless | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_B Phase Power Factor | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00010_B_Phase_Power_Factor | Phase Power Factor | 2434 | Unitless | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_C Phase Power Factor | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00011_C_Phase_Power_Factor | Phase Power Factor | 2435 | Unitless | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Power Factor | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00012_Power_Factor | Power Factor | 2436 | Unitless | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Frequency | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00013_Frequency | Frequency | 2437 | Hz | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Reactive Power | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00014_Reactive_Power | AC Reactive Power | 2438 | MVAR | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Real Power-AC | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00015_Real_Power_AC | AC Real Power | 2439 | MW | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage A-B | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00016_Voltage_A_B | Phase-Phase Voltages | 2440 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage B-C | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00017_Voltage_B_C | Phase-Phase Voltages | 2441 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage C-A | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00018_Voltage_C_A | Phase-Phase Voltages | 2442 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage A-N | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00019_Voltage_A_N | L-N Phase Voltages | 2443 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage B-N | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00020_Voltage_B_N | L-N Phase Voltages | 2444 | kV | Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Voltage C-N | Line Relay | GE_N60_RAS_1A_DNP.ANALOG_INPUT_00021_Voltage_C_N | L-N Phase Voltages | 2445 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_A Phase Apparent Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00000_A_Phase_Apparent_Power | Phase Apparent Power | 2446 | MVA | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_B Phase Apparent Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00001_B_Phase_Apparent_Power | Phase Apparent Power | 2447 | MVA | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_C Phase Apparent Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00002_C_Phase_Apparent_Power | Phase Apparent Power | 2448 | MVA | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_A Phase Current | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00003_A_Phase_Current | Phase Currents | 2449 | A | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_B Phase Current | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00004_B_Phase_Current | Phase Currents | 2450 | A | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_C Phase Current | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00005_C_Phase_Current | Phase Currents | 2451 | A | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_A Phase Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00006_A_Phase_Power | Phase Power | 2452 | MW | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_B Phase Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00007_B_Phase_Power | Phase Power | 2453 | MW | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_C Phase Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00008_C_Phase_Power | Phase Power | 2454 | MW | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_A Phase Power Factor | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00009_A_Phase_Power_Factor | Phase Power Factor | 2455 | Unitless | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_B Phase Power Factor | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00010_B_Phase_Power_Factor | Phase Power Factor | 2456 | Unitless | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_C Phase Power Factor | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00011_C_Phase_Power_Factor | Phase Power Factor | 2457 | Unitless | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Power Factor | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00012_Power_Factor | Power Factor | 2458 | Unitless | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Frequency | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00013_Frequency | Frequency | 2459 | Hz | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Reactive Power | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00014_Reactive_Power | AC Reactive Power | 2460 | MVAR | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Real Power-AC | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00015_Real_Power_AC | AC Real Power | 2461 | MW | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage A-B | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00016_Voltage_A_B | Phase-Phase Voltages | 2462 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage B-C | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00017_Voltage_B_C | Phase-Phase Voltages | 2463 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage C-A | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00018_Voltage_C_A | Phase-Phase Voltages | 2464 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage A-N | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00019_Voltage_A_N | L-N Phase Voltages | 2465 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage B-N | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00020_Voltage_B_N | L-N Phase Voltages | 2466 | kV | Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Voltage C-N | Line Relay | GE_N60_RAS_1B_DNP.ANALOG_INPUT_00021_Voltage_C_N | L-N Phase Voltages | 2467 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ CSC11 MVAR Contribution | Reactive Power Relay |  | MVAR Contribution |  | MVAR | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ CSC12 MVAR Contribution | Reactive Power Relay |  | MVAR Contribution |  | MVAR | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Real Power-AC | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_P3W | AC Real Power | 2468 | MW | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Reactive Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_Q3W | AC Reactive Power | 2469 | MVAR | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_004 | Power Factor | 2470 | Unitless | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage A-B | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VABY | Phase-Phase Voltages | 2471 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage B-C | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VBCY | Phase-Phase Voltages | 2472 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage C-A | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VCAY | Phase-Phase Voltages | 2473 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ A Phase Current | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_IAW | Phase Currents | 2474 | A | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ B Phase Current | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_IBW | Phase Currents | 2475 | A | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ C Phase Current | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_ICW | Phase Currents | 2476 | A | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_Frequency | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_FREQ | Frequency | 2477 | Hz | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ A Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PAW | Phase Power | 2478 | MW | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ B Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PBW | Phase Power | 2479 | MW | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ C Phase Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_PCW | Phase Power | 2480 | MW | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage A-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VAY | L-N Phase Voltages | 2481 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage B-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VBY | L-N Phase Voltages | 2482 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ Voltage C-N | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_VCY | L-N Phase Voltages | 2483 | kV | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ A Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SAW | Phase Apparent Power | 2484 | MVA | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ B Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SBW | Phase Apparent Power | 2485 | MVA | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ C Phase Apparent Power | Reactive Power Relay | SEL_487V_87C1_SEL.F_METER2_SCW | Phase Apparent Power | 2486 | MVA | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ A Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_001 | Phase Power Factor | 2487 | Unitless | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ B Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_002 | Phase Power Factor | 2488 | Unitless | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_ C Phase Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_003 | Phase Power Factor | 2489 | Unitless | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CAP BANK BLOCK CLOSE TIMER | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_AMV001 | Block Close Timer | 2490 | Unitless | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_ CSC21 MVAR Contribution | Reactive Power Relay |  | MVAR Contribution |  | MVAR | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Real Power-AC | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_P3W | AC Real Power | 2491 | MW | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Reactive Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_Q3W | AC Reactive Power | 2492 | MVAR | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Power Factor | Reactive Power Relay | SEL_487V_87C1_SEL.FPP_1_004 | Power Factor | 2493 | Unitless | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage A-B | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VABY | Phase-Phase Voltages | 2494 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage B-C | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VBCY | Phase-Phase Voltages | 2495 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage C-A | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VCAY | Phase-Phase Voltages | 2496 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_A Phase Current | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_IAW | Phase Currents | 2497 | A | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_B Phase Current | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_IBW | Phase Currents | 2498 | A | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_C Phase Current | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_ICW | Phase Currents | 2499 | A | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Frequency | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_FREQ | Frequency | 2500 | Hz | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_A Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PAW | Phase Power | 2501 | MW | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_B Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PBW | Phase Power | 2502 | MW | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_C Phase Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_PCW | Phase Power | 2503 | MW | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage A-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VAY | L-N Phase Voltages | 2504 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage B-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VBY | L-N Phase Voltages | 2505 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Voltage C-N | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_VCY | L-N Phase Voltages | 2506 | kV | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_A Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SAW | Phase Apparent Power | 2507 | MVA | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_B Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SBW | Phase Apparent Power | 2508 | MVA | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_C Phase Apparent Power | Reactive Power Relay | SEL_487V_87C2_SEL.F_METER2_SCW | Phase Apparent Power | 2509 | MVA | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_A Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_001 | Phase Power Factor | 2510 | Unitless | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_B Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_002 | Phase Power Factor | 2511 | Unitless | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_C Phase Power Factor | Reactive Power Relay | SEL_487V_87C2_SEL.FPP_1_003 | Phase Power Factor | 2512 | Unitless | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CAP BANK BLOCK CLOSE TIMER | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_AMV001 | Block Close Timer | 2513 | Unitless | Not Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_ Real Power-AC | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2514 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Reactive Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2515 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Power Factor | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2516 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage A-B | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2517 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage B-C | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2518 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage C-A | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2519 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Current | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2520 | A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Current | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2521 | A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Current | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2522 | A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Frequency | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2523 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage THD | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2524 | % | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Current THD | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2525 | % | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2526 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2527 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2528 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage A-N | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2529 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage B-N | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2530 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Voltage C-N | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2531 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2532 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2533 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2534 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Power Factor | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2535 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Power Factor | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2536 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Power Factor | Meter | ION_8650_CAISO_1A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2537 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_ Real Power-AC | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2538 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Reactive Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2539 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Power Factor | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2540 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage A-B | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2541 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage B-C | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2542 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage C-A | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2543 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Current | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2544 | A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Current | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2545 | A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Current | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2546 | A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Frequency | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2547 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage THD | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2548 | % | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Current THD | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2549 | % | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2550 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2551 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2552 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage A-N | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2553 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage B-N | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2554 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Voltage C-N | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2555 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2556 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2557 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2558 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Power Factor | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2559 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Power Factor | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2560 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Power Factor | Meter | ION_8650_CAISO_1B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2561 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_ Real Power-AC | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2562 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Reactive Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2563 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Power Factor | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2564 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage A-B | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2565 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage B-C | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2566 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage C-A | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2567 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Current | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2568 | A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Current | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2569 | A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Current | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2570 | A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Frequency | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2571 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage THD | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2572 | % | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Current THD | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2573 | % | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2574 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2575 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2576 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage A-N | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2577 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage B-N | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2578 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Voltage C-N | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2579 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Apparent Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2580 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Apparent Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2581 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Apparent Power | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2582 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Power Factor | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2583 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Power Factor | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2584 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Power Factor | Meter | ION_8650_CAISO_1C_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2585 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_ Real Power-AC | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2586 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Reactive Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2587 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Power Factor | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2588 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage A-B | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2589 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage B-C | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2590 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage C-A | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2591 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Current | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2592 | A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Current | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2593 | A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Current | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2594 | A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Frequency | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2595 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage THD | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2596 | % | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Current THD | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2597 | % | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2598 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2599 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2600 | MW | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage A-N | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2601 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage B-N | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2602 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Voltage C-N | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2603 | kV | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Apparent Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2604 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Apparent Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2605 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Apparent Power | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2606 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Power Factor | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2607 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Power Factor | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2608 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Power Factor | Meter | ION_8650_CAISO_1D_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2609 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_ Real Power-AC | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2610 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Reactive Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2611 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Power Factor | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2612 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage A-B | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2613 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage B-C | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2614 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage C-A | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2615 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Current | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2616 | A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Current | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2617 | A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Current | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2618 | A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Frequency | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2619 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage THD | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2620 | % | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Current THD | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2621 | % | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2622 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2623 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2624 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage A-N | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2625 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage B-N | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2626 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Voltage C-N | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2627 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2628 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2629 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2630 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Power Factor | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2631 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Power Factor | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2632 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Power Factor | Meter | ION_8650_CAISO_2A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2633 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_ Real Power-AC | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2634 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Reactive Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2635 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Power Factor | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2636 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage A-B | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2637 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage B-C | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2638 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage C-A | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2639 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Current | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2640 | A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Current | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2641 | A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Current | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2642 | A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Frequency | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2643 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage THD | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2644 | % | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Current THD | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2645 | % | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2646 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2647 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2648 | MW | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage A-N | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2649 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage B-N | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2650 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Voltage C-N | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2651 | kV | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2652 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2653 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2654 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Power Factor | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2655 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Power Factor | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2656 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Power Factor | Meter | ION_8650_CAISO_2B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2657 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_ Real Power-AC | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2658 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Reactive Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2659 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Power Factor | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2660 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage A-B | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2661 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage B-C | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2662 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage C-A | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2663 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Current | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2664 | A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Current | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2665 | A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Current | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2666 | A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Frequency | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2667 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage THD | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2668 | % | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Current THD | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2669 | % | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2670 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2671 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2672 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage A-N | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2673 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage B-N | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2674 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Voltage C-N | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2675 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2676 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2677 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2678 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Power Factor | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2679 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Power Factor | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2680 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Power Factor | Meter | ION_8650_CAISO_3A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2681 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_ Real Power-AC | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2682 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Reactive Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2683 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Power Factor | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2684 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage A-B | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2685 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage B-C | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2686 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage C-A | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2687 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Current | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2688 | A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Current | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2689 | A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Current | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2690 | A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Frequency | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2691 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage THD | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2692 | % | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Current THD | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2693 | % | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2694 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2695 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2696 | MW | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage A-N | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2697 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage B-N | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2698 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Voltage C-N | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2699 | kV | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2700 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2701 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2702 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Power Factor | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2703 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Power Factor | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2704 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Power Factor | Meter | ION_8650_CAISO_3B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2705 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_ Real Power-AC | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2706 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Reactive Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2707 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Power Factor | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2708 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage A-B | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2709 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage B-C | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2710 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage C-A | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2711 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Current | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2712 | A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Current | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2713 | A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Current | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2714 | A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Frequency | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2715 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage THD | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2716 | % | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Current THD | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2717 | % | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2718 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2719 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2720 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage A-N | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2721 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage B-N | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2722 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Voltage C-N | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2723 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2724 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2725 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2726 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Power Factor | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2727 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Power Factor | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2728 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Power Factor | Meter | ION_8650_CAISO_4A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2729 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_ Real Power-AC | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2730 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Reactive Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2731 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Power Factor | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2732 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage A-B | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2733 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage B-C | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2734 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage C-A | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2735 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Current | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2736 | A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Current | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2737 | A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Current | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2738 | A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Frequency | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2739 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage THD | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2740 | % | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Current THD | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2741 | % | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2742 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2743 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2744 | MW | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage A-N | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2745 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage B-N | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2746 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Voltage C-N | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2747 | kV | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2748 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2749 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2750 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Power Factor | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2751 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Power Factor | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2752 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Power Factor | Meter | ION_8650_CAISO_4B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2753 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_ Real Power-AC | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2754 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Reactive Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2755 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Power Factor | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2756 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage A-B | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2757 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage B-C | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2758 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage C-A | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2759 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Current | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2760 | A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Current | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2761 | A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Current | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2762 | A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Frequency | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2763 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage THD | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2764 | % | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Current THD | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2765 | % | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2766 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2767 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2768 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage A-N | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2769 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage B-N | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2770 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Voltage C-N | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2771 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2772 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2773 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2774 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Power Factor | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2775 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Power Factor | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2776 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Power Factor | Meter | ION_8650_CAISO_5A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2777 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_ Real Power-AC | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2778 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Reactive Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2779 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Power Factor | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2780 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage A-B | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2781 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage B-C | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2782 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage C-A | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2783 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Current | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2784 | A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Current | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2785 | A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Current | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2786 | A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Frequency | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2787 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage THD | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2788 | % | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Current THD | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2789 | % | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2790 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2791 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2792 | MW | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage A-N | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2793 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage B-N | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2794 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Voltage C-N | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2795 | kV | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2796 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2797 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2798 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Power Factor | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2799 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Power Factor | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2800 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Power Factor | Meter | ION_8650_CAISO_5B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2801 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_ Real Power-AC | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2802 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Reactive Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2803 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Power Factor | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2804 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage A-B | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2805 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage B-C | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2806 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage C-A | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2807 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Current | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2808 | A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Current | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2809 | A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Current | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2810 | A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Frequency | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2811 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage THD | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2812 | % | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Current THD | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2813 | % | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2814 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2815 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2816 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage A-N | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2817 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage B-N | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2818 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Voltage C-N | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2819 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2820 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2821 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2822 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Power Factor | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2823 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Power Factor | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2824 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Power Factor | Meter | ION_8650_CAISO_6A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2825 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_ Real Power-AC | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2826 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Reactive Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2827 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Power Factor | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2828 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage A-B | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2829 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage B-C | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2830 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage C-A | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2831 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Current | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2832 | A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Current | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2833 | A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Current | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2834 | A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Frequency | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2835 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage THD | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2836 | % | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Current THD | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2837 | % | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2838 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2839 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2840 | MW | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage A-N | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2841 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage B-N | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2842 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Voltage C-N | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2843 | kV | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2844 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2845 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2846 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Power Factor | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2847 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Power Factor | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2848 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Power Factor | Meter | ION_8650_CAISO_6B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2849 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_ Real Power-AC | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2850 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Reactive Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2851 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Power Factor | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2852 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage A-B | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2853 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage B-C | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2854 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage C-A | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2855 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Current | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2856 | A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Current | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2857 | A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Current | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2858 | A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Frequency | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2859 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage THD | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2860 | % | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Current THD | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2861 | % | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2862 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2863 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2864 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage A-N | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2865 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage B-N | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2866 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Voltage C-N | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2867 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2868 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2869 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2870 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Power Factor | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2871 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Power Factor | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2872 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Power Factor | Meter | ION_8650_CAISO_7A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2873 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_ Real Power-AC | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2874 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Reactive Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2875 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Power Factor | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2876 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage A-B | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2877 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage B-C | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2878 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage C-A | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2879 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Current | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2880 | A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Current | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2881 | A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Current | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2882 | A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Frequency | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2883 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage THD | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2884 | % | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Current THD | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2885 | % | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2886 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2887 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2888 | MW | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage A-N | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2889 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage B-N | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2890 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Voltage C-N | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2891 | kV | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2892 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2893 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2894 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Power Factor | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2895 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Power Factor | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2896 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Power Factor | Meter | ION_8650_CAISO_7B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2897 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_ Real Power-AC | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2898 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Reactive Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2899 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Power Factor | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2900 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage A-B | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2901 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage B-C | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2902 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage C-A | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2903 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Current | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2904 | A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Current | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2905 | A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Current | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2906 | A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Frequency | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2907 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage THD | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2908 | % | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Current THD | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2909 | % | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2910 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2911 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2912 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage A-N | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2913 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage B-N | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2914 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Voltage C-N | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2915 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2916 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2917 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2918 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Power Factor | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2919 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Power Factor | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2920 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Power Factor | Meter | ION_8650_CAISO_8A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2921 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_ Real Power-AC | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2922 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Reactive Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2923 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Power Factor | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2924 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage A-B | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2925 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage B-C | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2926 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage C-A | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2927 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Current | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2928 | A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Current | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2929 | A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Current | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2930 | A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Frequency | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2931 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage THD | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2932 | % | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Current THD | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2933 | % | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2934 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2935 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2936 | MW | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage A-N | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2937 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage B-N | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2938 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Voltage C-N | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2939 | kV | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2940 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2941 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2942 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Power Factor | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2943 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Power Factor | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2944 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Power Factor | Meter | ION_8650_CAISO_8B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2945 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_ Real Power-AC | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2946 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Reactive Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2947 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Power Factor | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2948 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage A-B | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2949 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage B-C | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2950 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage C-A | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2951 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Current | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2952 | A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Current | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2953 | A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Current | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2954 | A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Frequency | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2955 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage THD | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2956 | % | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Current THD | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2957 | % | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2958 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2959 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2960 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage A-N | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2961 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage B-N | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2962 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Voltage C-N | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2963 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2964 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2965 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2966 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Power Factor | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2967 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Power Factor | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2968 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Power Factor | Meter | ION_8650_CAISO_9A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2969 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_ Real Power-AC | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2970 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Reactive Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2971 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Power Factor | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2972 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage A-B | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2973 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage B-C | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2974 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage C-A | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2975 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Current | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 2976 | A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Current | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 2977 | A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Current | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 2978 | A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Frequency | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 2979 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage THD | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 2980 | % | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Current THD | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 2981 | % | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 2982 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 2983 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 2984 | MW | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage A-N | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2985 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage B-N | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2986 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Voltage C-N | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 2987 | kV | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 2988 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 2989 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 2990 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Power Factor | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 2991 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Power Factor | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 2992 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Power Factor | Meter | ION_8650_CAISO_9B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 2993 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_ Real Power-AC | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 2994 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Reactive Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 2995 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Power Factor | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 2996 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage A-B | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2997 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage B-C | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2998 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage C-A | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 2999 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Current | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3000 | A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Current | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3001 | A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Current | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3002 | A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Frequency | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3003 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage THD | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3004 | % | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Current THD | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3005 | % | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3006 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3007 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3008 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage A-N | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3009 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage B-N | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3010 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Voltage C-N | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3011 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3012 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3013 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3014 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Power Factor | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3015 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Power Factor | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3016 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Power Factor | Meter | ION_8650_CAISO_10A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3017 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_ Real Power-AC | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3018 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Reactive Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3019 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Power Factor | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3020 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage A-B | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3021 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage B-C | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3022 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage C-A | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3023 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Current | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3024 | A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Current | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3025 | A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Current | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3026 | A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Frequency | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3027 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage THD | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3028 | % | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Current THD | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3029 | % | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3030 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3031 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3032 | MW | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage A-N | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3033 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage B-N | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3034 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Voltage C-N | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3035 | kV | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3036 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3037 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3038 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Power Factor | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3039 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Power Factor | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3040 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Power Factor | Meter | ION_8650_CAISO_10B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3041 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_ Real Power-AC | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3042 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Reactive Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3043 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Power Factor | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3044 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage A-B | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3045 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage B-C | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3046 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage C-A | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3047 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Current | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3048 | A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Current | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3049 | A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Current | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3050 | A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Frequency | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3051 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage THD | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3052 | % | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Current THD | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3053 | % | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3054 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3055 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3056 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage A-N | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3057 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage B-N | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3058 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Voltage C-N | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3059 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3060 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3061 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3062 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Power Factor | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3063 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Power Factor | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3064 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Power Factor | Meter | ION_8650_CAISO_11A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3065 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_ Real Power-AC | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3066 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Reactive Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3067 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Power Factor | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3068 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage A-B | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3069 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage B-C | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3070 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage C-A | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3071 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Current | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3072 | A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Current | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3073 | A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Current | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3074 | A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Frequency | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3075 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage THD | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3076 | % | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Current THD | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3077 | % | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3078 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3079 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3080 | MW | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage A-N | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3081 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage B-N | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3082 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Voltage C-N | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3083 | kV | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3084 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3085 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3086 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Power Factor | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3087 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Power Factor | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3088 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Power Factor | Meter | ION_8650_CAISO_11B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3089 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_ Real Power-AC | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3090 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Reactive Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3091 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Power Factor | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3092 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage A-B | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3093 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage B-C | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3094 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage C-A | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3095 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Current | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3096 | A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Current | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3097 | A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Current | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3098 | A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Frequency | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3099 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage THD | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3100 | % | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Current THD | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3101 | % | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3102 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3103 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3104 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage A-N | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3105 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage B-N | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3106 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Voltage C-N | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3107 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3108 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3109 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3110 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Power Factor | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3111 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Power Factor | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3112 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Power Factor | Meter | ION_8650_CAISO_12A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3113 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_ Real Power-AC | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3114 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Reactive Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3115 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Power Factor | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3116 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage A-B | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3117 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage B-C | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3118 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage C-A | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3119 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Current | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3120 | A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Current | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3121 | A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Current | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3122 | A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Frequency | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3123 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage THD | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3124 | % | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Current THD | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3125 | % | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3126 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3127 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3128 | MW | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage A-N | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3129 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage B-N | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3130 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Voltage C-N | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3131 | kV | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3132 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3133 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3134 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Power Factor | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3135 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Power Factor | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3136 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Power Factor | Meter | ION_8650_CAISO_12B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3137 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_ Real Power-AC | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3138 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Reactive Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3139 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Power Factor | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3140 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage A-B | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3141 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage B-C | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3142 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage C-A | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3143 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Current | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3144 | A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Current | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3145 | A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Current | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3146 | A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Frequency | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3147 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage THD | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3148 | % | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Current THD | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3149 | % | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3150 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3151 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3152 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage A-N | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3153 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage B-N | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3154 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Voltage C-N | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3155 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Apparent Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3156 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Apparent Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3157 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Apparent Power | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3158 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Power Factor | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3159 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Power Factor | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3160 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Power Factor | Meter | ION_8650_CAISO_13A_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3161 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_ Real Power-AC | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_000_AC_REAL_POWER | AC Real Power | 3162 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Reactive Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_001_AC_REACTIVE_POWER | AC Reactive Power | 3163 | MVAR | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Power Factor | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_002_POWER_FACTOR | Power Factor | 3164 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage A-B | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_003_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3165 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage B-C | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_004_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3166 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage C-A | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_005_PHASE_PHASE_VOLTAGES | Phase-Phase Voltages | 3167 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Current | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_006_PHASE_CURRENTS | Phase Currents | 3168 | A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Current | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_007_PHASE_CURRENTS | Phase Currents | 3169 | A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Current | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_008_PHASE_CURRENTS | Phase Currents | 3170 | A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Frequency | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_009_FREQUENCY | Frequency | 3171 | Hz | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage THD | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_010_PHASE_TOTAL_HARMONIC_VOLTAGE_DISTORTION | Phase Total Harmonic Voltage Distortion | 3172 | % | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Current THD | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_011_PHASE_TOTAL_HARMONIC_CURRENT_DISTORTION | Phase Total Harmonic Current Distortion | 3173 | % | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_012_PHASE_POWER | Phase Power | 3174 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_013_PHASE_POWER | Phase Power | 3175 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_014_PHASE_POWER | Phase Power | 3176 | MW | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage A-N | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_015_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3177 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage B-N | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_016_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3178 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Voltage C-N | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_017_L_N_PHASE_VOLTAGES | L-N Phase Voltages | 3179 | kV | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Apparent Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_018_PHASE_APPARENT_POWER | Phase Apparent Power | 3180 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Apparent Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_019_PHASE_APPARENT_POWER | Phase Apparent Power | 3181 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Apparent Power | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_020_PHASE_APPARENT_POWER | Phase Apparent Power | 3182 | MVA | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Power Factor | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_021_PHASE_POWER_FACTOR | Phase Power Factor | 3183 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Power Factor | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_022_PHASE_POWER_FACTOR | Phase Power Factor | 3184 | N/A | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Power Factor | Meter | ION_8650_CAISO_13B_LS_DNP.ANALOG_INPUT_023_PHASE_POWER_FACTOR | Phase Power Factor | 3185 | N/A | Requested-Available
Digital Inputs
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19971 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 0 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 1 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 2 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 3 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 4 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 5 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 6 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Unit 21GEN19971 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 7 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Invalid GMS Unit 21GEN19971 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 8 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 9 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 10 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 11 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 12 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 13 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 14 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 15 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 16 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 17 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 18 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 19 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 20 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 21 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 22 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 23 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 24 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 25 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 26 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 27 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 28 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 29 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 30 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 3P Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 31 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Breaker Closed | PPC | PPC.bessStatus.cb52 | BESS Site Breaker Status Indicator | 32 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Relay Faulted | PPC | PPC.bessStatus.relayFault | BESS Site Protection Relay Fault Indictor | 33 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Auto Operation Enabled | PPC | PPC.bessStatus.autoOperation | BESS Site Auto-operation Indicator | 34 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Locked | PPC | PPC.bessStatus.locked | BESS Site ESS Lock Indicator | 35 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Running | PPC | PPC.bessStatus.run | BESS Site ESS Run Indicator | 36 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Auto Start Enabled | PPC | PPC.bessStatus.autoStart | BESS Site ESS Auto-start Indicator | 37 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Remote Control Enabled | PPC | PPC.bessStatus.remoteControl | BESS Site ESS Remote Control Indicator | 38 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Warning | PPC | PPC.bessStatus.warning | BESS Site ESS Warning Indicator | 39 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Faulted | PPC | PPC.bessStatus.faulted | BESS Site ESS Fault Indicator | 40 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Locked | PPC | PPC.bessStatus.ess01_locked | BESS Site ESS Unit Lock Indicator | 41 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Running | PPC | PPC.bessStatus.ess01_run | BESS Site ESS Unit Run Indicator | 42 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Participating | PPC | PPC.bessStatus.ess01_participating | BESS Site ESS Unit Site Participation Indicator | 43 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Warning | PPC | PPC.bessStatus.ess01_warning | BESS Site ESS Unit Warning Indicator | 44 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Faulted | PPC | PPC.bessStatus.ess01_faulted | BESS Site ESS Unit Fault Indicator | 45 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Fire Warning | PPC | PPC.bessStatus.ess01_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 46 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Fire Faulted | PPC | PPC.bessStatus.ess01_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 47 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Door Warning | PPC | PPC.bessStatus.ess01_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 48 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Door Faulted | PPC | PPC.bessStatus.ess01_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 49 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Estop Faulted | PPC | PPC.bessStatus.ess01_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 50 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Locked | PPC | PPC.bessStatus.ess02_locked | BESS Site ESS Unit Lock Indicator | 51 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Running | PPC | PPC.bessStatus.ess02_run | BESS Site ESS Unit Run Indicator | 52 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Participating | PPC | PPC.bessStatus.ess02_participating | BESS Site ESS Unit Site Participation Indicator | 53 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Warning | PPC | PPC.bessStatus.ess02_warning | BESS Site ESS Unit Warning Indicator | 54 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Faulted | PPC | PPC.bessStatus.ess02_faulted | BESS Site ESS Unit Fault Indicator | 55 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Fire Warning | PPC | PPC.bessStatus.ess02_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 56 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Fire Faulted | PPC | PPC.bessStatus.ess02_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 57 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Door Warning | PPC | PPC.bessStatus.ess02_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 58 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Door Faulted | PPC | PPC.bessStatus.ess02_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 59 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Estop Faulted | PPC | PPC.bessStatus.ess02_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 60 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Locked | PPC | PPC.bessStatus.ess03_locked | BESS Site ESS Unit Lock Indicator | 61 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Running | PPC | PPC.bessStatus.ess03_run | BESS Site ESS Unit Run Indicator | 62 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Participating | PPC | PPC.bessStatus.ess03_participating | BESS Site ESS Unit Site Participation Indicator | 63 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Warning | PPC | PPC.bessStatus.ess03_warning | BESS Site ESS Unit Warning Indicator | 64 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Faulted | PPC | PPC.bessStatus.ess03_faulted | BESS Site ESS Unit Fault Indicator | 65 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Fire Warning | PPC | PPC.bessStatus.ess03_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 66 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Fire Faulted | PPC | PPC.bessStatus.ess03_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 67 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Door Warning | PPC | PPC.bessStatus.ess03_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 68 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Door Faulted | PPC | PPC.bessStatus.ess03_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 69 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Estop Faulted | PPC | PPC.bessStatus.ess03_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 70 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Locked | PPC | PPC.bessStatus.ess04_locked | BESS Site ESS Unit Lock Indicator | 71 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Running | PPC | PPC.bessStatus.ess04_run | BESS Site ESS Unit Run Indicator | 72 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Participating | PPC | PPC.bessStatus.ess04_participating | BESS Site ESS Unit Site Participation Indicator | 73 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Warning | PPC | PPC.bessStatus.ess04_warning | BESS Site ESS Unit Warning Indicator | 74 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Faulted | PPC | PPC.bessStatus.ess04_faulted | BESS Site ESS Unit Fault Indicator | 75 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Fire Warning | PPC | PPC.bessStatus.ess04_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 76 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Fire Faulted | PPC | PPC.bessStatus.ess04_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 77 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Door Warning | PPC | PPC.bessStatus.ess04_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 78 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Door Faulted | PPC | PPC.bessStatus.ess04_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 79 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Estop Faulted | PPC | PPC.bessStatus.ess04_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 80 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Locked | PPC | PPC.bessStatus.ess05_locked | BESS Site ESS Unit Lock Indicator | 81 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Running | PPC | PPC.bessStatus.ess05_run | BESS Site ESS Unit Run Indicator | 82 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Participating | PPC | PPC.bessStatus.ess05_participating | BESS Site ESS Unit Site Participation Indicator | 83 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Warning | PPC | PPC.bessStatus.ess05_warning | BESS Site ESS Unit Warning Indicator | 84 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Faulted | PPC | PPC.bessStatus.ess05_faulted | BESS Site ESS Unit Fault Indicator | 85 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Fire Warning | PPC | PPC.bessStatus.ess05_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 86 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Fire Faulted | PPC | PPC.bessStatus.ess05_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 87 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Door Warning | PPC | PPC.bessStatus.ess05_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 88 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Door Faulted | PPC | PPC.bessStatus.ess05_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 89 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Estop Faulted | PPC | PPC.bessStatus.ess05_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 90 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Locked | PPC | PPC.bessStatus.ess06_locked | BESS Site ESS Unit Lock Indicator | 91 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Running | PPC | PPC.bessStatus.ess06_run | BESS Site ESS Unit Run Indicator | 92 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Participating | PPC | PPC.bessStatus.ess06_participating | BESS Site ESS Unit Site Participation Indicator | 93 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Warning | PPC | PPC.bessStatus.ess06_warning | BESS Site ESS Unit Warning Indicator | 94 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Faulted | PPC | PPC.bessStatus.ess06_faulted | BESS Site ESS Unit Fault Indicator | 95 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Fire Warning | PPC | PPC.bessStatus.ess06_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 96 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Fire Faulted | PPC | PPC.bessStatus.ess06_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 97 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Door Warning | PPC | PPC.bessStatus.ess06_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 98 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Door Faulted | PPC | PPC.bessStatus.ess06_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 99 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Estop Faulted | PPC | PPC.bessStatus.ess06_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 100 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Locked | PPC | PPC.bessStatus.ess07_locked | BESS Site ESS Unit Lock Indicator | 101 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Running | PPC | PPC.bessStatus.ess07_run | BESS Site ESS Unit Run Indicator | 102 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Participating | PPC | PPC.bessStatus.ess07_participating | BESS Site ESS Unit Site Participation Indicator | 103 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Warning | PPC | PPC.bessStatus.ess07_warning | BESS Site ESS Unit Warning Indicator | 104 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Faulted | PPC | PPC.bessStatus.ess07_faulted | BESS Site ESS Unit Fault Indicator | 105 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Fire Warning | PPC | PPC.bessStatus.ess07_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 106 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Fire Faulted | PPC | PPC.bessStatus.ess07_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 107 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Door Warning | PPC | PPC.bessStatus.ess07_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 108 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Door Faulted | PPC | PPC.bessStatus.ess07_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 109 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Estop Faulted | PPC | PPC.bessStatus.ess07_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 110 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Locked | PPC | PPC.bessStatus.ess08_locked | BESS Site ESS Unit Lock Indicator | 111 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Running | PPC | PPC.bessStatus.ess08_run | BESS Site ESS Unit Run Indicator | 112 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Participating | PPC | PPC.bessStatus.ess08_participating | BESS Site ESS Unit Site Participation Indicator | 113 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Warning | PPC | PPC.bessStatus.ess08_warning | BESS Site ESS Unit Warning Indicator | 114 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Faulted | PPC | PPC.bessStatus.ess08_faulted | BESS Site ESS Unit Fault Indicator | 115 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Fire Warning | PPC | PPC.bessStatus.ess08_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 116 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Fire Faulted | PPC | PPC.bessStatus.ess08_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 117 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Door Warning | PPC | PPC.bessStatus.ess08_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 118 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Door Faulted | PPC | PPC.bessStatus.ess08_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 119 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Estop Faulted | PPC | PPC.bessStatus.ess08_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 120 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Locked | PPC | PPC.bessStatus.ess09_locked | BESS Site ESS Unit Lock Indicator | 121 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Running | PPC | PPC.bessStatus.ess09_run | BESS Site ESS Unit Run Indicator | 122 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Participating | PPC | PPC.bessStatus.ess09_participating | BESS Site ESS Unit Site Participation Indicator | 123 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Warning | PPC | PPC.bessStatus.ess09_warning | BESS Site ESS Unit Warning Indicator | 124 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Faulted | PPC | PPC.bessStatus.ess09_faulted | BESS Site ESS Unit Fault Indicator | 125 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Fire Warning | PPC | PPC.bessStatus.ess09_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 126 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Fire Faulted | PPC | PPC.bessStatus.ess09_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 127 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Door Warning | PPC | PPC.bessStatus.ess09_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 128 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Door Faulted | PPC | PPC.bessStatus.ess09_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 129 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Estop Faulted | PPC | PPC.bessStatus.ess09_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 130 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Locked | PPC | PPC.bessStatus.ess10_locked | BESS Site ESS Unit Lock Indicator | 131 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Running | PPC | PPC.bessStatus.ess10_run | BESS Site ESS Unit Run Indicator | 132 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Participating | PPC | PPC.bessStatus.ess10_participating | BESS Site ESS Unit Site Participation Indicator | 133 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Warning | PPC | PPC.bessStatus.ess10_warning | BESS Site ESS Unit Warning Indicator | 134 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Faulted | PPC | PPC.bessStatus.ess10_faulted | BESS Site ESS Unit Fault Indicator | 135 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Fire Warning | PPC | PPC.bessStatus.ess10_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 136 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Fire Faulted | PPC | PPC.bessStatus.ess10_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 137 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Door Warning | PPC | PPC.bessStatus.ess10_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 138 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Door Faulted | PPC | PPC.bessStatus.ess10_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 139 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Estop Faulted | PPC | PPC.bessStatus.ess10_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 140 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Locked | PPC | PPC.bessStatus.ess11_locked | BESS Site ESS Unit Lock Indicator | 141 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Running | PPC | PPC.bessStatus.ess11_run | BESS Site ESS Unit Run Indicator | 142 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Participating | PPC | PPC.bessStatus.ess11_participating | BESS Site ESS Unit Site Participation Indicator | 143 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Warning | PPC | PPC.bessStatus.ess11_warning | BESS Site ESS Unit Warning Indicator | 144 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Faulted | PPC | PPC.bessStatus.ess11_faulted | BESS Site ESS Unit Fault Indicator | 145 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Fire Warning | PPC | PPC.bessStatus.ess11_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 146 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Fire Faulted | PPC | PPC.bessStatus.ess11_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 147 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Door Warning | PPC | PPC.bessStatus.ess11_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 148 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Door Faulted | PPC | PPC.bessStatus.ess11_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 149 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Estop Faulted | PPC | PPC.bessStatus.ess11_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 150 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Locked | PPC | PPC.bessStatus.ess12_locked | BESS Site ESS Unit Lock Indicator | 151 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Running | PPC | PPC.bessStatus.ess12_run | BESS Site ESS Unit Run Indicator | 152 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Participating | PPC | PPC.bessStatus.ess12_participating | BESS Site ESS Unit Site Participation Indicator | 153 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Warning | PPC | PPC.bessStatus.ess12_warning | BESS Site ESS Unit Warning Indicator | 154 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Faulted | PPC | PPC.bessStatus.ess12_faulted | BESS Site ESS Unit Fault Indicator | 155 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Fire Warning | PPC | PPC.bessStatus.ess12_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 156 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Fire Faulted | PPC | PPC.bessStatus.ess12_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 157 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Door Warning | PPC | PPC.bessStatus.ess12_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 158 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Door Faulted | PPC | PPC.bessStatus.ess12_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 159 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Estop Faulted | PPC | PPC.bessStatus.ess12_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 160 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Locked | PPC | PPC.bessStatus.ess13_locked | BESS Site ESS Unit Lock Indicator | 161 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Running | PPC | PPC.bessStatus.ess13_run | BESS Site ESS Unit Run Indicator | 162 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Participating | PPC | PPC.bessStatus.ess13_participating | BESS Site ESS Unit Site Participation Indicator | 163 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Warning | PPC | PPC.bessStatus.ess13_warning | BESS Site ESS Unit Warning Indicator | 164 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Faulted | PPC | PPC.bessStatus.ess13_faulted | BESS Site ESS Unit Fault Indicator | 165 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Fire Warning | PPC | PPC.bessStatus.ess13_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 166 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Fire Faulted | PPC | PPC.bessStatus.ess13_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 167 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Door Warning | PPC | PPC.bessStatus.ess13_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 168 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Door Faulted | PPC | PPC.bessStatus.ess13_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 169 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Estop Faulted | PPC | PPC.bessStatus.ess13_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 170 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Locked | PPC | PPC.bessStatus.ess14_locked | BESS Site ESS Unit Lock Indicator | 171 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Running | PPC | PPC.bessStatus.ess14_run | BESS Site ESS Unit Run Indicator | 172 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Participating | PPC | PPC.bessStatus.ess14_participating | BESS Site ESS Unit Site Participation Indicator | 173 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Warning | PPC | PPC.bessStatus.ess14_warning | BESS Site ESS Unit Warning Indicator | 174 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Faulted | PPC | PPC.bessStatus.ess14_faulted | BESS Site ESS Unit Fault Indicator | 175 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Fire Warning | PPC | PPC.bessStatus.ess14_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 176 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Fire Faulted | PPC | PPC.bessStatus.ess14_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 177 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Door Warning | PPC | PPC.bessStatus.ess14_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 178 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Door Faulted | PPC | PPC.bessStatus.ess14_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 179 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Estop Faulted | PPC | PPC.bessStatus.ess14_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 180 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Locked | PPC | PPC.bessStatus.ess15_locked | BESS Site ESS Unit Lock Indicator | 181 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Running | PPC | PPC.bessStatus.ess15_run | BESS Site ESS Unit Run Indicator | 182 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Participating | PPC | PPC.bessStatus.ess15_participating | BESS Site ESS Unit Site Participation Indicator | 183 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Warning | PPC | PPC.bessStatus.ess15_warning | BESS Site ESS Unit Warning Indicator | 184 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Faulted | PPC | PPC.bessStatus.ess15_faulted | BESS Site ESS Unit Fault Indicator | 185 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Fire Warning | PPC | PPC.bessStatus.ess15_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 186 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Fire Faulted | PPC | PPC.bessStatus.ess15_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 187 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Door Warning | PPC | PPC.bessStatus.ess15_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 188 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Door Faulted | PPC | PPC.bessStatus.ess15_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 189 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Estop Faulted | PPC | PPC.bessStatus.ess15_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 190 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Locked | PPC | PPC.bessStatus.ess16_locked | BESS Site ESS Unit Lock Indicator | 191 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Running | PPC | PPC.bessStatus.ess16_run | BESS Site ESS Unit Run Indicator | 192 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Participating | PPC | PPC.bessStatus.ess16_participating | BESS Site ESS Unit Site Participation Indicator | 193 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Warning | PPC | PPC.bessStatus.ess16_warning | BESS Site ESS Unit Warning Indicator | 194 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Faulted | PPC | PPC.bessStatus.ess16_faulted | BESS Site ESS Unit Fault Indicator | 195 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Fire Warning | PPC | PPC.bessStatus.ess16_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 196 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Fire Faulted | PPC | PPC.bessStatus.ess16_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 197 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Door Warning | PPC | PPC.bessStatus.ess16_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 198 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Door Faulted | PPC | PPC.bessStatus.ess16_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 199 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Estop Faulted | PPC | PPC.bessStatus.ess16_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 200 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Locked | PPC | PPC.bessStatus.ess17_locked | BESS Site ESS Unit Lock Indicator | 201 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Running | PPC | PPC.bessStatus.ess17_run | BESS Site ESS Unit Run Indicator | 202 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Participating | PPC | PPC.bessStatus.ess17_participating | BESS Site ESS Unit Site Participation Indicator | 203 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Warning | PPC | PPC.bessStatus.ess17_warning | BESS Site ESS Unit Warning Indicator | 204 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Faulted | PPC | PPC.bessStatus.ess17_faulted | BESS Site ESS Unit Fault Indicator | 205 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Fire Warning | PPC | PPC.bessStatus.ess17_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 206 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Fire Faulted | PPC | PPC.bessStatus.ess17_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 207 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Door Warning | PPC | PPC.bessStatus.ess17_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 208 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Door Faulted | PPC | PPC.bessStatus.ess17_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 209 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Estop Faulted | PPC | PPC.bessStatus.ess17_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 210 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Locked | PPC | PPC.bessStatus.ess18_locked | BESS Site ESS Unit Lock Indicator | 211 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Running | PPC | PPC.bessStatus.ess18_run | BESS Site ESS Unit Run Indicator | 212 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Participating | PPC | PPC.bessStatus.ess18_participating | BESS Site ESS Unit Site Participation Indicator | 213 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Warning | PPC | PPC.bessStatus.ess18_warning | BESS Site ESS Unit Warning Indicator | 214 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Faulted | PPC | PPC.bessStatus.ess18_faulted | BESS Site ESS Unit Fault Indicator | 215 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Fire Warning | PPC | PPC.bessStatus.ess18_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 216 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Fire Faulted | PPC | PPC.bessStatus.ess18_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 217 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Door Warning | PPC | PPC.bessStatus.ess18_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 218 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Door Faulted | PPC | PPC.bessStatus.ess18_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 219 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Estop Faulted | PPC | PPC.bessStatus.ess18_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 220 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Locked | PPC | PPC.bessStatus.ess19_locked | BESS Site ESS Unit Lock Indicator | 221 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Running | PPC | PPC.bessStatus.ess19_run | BESS Site ESS Unit Run Indicator | 222 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Participating | PPC | PPC.bessStatus.ess19_participating | BESS Site ESS Unit Site Participation Indicator | 223 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Warning | PPC | PPC.bessStatus.ess19_warning | BESS Site ESS Unit Warning Indicator | 224 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Faulted | PPC | PPC.bessStatus.ess19_faulted | BESS Site ESS Unit Fault Indicator | 225 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Fire Warning | PPC | PPC.bessStatus.ess19_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 226 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Fire Faulted | PPC | PPC.bessStatus.ess19_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 227 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Door Warning | PPC | PPC.bessStatus.ess19_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 228 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Door Faulted | PPC | PPC.bessStatus.ess19_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 229 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Estop Faulted | PPC | PPC.bessStatus.ess19_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 230 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Locked | PPC | PPC.bessStatus.ess20_locked | BESS Site ESS Unit Lock Indicator | 231 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Running | PPC | PPC.bessStatus.ess20_run | BESS Site ESS Unit Run Indicator | 232 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Participating | PPC | PPC.bessStatus.ess20_participating | BESS Site ESS Unit Site Participation Indicator | 233 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Warning | PPC | PPC.bessStatus.ess20_warning | BESS Site ESS Unit Warning Indicator | 234 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Faulted | PPC | PPC.bessStatus.ess20_faulted | BESS Site ESS Unit Fault Indicator | 235 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Fire Warning | PPC | PPC.bessStatus.ess20_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 236 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Fire Faulted | PPC | PPC.bessStatus.ess20_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 237 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Door Warning | PPC | PPC.bessStatus.ess20_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 238 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Door Faulted | PPC | PPC.bessStatus.ess20_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 239 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Estop Faulted | PPC | PPC.bessStatus.ess20_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 240 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19975 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 241 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 242 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 243 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 244 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 245 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 246 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 247 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Unit 21GEN19975 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 248 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Invalid GMS Unit 21GEN19975 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 249 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 250 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 251 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 252 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 253 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 254 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 255 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 256 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 257 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 258 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 259 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 260 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 261 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 262 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 263 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 264 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 265 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 266 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 267 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 268 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 269 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 270 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 271 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 3P Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 272 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Breaker Closed | PPC | PPC.bessStatus.cb52 | BESS Site Breaker Status Indicator | 273 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Relay Faulted | PPC | PPC.bessStatus.relayFault | BESS Site Protection Relay Fault Indictor | 274 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Auto Operation Enabled | PPC | PPC.bessStatus.autoOperation | BESS Site Auto-operation Indicator | 275 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Locked | PPC | PPC.bessStatus.locked | BESS Site ESS Lock Indicator | 276 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Running | PPC | PPC.bessStatus.run | BESS Site ESS Run Indicator | 277 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Auto Start Enabled | PPC | PPC.bessStatus.autoStart | BESS Site ESS Auto-start Indicator | 278 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Remote Control Enabled | PPC | PPC.bessStatus.remoteControl | BESS Site ESS Remote Control Indicator | 279 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Warning | PPC | PPC.bessStatus.warning | BESS Site ESS Warning Indicator | 280 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Faulted | PPC | PPC.bessStatus.faulted | BESS Site ESS Fault Indicator | 281 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Locked | PPC | PPC.bessStatus.ess01_locked | BESS Site ESS Unit Lock Indicator | 282 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Running | PPC | PPC.bessStatus.ess01_run | BESS Site ESS Unit Run Indicator | 283 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Participating | PPC | PPC.bessStatus.ess01_participating | BESS Site ESS Unit Site Participation Indicator | 284 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Warning | PPC | PPC.bessStatus.ess01_warning | BESS Site ESS Unit Warning Indicator | 285 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Faulted | PPC | PPC.bessStatus.ess01_faulted | BESS Site ESS Unit Fault Indicator | 286 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Fire Warning | PPC | PPC.bessStatus.ess01_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 287 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Fire Faulted | PPC | PPC.bessStatus.ess01_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 288 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Door Warning | PPC | PPC.bessStatus.ess01_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 289 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Door Faulted | PPC | PPC.bessStatus.ess01_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 290 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Estop Faulted | PPC | PPC.bessStatus.ess01_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 291 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Locked | PPC | PPC.bessStatus.ess02_locked | BESS Site ESS Unit Lock Indicator | 292 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Running | PPC | PPC.bessStatus.ess02_run | BESS Site ESS Unit Run Indicator | 293 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Participating | PPC | PPC.bessStatus.ess02_participating | BESS Site ESS Unit Site Participation Indicator | 294 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Warning | PPC | PPC.bessStatus.ess02_warning | BESS Site ESS Unit Warning Indicator | 295 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Faulted | PPC | PPC.bessStatus.ess02_faulted | BESS Site ESS Unit Fault Indicator | 296 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Fire Warning | PPC | PPC.bessStatus.ess02_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 297 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Fire Faulted | PPC | PPC.bessStatus.ess02_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 298 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Door Warning | PPC | PPC.bessStatus.ess02_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 299 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Door Faulted | PPC | PPC.bessStatus.ess02_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 300 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Estop Faulted | PPC | PPC.bessStatus.ess02_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 301 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Locked | PPC | PPC.bessStatus.ess03_locked | BESS Site ESS Unit Lock Indicator | 302 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Running | PPC | PPC.bessStatus.ess03_run | BESS Site ESS Unit Run Indicator | 303 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Participating | PPC | PPC.bessStatus.ess03_participating | BESS Site ESS Unit Site Participation Indicator | 304 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Warning | PPC | PPC.bessStatus.ess03_warning | BESS Site ESS Unit Warning Indicator | 305 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Faulted | PPC | PPC.bessStatus.ess03_faulted | BESS Site ESS Unit Fault Indicator | 306 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Fire Warning | PPC | PPC.bessStatus.ess03_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 307 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Fire Faulted | PPC | PPC.bessStatus.ess03_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 308 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Door Warning | PPC | PPC.bessStatus.ess03_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 309 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Door Faulted | PPC | PPC.bessStatus.ess03_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 310 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Estop Faulted | PPC | PPC.bessStatus.ess03_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 311 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Locked | PPC | PPC.bessStatus.ess04_locked | BESS Site ESS Unit Lock Indicator | 312 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Running | PPC | PPC.bessStatus.ess04_run | BESS Site ESS Unit Run Indicator | 313 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Participating | PPC | PPC.bessStatus.ess04_participating | BESS Site ESS Unit Site Participation Indicator | 314 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Warning | PPC | PPC.bessStatus.ess04_warning | BESS Site ESS Unit Warning Indicator | 315 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Faulted | PPC | PPC.bessStatus.ess04_faulted | BESS Site ESS Unit Fault Indicator | 316 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Fire Warning | PPC | PPC.bessStatus.ess04_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 317 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Fire Faulted | PPC | PPC.bessStatus.ess04_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 318 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Door Warning | PPC | PPC.bessStatus.ess04_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 319 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Door Faulted | PPC | PPC.bessStatus.ess04_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 320 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Estop Faulted | PPC | PPC.bessStatus.ess04_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 321 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19979 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 322 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 323 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 324 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 325 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 326 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 327 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 328 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Unit 21GEN19979 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 329 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Invalid GMS Unit 21GEN19979 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 330 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 331 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 332 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 333 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 334 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 335 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 336 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 337 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 338 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 339 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 340 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 341 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 342 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 343 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 344 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 345 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 346 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 347 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 348 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 349 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 350 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 351 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 352 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 3P Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 353 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Breaker Closed | PPC | PPC.bessStatus.cb52 | BESS Site Breaker Status Indicator | 354 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Relay Faulted | PPC | PPC.bessStatus.relayFault | BESS Site Protection Relay Fault Indictor | 355 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Auto Operation Enabled | PPC | PPC.bessStatus.autoOperation | BESS Site Auto-operation Indicator | 356 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Locked | PPC | PPC.bessStatus.locked | BESS Site ESS Lock Indicator | 357 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Running | PPC | PPC.bessStatus.run | BESS Site ESS Run Indicator | 358 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Auto Start Enabled | PPC | PPC.bessStatus.autoStart | BESS Site ESS Auto-start Indicator | 359 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Remote Control Enabled | PPC | PPC.bessStatus.remoteControl | BESS Site ESS Remote Control Indicator | 360 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Warning | PPC | PPC.bessStatus.warning | BESS Site ESS Warning Indicator | 361 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Faulted | PPC | PPC.bessStatus.faulted | BESS Site ESS Fault Indicator | 362 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Locked | PPC | PPC.bessStatus.ess01_locked | BESS Site ESS Unit Lock Indicator | 363 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Running | PPC | PPC.bessStatus.ess01_run | BESS Site ESS Unit Run Indicator | 364 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Participating | PPC | PPC.bessStatus.ess01_participating | BESS Site ESS Unit Site Participation Indicator | 365 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Warning | PPC | PPC.bessStatus.ess01_warning | BESS Site ESS Unit Warning Indicator | 366 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Faulted | PPC | PPC.bessStatus.ess01_faulted | BESS Site ESS Unit Fault Indicator | 367 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Fire Warning | PPC | PPC.bessStatus.ess01_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 368 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Fire Faulted | PPC | PPC.bessStatus.ess01_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 369 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Door Warning | PPC | PPC.bessStatus.ess01_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 370 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Door Faulted | PPC | PPC.bessStatus.ess01_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 371 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Estop Faulted | PPC | PPC.bessStatus.ess01_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 372 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Locked | PPC | PPC.bessStatus.ess02_locked | BESS Site ESS Unit Lock Indicator | 373 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Running | PPC | PPC.bessStatus.ess02_run | BESS Site ESS Unit Run Indicator | 374 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Participating | PPC | PPC.bessStatus.ess02_participating | BESS Site ESS Unit Site Participation Indicator | 375 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Warning | PPC | PPC.bessStatus.ess02_warning | BESS Site ESS Unit Warning Indicator | 376 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Faulted | PPC | PPC.bessStatus.ess02_faulted | BESS Site ESS Unit Fault Indicator | 377 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Fire Warning | PPC | PPC.bessStatus.ess02_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 378 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Fire Faulted | PPC | PPC.bessStatus.ess02_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 379 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Door Warning | PPC | PPC.bessStatus.ess02_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 380 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Door Faulted | PPC | PPC.bessStatus.ess02_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 381 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Estop Faulted | PPC | PPC.bessStatus.ess02_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 382 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Locked | PPC | PPC.bessStatus.ess03_locked | BESS Site ESS Unit Lock Indicator | 383 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Running | PPC | PPC.bessStatus.ess03_run | BESS Site ESS Unit Run Indicator | 384 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Participating | PPC | PPC.bessStatus.ess03_participating | BESS Site ESS Unit Site Participation Indicator | 385 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Warning | PPC | PPC.bessStatus.ess03_warning | BESS Site ESS Unit Warning Indicator | 386 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Faulted | PPC | PPC.bessStatus.ess03_faulted | BESS Site ESS Unit Fault Indicator | 387 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Fire Warning | PPC | PPC.bessStatus.ess03_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 388 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Fire Faulted | PPC | PPC.bessStatus.ess03_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 389 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Door Warning | PPC | PPC.bessStatus.ess03_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 390 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Door Faulted | PPC | PPC.bessStatus.ess03_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 391 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Estop Faulted | PPC | PPC.bessStatus.ess03_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 392 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Locked | PPC | PPC.bessStatus.ess04_locked | BESS Site ESS Unit Lock Indicator | 393 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Running | PPC | PPC.bessStatus.ess04_run | BESS Site ESS Unit Run Indicator | 394 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Participating | PPC | PPC.bessStatus.ess04_participating | BESS Site ESS Unit Site Participation Indicator | 395 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Warning | PPC | PPC.bessStatus.ess04_warning | BESS Site ESS Unit Warning Indicator | 396 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Faulted | PPC | PPC.bessStatus.ess04_faulted | BESS Site ESS Unit Fault Indicator | 397 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Fire Warning | PPC | PPC.bessStatus.ess04_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 398 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Fire Faulted | PPC | PPC.bessStatus.ess04_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 399 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Door Warning | PPC | PPC.bessStatus.ess04_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 400 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Door Faulted | PPC | PPC.bessStatus.ess04_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 401 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Estop Faulted | PPC | PPC.bessStatus.ess04_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 402 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Locked | PPC | PPC.bessStatus.ess05_locked | BESS Site ESS Unit Lock Indicator | 403 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Running | PPC | PPC.bessStatus.ess05_run | BESS Site ESS Unit Run Indicator | 404 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Participating | PPC | PPC.bessStatus.ess05_participating | BESS Site ESS Unit Site Participation Indicator | 405 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Warning | PPC | PPC.bessStatus.ess05_warning | BESS Site ESS Unit Warning Indicator | 406 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Faulted | PPC | PPC.bessStatus.ess05_faulted | BESS Site ESS Unit Fault Indicator | 407 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Fire Warning | PPC | PPC.bessStatus.ess05_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 408 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Fire Faulted | PPC | PPC.bessStatus.ess05_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 409 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Door Warning | PPC | PPC.bessStatus.ess05_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 410 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Door Faulted | PPC | PPC.bessStatus.ess05_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 411 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Estop Faulted | PPC | PPC.bessStatus.ess05_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 412 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19973 Curtailment Disabled/Enabled | PPC | PPC.status.curtailmentEnabled | GMS Curtailment Disabled/Enabled | 413 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Reactive Power Control Disabled/Enabled | PPC | PPC.status.qControlEnabled | GMS Reactive Power Control Disabled/Enabled | 414 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Power Factor Control Disabled/Enabled | PPC | PPC.status.pfControlEnabled | GMS Power Factor Control Disabled/Enabled | 415 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Voltage Control Disabled/Enabled | PPC | PPC.status.vControlEnabled | GMS Voltage Control Disabled/Enabled | 416 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Up Rate Control Disabled/Enabled | PPC | PPC.status.RampUpEnabled | GMS Ramp Up Rate Control Disabled/Enabled | 417 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Down Rate Control Disabled/Enabled | PPC | PPC.status.RampDownEnabled | GMS Ramp Down Rate Control Disabled/Enabled | 418 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 AVR Active | PPC | PPC.status.avrEnabled | AVR Active | 419 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Unit 21GEN19973 Active Curtailment | PPC | PPC.status.curtailed | Active Curtailment | 420 | 0=FALSE, 1=TRUE | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_Invalid GMS Unit 21GEN19973 Curtailment Setpoint Alarm | PPC | PPC.status.invalidPsp | Invalid GMS Curtailment Setpoint Alarm | 421 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Invalid GMS Voltage Setpoint Alarm | PPC | PPC.status.invalidVsp | Invalid GMS Voltage Setpoint Alarm | 422 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Invalid GMS VAR Setpoint Alarm | PPC | PPC.status.invalidQsp | Invalid GMS VAR Setpoint Alarm | 423 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Invalid GMS PF Setpoint Alarm | PPC | PPC.status.invalidPFsp | Invalid GMS PF Setpoint Alarm | 424 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Invalid GMS Ramp Rate Setpoint Alarm | PPC | PPC.status.invalidRampRate | Invalid GMS Ramp Rate Setpoint Alarm | 425 | 0=Normal, 1=Alarm | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 High Frequency Event Flag | PPC | PPC.status.f3High | High Frequency Event Flag | 426 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Low Frequency Event Flag | PPC | PPC.status.f3Low | Low Frequency Event Flag | 427 | 0=Off, 1=On | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed SP | PPC | PPC.status.curtailmentPsp | Curtailment active due to P setpoint | 428 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed Capability | PPC | PPC.status.curtailmentCapability | Curtailment active due to plant capability | 429 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed Ramping | PPC | PPC.status.curtailmentRamping | Curtailment active due to Ramping | 430 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed Freq Reg | PPC | PPC.status.curtailmentFreqReg | Curtailment active due to Frequency Regulation | 431 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 Curtailed AGC | PPC | PPC.status.curtailmentAGC | Curtailment active due to AGC command | 432 | 0=Off, 1=On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Curtailment EN Feedback | PPC | PPC.hmi.ppa1CurtailmentEn | HMI Curtailment Enabled Feedback | 433 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Voltage Mode EN Feedback | PPC | PPC.hmi.vModeEN | HMI Voltage Mode Enabled Feedback | 434 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI PF Mode EN Feedback | PPC | PPC.hmi.pfModeEn | HMI PF Mode Enabled Feedback | 435 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI MVAR Mode EN Feedback | PPC | PPC.hmi.qModeEn | HMI MVAR Mode Enabled Feedback | 436 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Ramp Up Rate EN Feedback | PPC | PPC.hmi.pUpSpEn | HMI Ramp Up Rate SP Enabled Feedback | 437 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 HMI Ramp Down Rate EN Feedback | PPC | PPC.hmi.pDownSpEn | HMI Ramp Down Rate SP Enabled Feedback | 438 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Curtailment EN Feedback | PPC | PPC.rem.ppa1CurtailmentEn | 3rd Party Curtailment Enabled Feedback | 439 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Voltage Mode EN Feedback | PPC | PPC.rem.vModeEN | 3rd Party Voltage Mode Enabled Feedback | 440 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P PF Mode EN Feedback | PPC | PPC.rem.pfModeEn | 3rd Party PF Mode Enabled Feedback | 441 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P MVAR Mode EN Feedback | PPC | PPC.rem.qModeEn | 3rd Party MVAR Mode Enabled Feedback | 442 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Ramp Up Rate EN Feedback | PPC | PPC.rem.pUpSpEn | 3rd Party Ramp Up Rate SP Enabled Feedback | 443 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 3P Ramp Down Rate EN Feedback | PPC | PPC.rem.pDownSpEn | 3rd Party Ramp Down Rate SP Enabled Feedback | 444 | Latch Off = Disable, Latch On = Enable | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Breaker Closed | PPC | PPC.bessStatus.cb52 | BESS Site Breaker Status Indicator | 445 | 0 - The site breaker is open thus disconnected from the utility grid; 1 -The site breaker is closed thus connected to utility grid. The site breaker can be openned by manual operation or openned by protection relay due to fault detection | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Relay Faulted | PPC | PPC.bessStatus.relayFault | BESS Site Protection Relay Fault Indictor | 446 | 0 - The site protection relay reports no fault; 1 - Th site protection relay reports fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Auto Operation Enabled | PPC | PPC.bessStatus.autoOperation | BESS Site Auto-operation Indicator | 447 | 0 - Disabled; 1 - Enabled. When enabled, GEMS rule engine mange system opeations automatically according to pre-configured rule set; When disabled, opeator can dispatch operations manually via UI | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Locked | PPC | PPC.bessStatus.locked | BESS Site ESS Lock Indicator | 448 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Running | PPC | PPC.bessStatus.run | BESS Site ESS Run Indicator | 449 | 0 - Off; 1 - On | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Auto Start Enabled | PPC | PPC.bessStatus.autoStart | BESS Site ESS Auto-start Indicator | 450 | 0 - Disabled; 1 - Enabled. When auto start enabled, all GEMS enasures all ESS units keep running if not locked or has critical faults | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Remote Control Enabled | PPC | PPC.bessStatus.remoteControl | BESS Site ESS Remote Control Indicator | 451 | 0 - Disabled; 1 - Enabled. When external power control enabled, GEMS follows P and Q set points received at the AO point list | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Warning | PPC | PPC.bessStatus.warning | BESS Site ESS Warning Indicator | 452 | 0 - No Site ESS warning; 1 - Site ESS warning present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Faulted | PPC | PPC.bessStatus.faulted | BESS Site ESS Fault Indicator | 453 | 0 - No Site ESS fault; 1 - Site ESS fault present | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Locked | PPC | PPC.bessStatus.ess01_locked | BESS Site ESS Unit Lock Indicator | 454 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Running | PPC | PPC.bessStatus.ess01_run | BESS Site ESS Unit Run Indicator | 455 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Participating | PPC | PPC.bessStatus.ess01_participating | BESS Site ESS Unit Site Participation Indicator | 456 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Warning | PPC | PPC.bessStatus.ess01_warning | BESS Site ESS Unit Warning Indicator | 457 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Faulted | PPC | PPC.bessStatus.ess01_faulted | BESS Site ESS Unit Fault Indicator | 458 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Fire Warning | PPC | PPC.bessStatus.ess01_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 459 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Fire Faulted | PPC | PPC.bessStatus.ess01_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 460 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Door Warning | PPC | PPC.bessStatus.ess01_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 461 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Door Faulted | PPC | PPC.bessStatus.ess01_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 462 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Estop Faulted | PPC | PPC.bessStatus.ess01_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 463 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Locked | PPC | PPC.bessStatus.ess02_locked | BESS Site ESS Unit Lock Indicator | 464 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Running | PPC | PPC.bessStatus.ess02_run | BESS Site ESS Unit Run Indicator | 465 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Participating | PPC | PPC.bessStatus.ess02_participating | BESS Site ESS Unit Site Participation Indicator | 466 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Warning | PPC | PPC.bessStatus.ess02_warning | BESS Site ESS Unit Warning Indicator | 467 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Faulted | PPC | PPC.bessStatus.ess02_faulted | BESS Site ESS Unit Fault Indicator | 468 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Fire Warning | PPC | PPC.bessStatus.ess02_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 469 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Fire Faulted | PPC | PPC.bessStatus.ess02_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 470 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Door Warning | PPC | PPC.bessStatus.ess02_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 471 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Door Faulted | PPC | PPC.bessStatus.ess02_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 472 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Estop Faulted | PPC | PPC.bessStatus.ess02_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 473 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Locked | PPC | PPC.bessStatus.ess03_locked | BESS Site ESS Unit Lock Indicator | 474 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Running | PPC | PPC.bessStatus.ess03_run | BESS Site ESS Unit Run Indicator | 475 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Participating | PPC | PPC.bessStatus.ess03_participating | BESS Site ESS Unit Site Participation Indicator | 476 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Warning | PPC | PPC.bessStatus.ess03_warning | BESS Site ESS Unit Warning Indicator | 477 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Faulted | PPC | PPC.bessStatus.ess03_faulted | BESS Site ESS Unit Fault Indicator | 478 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Fire Warning | PPC | PPC.bessStatus.ess03_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 479 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Fire Faulted | PPC | PPC.bessStatus.ess03_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 480 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Door Warning | PPC | PPC.bessStatus.ess03_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 481 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Door Faulted | PPC | PPC.bessStatus.ess03_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 482 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Estop Faulted | PPC | PPC.bessStatus.ess03_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 483 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Locked | PPC | PPC.bessStatus.ess04_locked | BESS Site ESS Unit Lock Indicator | 484 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Running | PPC | PPC.bessStatus.ess04_run | BESS Site ESS Unit Run Indicator | 485 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Participating | PPC | PPC.bessStatus.ess04_participating | BESS Site ESS Unit Site Participation Indicator | 486 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Warning | PPC | PPC.bessStatus.ess04_warning | BESS Site ESS Unit Warning Indicator | 487 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Faulted | PPC | PPC.bessStatus.ess04_faulted | BESS Site ESS Unit Fault Indicator | 488 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Fire Warning | PPC | PPC.bessStatus.ess04_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 489 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Fire Faulted | PPC | PPC.bessStatus.ess04_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 490 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Door Warning | PPC | PPC.bessStatus.ess04_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 491 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Door Faulted | PPC | PPC.bessStatus.ess04_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 492 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Estop Faulted | PPC | PPC.bessStatus.ess04_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 493 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Locked | PPC | PPC.bessStatus.ess05_locked | BESS Site ESS Unit Lock Indicator | 494 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Running | PPC | PPC.bessStatus.ess05_run | BESS Site ESS Unit Run Indicator | 495 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Participating | PPC | PPC.bessStatus.ess05_participating | BESS Site ESS Unit Site Participation Indicator | 496 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Warning | PPC | PPC.bessStatus.ess05_warning | BESS Site ESS Unit Warning Indicator | 497 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Faulted | PPC | PPC.bessStatus.ess05_faulted | BESS Site ESS Unit Fault Indicator | 498 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Fire Warning | PPC | PPC.bessStatus.ess05_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 499 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Fire Faulted | PPC | PPC.bessStatus.ess05_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 500 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Door Warning | PPC | PPC.bessStatus.ess05_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 501 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Door Faulted | PPC | PPC.bessStatus.ess05_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 502 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Estop Faulted | PPC | PPC.bessStatus.ess05_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 503 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Locked | PPC | PPC.bessStatus.ess06_locked | BESS Site ESS Unit Lock Indicator | 504 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Running | PPC | PPC.bessStatus.ess06_run | BESS Site ESS Unit Run Indicator | 505 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Participating | PPC | PPC.bessStatus.ess06_participating | BESS Site ESS Unit Site Participation Indicator | 506 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Warning | PPC | PPC.bessStatus.ess06_warning | BESS Site ESS Unit Warning Indicator | 507 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Faulted | PPC | PPC.bessStatus.ess06_faulted | BESS Site ESS Unit Fault Indicator | 508 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Fire Warning | PPC | PPC.bessStatus.ess06_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 509 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Fire Faulted | PPC | PPC.bessStatus.ess06_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 510 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Door Warning | PPC | PPC.bessStatus.ess06_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 511 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Door Faulted | PPC | PPC.bessStatus.ess06_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 512 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Estop Faulted | PPC | PPC.bessStatus.ess06_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 513 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Locked | PPC | PPC.bessStatus.ess07_locked | BESS Site ESS Unit Lock Indicator | 514 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Running | PPC | PPC.bessStatus.ess07_run | BESS Site ESS Unit Run Indicator | 515 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Participating | PPC | PPC.bessStatus.ess07_participating | BESS Site ESS Unit Site Participation Indicator | 516 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Warning | PPC | PPC.bessStatus.ess07_warning | BESS Site ESS Unit Warning Indicator | 517 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Faulted | PPC | PPC.bessStatus.ess07_faulted | BESS Site ESS Unit Fault Indicator | 518 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Fire Warning | PPC | PPC.bessStatus.ess07_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 519 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Fire Faulted | PPC | PPC.bessStatus.ess07_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 520 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Door Warning | PPC | PPC.bessStatus.ess07_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 521 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Door Faulted | PPC | PPC.bessStatus.ess07_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 522 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Estop Faulted | PPC | PPC.bessStatus.ess07_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 523 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Locked | PPC | PPC.bessStatus.ess08_locked | BESS Site ESS Unit Lock Indicator | 524 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Running | PPC | PPC.bessStatus.ess08_run | BESS Site ESS Unit Run Indicator | 525 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Participating | PPC | PPC.bessStatus.ess08_participating | BESS Site ESS Unit Site Participation Indicator | 526 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Warning | PPC | PPC.bessStatus.ess08_warning | BESS Site ESS Unit Warning Indicator | 527 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Faulted | PPC | PPC.bessStatus.ess08_faulted | BESS Site ESS Unit Fault Indicator | 528 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Fire Warning | PPC | PPC.bessStatus.ess08_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 529 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Fire Faulted | PPC | PPC.bessStatus.ess08_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 530 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Door Warning | PPC | PPC.bessStatus.ess08_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 531 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Door Faulted | PPC | PPC.bessStatus.ess08_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 532 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Estop Faulted | PPC | PPC.bessStatus.ess08_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 533 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Locked | PPC | PPC.bessStatus.ess09_locked | BESS Site ESS Unit Lock Indicator | 534 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Running | PPC | PPC.bessStatus.ess09_run | BESS Site ESS Unit Run Indicator | 535 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Participating | PPC | PPC.bessStatus.ess09_participating | BESS Site ESS Unit Site Participation Indicator | 536 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Warning | PPC | PPC.bessStatus.ess09_warning | BESS Site ESS Unit Warning Indicator | 537 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Faulted | PPC | PPC.bessStatus.ess09_faulted | BESS Site ESS Unit Fault Indicator | 538 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Fire Warning | PPC | PPC.bessStatus.ess09_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 539 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Fire Faulted | PPC | PPC.bessStatus.ess09_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 540 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Door Warning | PPC | PPC.bessStatus.ess09_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 541 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Door Faulted | PPC | PPC.bessStatus.ess09_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 542 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Estop Faulted | PPC | PPC.bessStatus.ess09_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 543 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Locked | PPC | PPC.bessStatus.ess10_locked | BESS Site ESS Unit Lock Indicator | 544 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Running | PPC | PPC.bessStatus.ess10_run | BESS Site ESS Unit Run Indicator | 545 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Participating | PPC | PPC.bessStatus.ess10_participating | BESS Site ESS Unit Site Participation Indicator | 546 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Warning | PPC | PPC.bessStatus.ess10_warning | BESS Site ESS Unit Warning Indicator | 547 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Faulted | PPC | PPC.bessStatus.ess10_faulted | BESS Site ESS Unit Fault Indicator | 548 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Fire Warning | PPC | PPC.bessStatus.ess10_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 549 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Fire Faulted | PPC | PPC.bessStatus.ess10_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 550 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Door Warning | PPC | PPC.bessStatus.ess10_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 551 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Door Faulted | PPC | PPC.bessStatus.ess10_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 552 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Estop Faulted | PPC | PPC.bessStatus.ess10_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 553 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Locked | PPC | PPC.bessStatus.ess11_locked | BESS Site ESS Unit Lock Indicator | 554 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Running | PPC | PPC.bessStatus.ess11_run | BESS Site ESS Unit Run Indicator | 555 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Participating | PPC | PPC.bessStatus.ess11_participating | BESS Site ESS Unit Site Participation Indicator | 556 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Warning | PPC | PPC.bessStatus.ess11_warning | BESS Site ESS Unit Warning Indicator | 557 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Faulted | PPC | PPC.bessStatus.ess11_faulted | BESS Site ESS Unit Fault Indicator | 558 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Fire Warning | PPC | PPC.bessStatus.ess11_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 559 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Fire Faulted | PPC | PPC.bessStatus.ess11_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 560 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Door Warning | PPC | PPC.bessStatus.ess11_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 561 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Door Faulted | PPC | PPC.bessStatus.ess11_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 562 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Estop Faulted | PPC | PPC.bessStatus.ess11_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 563 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Locked | PPC | PPC.bessStatus.ess12_locked | BESS Site ESS Unit Lock Indicator | 564 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Running | PPC | PPC.bessStatus.ess12_run | BESS Site ESS Unit Run Indicator | 565 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Participating | PPC | PPC.bessStatus.ess12_participating | BESS Site ESS Unit Site Participation Indicator | 566 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Warning | PPC | PPC.bessStatus.ess12_warning | BESS Site ESS Unit Warning Indicator | 567 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Faulted | PPC | PPC.bessStatus.ess12_faulted | BESS Site ESS Unit Fault Indicator | 568 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Fire Warning | PPC | PPC.bessStatus.ess12_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 569 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Fire Faulted | PPC | PPC.bessStatus.ess12_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 570 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Door Warning | PPC | PPC.bessStatus.ess12_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 571 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Door Faulted | PPC | PPC.bessStatus.ess12_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 572 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Estop Faulted | PPC | PPC.bessStatus.ess12_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 573 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Locked | PPC | PPC.bessStatus.ess13_locked | BESS Site ESS Unit Lock Indicator | 574 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Running | PPC | PPC.bessStatus.ess13_run | BESS Site ESS Unit Run Indicator | 575 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Participating | PPC | PPC.bessStatus.ess13_participating | BESS Site ESS Unit Site Participation Indicator | 576 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Warning | PPC | PPC.bessStatus.ess13_warning | BESS Site ESS Unit Warning Indicator | 577 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Faulted | PPC | PPC.bessStatus.ess13_faulted | BESS Site ESS Unit Fault Indicator | 578 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Fire Warning | PPC | PPC.bessStatus.ess13_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 579 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Fire Faulted | PPC | PPC.bessStatus.ess13_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 580 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Door Warning | PPC | PPC.bessStatus.ess13_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 581 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Door Faulted | PPC | PPC.bessStatus.ess13_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 582 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Estop Faulted | PPC | PPC.bessStatus.ess13_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 583 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Locked | PPC | PPC.bessStatus.ess14_locked | BESS Site ESS Unit Lock Indicator | 584 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Running | PPC | PPC.bessStatus.ess14_run | BESS Site ESS Unit Run Indicator | 585 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Participating | PPC | PPC.bessStatus.ess14_participating | BESS Site ESS Unit Site Participation Indicator | 586 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Warning | PPC | PPC.bessStatus.ess14_warning | BESS Site ESS Unit Warning Indicator | 587 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Faulted | PPC | PPC.bessStatus.ess14_faulted | BESS Site ESS Unit Fault Indicator | 588 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Fire Warning | PPC | PPC.bessStatus.ess14_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 589 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Fire Faulted | PPC | PPC.bessStatus.ess14_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 590 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Door Warning | PPC | PPC.bessStatus.ess14_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 591 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Door Faulted | PPC | PPC.bessStatus.ess14_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 592 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Estop Faulted | PPC | PPC.bessStatus.ess14_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 593 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Locked | PPC | PPC.bessStatus.ess15_locked | BESS Site ESS Unit Lock Indicator | 594 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Running | PPC | PPC.bessStatus.ess15_run | BESS Site ESS Unit Run Indicator | 595 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Participating | PPC | PPC.bessStatus.ess15_participating | BESS Site ESS Unit Site Participation Indicator | 596 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Warning | PPC | PPC.bessStatus.ess15_warning | BESS Site ESS Unit Warning Indicator | 597 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Faulted | PPC | PPC.bessStatus.ess15_faulted | BESS Site ESS Unit Fault Indicator | 598 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Fire Warning | PPC | PPC.bessStatus.ess15_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 599 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Fire Faulted | PPC | PPC.bessStatus.ess15_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 600 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Door Warning | PPC | PPC.bessStatus.ess15_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 601 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Door Faulted | PPC | PPC.bessStatus.ess15_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 602 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Estop Faulted | PPC | PPC.bessStatus.ess15_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 603 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Locked | PPC | PPC.bessStatus.ess16_locked | BESS Site ESS Unit Lock Indicator | 604 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Running | PPC | PPC.bessStatus.ess16_run | BESS Site ESS Unit Run Indicator | 605 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Participating | PPC | PPC.bessStatus.ess16_participating | BESS Site ESS Unit Site Participation Indicator | 606 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Warning | PPC | PPC.bessStatus.ess16_warning | BESS Site ESS Unit Warning Indicator | 607 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Faulted | PPC | PPC.bessStatus.ess16_faulted | BESS Site ESS Unit Fault Indicator | 608 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Fire Warning | PPC | PPC.bessStatus.ess16_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 609 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Fire Faulted | PPC | PPC.bessStatus.ess16_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 610 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Door Warning | PPC | PPC.bessStatus.ess16_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 611 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Door Faulted | PPC | PPC.bessStatus.ess16_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 612 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Estop Faulted | PPC | PPC.bessStatus.ess16_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 613 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Locked | PPC | PPC.bessStatus.ess17_locked | BESS Site ESS Unit Lock Indicator | 614 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Running | PPC | PPC.bessStatus.ess17_run | BESS Site ESS Unit Run Indicator | 615 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Participating | PPC | PPC.bessStatus.ess17_participating | BESS Site ESS Unit Site Participation Indicator | 616 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Warning | PPC | PPC.bessStatus.ess17_warning | BESS Site ESS Unit Warning Indicator | 617 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Faulted | PPC | PPC.bessStatus.ess17_faulted | BESS Site ESS Unit Fault Indicator | 618 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Fire Warning | PPC | PPC.bessStatus.ess17_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 619 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Fire Faulted | PPC | PPC.bessStatus.ess17_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 620 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Door Warning | PPC | PPC.bessStatus.ess17_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 621 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Door Faulted | PPC | PPC.bessStatus.ess17_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 622 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Estop Faulted | PPC | PPC.bessStatus.ess17_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 623 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Locked | PPC | PPC.bessStatus.ess18_locked | BESS Site ESS Unit Lock Indicator | 624 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Running | PPC | PPC.bessStatus.ess18_run | BESS Site ESS Unit Run Indicator | 625 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Participating | PPC | PPC.bessStatus.ess18_participating | BESS Site ESS Unit Site Participation Indicator | 626 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Warning | PPC | PPC.bessStatus.ess18_warning | BESS Site ESS Unit Warning Indicator | 627 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Faulted | PPC | PPC.bessStatus.ess18_faulted | BESS Site ESS Unit Fault Indicator | 628 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Fire Warning | PPC | PPC.bessStatus.ess18_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 629 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Fire Faulted | PPC | PPC.bessStatus.ess18_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 630 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Door Warning | PPC | PPC.bessStatus.ess18_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 631 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Door Faulted | PPC | PPC.bessStatus.ess18_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 632 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Estop Faulted | PPC | PPC.bessStatus.ess18_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 633 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Locked | PPC | PPC.bessStatus.ess19_locked | BESS Site ESS Unit Lock Indicator | 634 | 0 - Unlocked; 1 - Locked | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Running | PPC | PPC.bessStatus.ess19_run | BESS Site ESS Unit Run Indicator | 635 | 0 - Stop; 1 - Run | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Participating | PPC | PPC.bessStatus.ess19_participating | BESS Site ESS Unit Site Participation Indicator | 636 | 0 - Not Paticipate; 1 - Paticipate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Warning | PPC | PPC.bessStatus.ess19_warning | BESS Site ESS Unit Warning Indicator | 637 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Faulted | PPC | PPC.bessStatus.ess19_faulted | BESS Site ESS Unit Fault Indicator | 638 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Fire Warning | PPC | PPC.bessStatus.ess19_fireWarning | BESS Site ESS BOP Fire Alarm Warning Indicator | 639 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Fire Faulted | PPC | PPC.bessStatus.ess19_fireFaulted | BESS Site ESS BOP Fire Alarm Fault Indicator | 640 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Door Warning | PPC | PPC.bessStatus.ess19_doorWarning | BESS Site ESS BOP Door Safety Warning Indicator | 641 | 0 - Normal; 1 - Warning | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Door Faulted | PPC | PPC.bessStatus.ess19_doorFaulted | BESS Site ESS BOP Door Safety Fault Indicator | 642 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Estop Faulted | PPC | PPC.bessStatus.ess19_eStopFaulted | BESS Site ESS BOP Estop Fault Indicator | 643 | 0 - Normal; 1 - Fault | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV001 Control Status | PPC | PPC.status.inv001_enabled | Inverter Control Status | 644 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV002 Control Status | PPC | PPC.status.inv002_enabled | Inverter Control Status | 645 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV003 Control Status | PPC | PPC.status.inv003_enabled | Inverter Control Status | 646 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV004 Control Status | PPC | PPC.status.inv004_enabled | Inverter Control Status | 647 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV005 Control Status | PPC | PPC.status.inv005_enabled | Inverter Control Status | 648 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV006 Control Status | PPC | PPC.status.inv006_enabled | Inverter Control Status | 649 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV007 Control Status | PPC | PPC.status.inv007_enabled | Inverter Control Status | 650 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV008 Control Status | PPC | PPC.status.inv008_enabled | Inverter Control Status | 651 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV009 Control Status | PPC | PPC.status.inv009_enabled | Inverter Control Status | 652 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV010 Control Status | PPC | PPC.status.inv010_enabled | Inverter Control Status | 653 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV011 Control Status | PPC | PPC.status.inv011_enabled | Inverter Control Status | 654 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV012 Control Status | PPC | PPC.status.inv012_enabled | Inverter Control Status | 655 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV013 Control Status | PPC | PPC.status.inv013_enabled | Inverter Control Status | 656 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV014 Control Status | PPC | PPC.status.inv014_enabled | Inverter Control Status | 657 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV015 Control Status | PPC | PPC.status.inv015_enabled | Inverter Control Status | 658 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV016 Control Status | PPC | PPC.status.inv016_enabled | Inverter Control Status | 659 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV017 Control Status | PPC | PPC.status.inv017_enabled | Inverter Control Status | 660 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV018 Control Status | PPC | PPC.status.inv018_enabled | Inverter Control Status | 661 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV019 Control Status | PPC | PPC.status.inv019_enabled | Inverter Control Status | 662 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV020 Control Status | PPC | PPC.status.inv020_enabled | Inverter Control Status | 663 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV021 Control Status | PPC | PPC.status.inv021_enabled | Inverter Control Status | 664 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV022 Control Status | PPC | PPC.status.inv022_enabled | Inverter Control Status | 665 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV023 Control Status | PPC | PPC.status.inv023_enabled | Inverter Control Status | 666 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV024 Control Status | PPC | PPC.status.inv024_enabled | Inverter Control Status | 667 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV025 Control Status | PPC | PPC.status.inv025_enabled | Inverter Control Status | 668 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV026 Control Status | PPC | PPC.status.inv026_enabled | Inverter Control Status | 669 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV027 Control Status | PPC | PPC.status.inv027_enabled | Inverter Control Status | 670 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV028 Control Status | PPC | PPC.status.inv028_enabled | Inverter Control Status | 671 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV029 Control Status | PPC | PPC.status.inv029_enabled | Inverter Control Status | 672 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV030 Control Status | PPC | PPC.status.inv030_enabled | Inverter Control Status | 673 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV031 Control Status | PPC | PPC.status.inv031_enabled | Inverter Control Status | 674 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV032 Control Status | PPC | PPC.status.inv032_enabled | Inverter Control Status | 675 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV033 Control Status | PPC | PPC.status.inv033_enabled | Inverter Control Status | 676 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV034 Control Status | PPC | PPC.status.inv034_enabled | Inverter Control Status | 677 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV035 Control Status | PPC | PPC.status.inv035_enabled | Inverter Control Status | 678 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV036 Control Status | PPC | PPC.status.inv036_enabled | Inverter Control Status | 679 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV037 Control Status | PPC | PPC.status.inv037_enabled | Inverter Control Status | 680 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV038 Control Status | PPC | PPC.status.inv038_enabled | Inverter Control Status | 681 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV039 Control Status | PPC | PPC.status.inv039_enabled | Inverter Control Status | 682 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV040 Control Status | PPC | PPC.status.inv040_enabled | Inverter Control Status | 683 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV041 Control Status | PPC | PPC.status.inv041_enabled | Inverter Control Status | 684 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV042 Control Status | PPC | PPC.status.inv042_enabled | Inverter Control Status | 685 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV043 Control Status | PPC | PPC.status.inv043_enabled | Inverter Control Status | 686 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV044 Control Status | PPC | PPC.status.inv044_enabled | Inverter Control Status | 687 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV045 Control Status | PPC | PPC.status.inv045_enabled | Inverter Control Status | 688 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV046 Control Status | PPC | PPC.status.inv046_enabled | Inverter Control Status | 689 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV047 Control Status | PPC | PPC.status.inv047_enabled | Inverter Control Status | 690 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV048 Control Status | PPC | PPC.status.inv048_enabled | Inverter Control Status | 691 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV049 Control Status | PPC | PPC.status.inv049_enabled | Inverter Control Status | 692 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV050 Control Status | PPC | PPC.status.inv050_enabled | Inverter Control Status | 693 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV051 Control Status | PPC | PPC.status.inv051_enabled | Inverter Control Status | 694 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV052 Control Status | PPC | PPC.status.inv052_enabled | Inverter Control Status | 695 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV053 Control Status | PPC | PPC.status.inv053_enabled | Inverter Control Status | 696 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV054 Control Status | PPC | PPC.status.inv054_enabled | Inverter Control Status | 697 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV055 Control Status | PPC | PPC.status.inv055_enabled | Inverter Control Status | 698 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV056 Control Status | PPC | PPC.status.inv056_enabled | Inverter Control Status | 699 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV057 Control Status | PPC | PPC.status.inv057_enabled | Inverter Control Status | 700 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV058 Control Status | PPC | PPC.status.inv058_enabled | Inverter Control Status | 701 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV059 Control Status | PPC | PPC.status.inv059_enabled | Inverter Control Status | 702 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV060 Control Status | PPC | PPC.status.inv060_enabled | Inverter Control Status | 703 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV061 Control Status | PPC | PPC.status.inv061_enabled | Inverter Control Status | 704 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV062 Control Status | PPC | PPC.status.inv062_enabled | Inverter Control Status | 705 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV063 Control Status | PPC | PPC.status.inv063_enabled | Inverter Control Status | 706 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV064 Control Status | PPC | PPC.status.inv064_enabled | Inverter Control Status | 707 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV065 Control Status | PPC | PPC.status.inv065_enabled | Inverter Control Status | 708 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV066 Control Status | PPC | PPC.status.inv066_enabled | Inverter Control Status | 709 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV067 Control Status | PPC | PPC.status.inv067_enabled | Inverter Control Status | 710 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV068 Control Status | PPC | PPC.status.inv068_enabled | Inverter Control Status | 711 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV069 Control Status | PPC | PPC.status.inv069_enabled | Inverter Control Status | 712 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV070 Control Status | PPC | PPC.status.inv070_enabled | Inverter Control Status | 713 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV071 Control Status | PPC | PPC.status.inv071_enabled | Inverter Control Status | 714 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV072 Control Status | PPC | PPC.status.inv072_enabled | Inverter Control Status | 715 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV073 Control Status | PPC | PPC.status.inv073_enabled | Inverter Control Status | 716 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV074 Control Status | PPC | PPC.status.inv074_enabled | Inverter Control Status | 717 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV075 Control Status | PPC | PPC.status.inv075_enabled | Inverter Control Status | 718 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV076 Control Status | PPC | PPC.status.inv076_enabled | Inverter Control Status | 719 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV077 Control Status | PPC | PPC.status.inv077_enabled | Inverter Control Status | 720 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV078 Control Status | PPC | PPC.status.inv078_enabled | Inverter Control Status | 721 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV079 Control Status | PPC | PPC.status.inv079_enabled | Inverter Control Status | 722 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV080 Control Status | PPC | PPC.status.inv080_enabled | Inverter Control Status | 723 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV081 Control Status | PPC | PPC.status.inv081_enabled | Inverter Control Status | 724 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV082 Control Status | PPC | PPC.status.inv082_enabled | Inverter Control Status | 725 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV083 Control Status | PPC | PPC.status.inv083_enabled | Inverter Control Status | 726 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV084 Control Status | PPC | PPC.status.inv084_enabled | Inverter Control Status | 727 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV085 Control Status | PPC | PPC.status.inv085_enabled | Inverter Control Status | 728 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV086 Control Status | PPC | PPC.status.inv086_enabled | Inverter Control Status | 729 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV087 Control Status | PPC | PPC.status.inv087_enabled | Inverter Control Status | 730 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV088 Control Status | PPC | PPC.status.inv088_enabled | Inverter Control Status | 731 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV089 Control Status | PPC | PPC.status.inv089_enabled | Inverter Control Status | 732 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV090 Control Status | PPC | PPC.status.inv090_enabled | Inverter Control Status | 733 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV091 Control Status | PPC | PPC.status.inv091_enabled | Inverter Control Status | 734 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV092 Control Status | PPC | PPC.status.inv092_enabled | Inverter Control Status | 735 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV093 Control Status | PPC | PPC.status.inv093_enabled | Inverter Control Status | 736 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV094 Control Status | PPC | PPC.status.inv094_enabled | Inverter Control Status | 737 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_INV095 Control Status | PPC | PPC.status.inv095_enabled | Inverter Control Status | 738 | 0=Disabled, 1=Enabled | Requested-Available
SUB1 | SOIL094 | Daggett 3_SUB1_SOIL094_Communication Status | Soiling Station | MET94_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL087 | Daggett 3_SUB1_SOIL087_Communication Status | Soiling Station | MET87_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL083 | Daggett 3_SUB1_SOIL083_Communication Status | Soiling Station | MET83_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL075 | Daggett 3_SUB1_SOIL075_Communication Status | Soiling Station | MET75_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL068 | Daggett 3_SUB1_SOIL068_Communication Status | Soiling Station | MET68_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL052 | Daggett 3_SUB1_SOIL052_Communication Status | Soiling Station | MET52_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL012 | Daggett 3_SUB1_SOIL012_Communication Status | Soiling Station | MET12_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL011 | Daggett 3_SUB1_SOIL011_Communication Status | Soiling Station | MET11_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL065 | Daggett 3_SUB1_SOIL065_Communication Status | Soiling Station | MET65_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL044 | Daggett 3_SUB1_SOIL044_Communication Status | Soiling Station | MET44_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL050 | Daggett 3_SUB1_SOIL050_Communication Status | Soiling Station | MET50_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL019 | Daggett 3_SUB1_SOIL019_Communication Status | Soiling Station | MET19_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL008 | Daggett 3_SUB1_SOIL008_Communication Status | Soiling Station | MET08_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL023 | Daggett 3_SUB1_SOIL023_Communication Status | Soiling Station | MET23_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL034 | Daggett 3_SUB1_SOIL034_Communication Status | Soiling Station | MET34_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL031 | Daggett 3_SUB1_SOIL031_Communication Status | Soiling Station | MET31_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SOIL042 | Daggett 3_SUB1_SOIL042_Communication Status | Soiling Station | MET42_commsFail | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Communication Status | Line Relay | GE_L90_87L1P_DNP_POU.Offline | Communication Status | 739 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Relay Enabled | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00000_ENABLED | Relay Online | 740 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Software Alarm | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00001_TROUBLE | Software Alarm | 741 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Hardware Alarm | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00002_ALARM | Hardware Alarm | 742 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Breaker Fail Initiate | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00003_OUT_H3 | Breaker Fail Initiate | 743 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Line Comm Cutout | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00004_Line_Relaying_Comm_Cutout | Line Relaying Comm Cutout | 744 | 0 = Normal, 1 = Cutout | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Line Comm Failure | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00005_Line_Relaying_Comm_Failure | Line Relaying Comm Failure | 745 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_Direct Transfer Trip | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00006_Direct_Transfer_Trip | Line Relaying Comm Failure |  | 0 = Normal, 1 = Trip | Requested-Not Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_52T1 Breaker Status | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00007_INH7c | Hard Wired Contacts | 746 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_52L1 Breaker Status | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00008_INH7a | Hard Wired Contacts | 747 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | GE-L90-87L1P | DAGGETT3_SUB1_GE-L90-87L1P_52T2 Breaker Status | Line Relay | GE_L90_87L1P_DNP.BINARY_INPUT_00009_INH8a | Hard Wired Contacts | 748 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Communication Status | Line Relay | SEL_411L_87L1S_SEL_POU.Offline | Communication Status | 749 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Relay Enabled | Line Relay | SEL_411L_87L1S_SEL_POU.EN | Relay Online | 750 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Software Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_SALARM | Software Alarm | 751 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Hardware Alarm | Line Relay | SEL_411L_87L1S_SEL.FM_INST_HALARM | Hardware Alarm | 752 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Breaker Fail Initiate | Line Relay | SEL_411L_87L1S_SEL.FM_INST_OUT203 | Breaker Fail Initiate | 753 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Line Comm Cutout | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN203 | Line Relaying Comm Cutout |  | 0 = Normal, 1 = Cutout | Requested-Not Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Line Comm Failure | Line Relay | Check for the CBAD elements | Line Relaying Comm Failure |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_52L1 Breaker Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 754 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_Direct Transfer Trip | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 755 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_87L Enable/Disable | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 756 | 0 = Enabled, 1 = Disabled | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L11 Breaker Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 757 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L12 Breaker Status | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 758 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L11 Remote/Local Ctl House | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 759 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L12 Remote/Local Ctl House | Line Relay | SEL_411L_87L1S_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 760 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Communication Status | Line Relay | GE_L90_87L2P_DNP_POU.Offline | Communication Status | 761 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Relay Enabled | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00000_ENABLED | Relay Online | 762 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Software Alarm | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00001_TROUBLE | Software Alarm | 763 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Hardware Alarm | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00002_ALARM | Hardware Alarm | 764 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Breaker Fail Initiate | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00003_OUT_H3 | Breaker Fail Initiate | 765 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Line Comm Cutout | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00004_Line_Relaying_Comm_Cutout | Line Relaying Comm Cutout | 766 | 0 = Normal, 1 = Cutout | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Line Comm Failure | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00005_Line_Relaying_Comm_Failure | Line Relaying Comm Failure | 767 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_Direct Transfer Trip | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00006_INH7c | Direct Transfer Trip | 768 | 0 = Normal, 1 = Trip | Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_52T1 Breaker Status | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00007_INH7a | Hard Wired Contacts | 769 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | GE-L90-87L2P | DAGGETT3_SUB1_GE-L90-87L2P_52T2 Breaker Status | Line Relay | GE_L90_87L2P_DNP.BINARY_INPUT_00008_INH8a | Hard Wired Contacts | 770 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Communication Status | Line Relay | SEL_411L_87L2S_SEL_POU.Offline | Communication Status | 771 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Relay Enabled | Line Relay | SEL_411L_87L2S_SEL_POU.EN | Relay Online | 772 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Software Alarm | Line Relay | SEL_411L_87L2S_SEL.FM_INST_SALARM | Software Alarm | 773 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Hardware Alarm | Line Relay | SEL_411L_87L2S_SEL.FM_INST_HALARM | Hardware Alarm | 774 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Breaker Fail Initiate | Line Relay | SEL_411L_87L2S_SEL.FM_INST_OUT203 | Breaker Fail Initiate | 775 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Line Comm Cutout | Line Relay | Same as above | Line Relaying Comm Cutout |  | 0 = Normal, 1 = Cutout | Requested-Not Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Line Comm Failure | Line Relay |  | Line Relaying Comm Failure |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52L1 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 776 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52T1 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 777 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_52T2 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 778 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_Direct Transfer Trip | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 779 | 0 = Open, 1 = Close | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_87L Enable/Disable | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 780 | 0 = Enabled, 1 = Disabled | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L21 Breaker Status | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 781 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L21 Remote/Local Ctl House | Line Relay | SEL_411L_87L2S_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 782 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Communication Status | Transformer Relay | SEL_487E_87T1P_SEL_POU.Offline | Communication Status | 783 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Relay Enabled | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_EN | Relay Online | 784 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Software Alarm | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_SALARM | Software Alarm | 785 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Hardware Alarm | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_HALARM | Hardware Alarm | 786 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Breaker Fail Initiate | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN206 | Breaker Fail Initiate | 787 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Rapid Pressure Rise Trip | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN101 | Hard Wired Contacts | 788 | 0 = Normal, 1 = Rise | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Pressure Relief Device Trip | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN102 | Hard Wired Contacts | 789 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Buchholz Relay Trip | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN103 | Hard Wired Contacts | 790 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_LTC Protective Relay Trip | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN104 | Hard Wired Contacts | 791 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Oil Temp Trip | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN105 | Hard Wired Contacts | 792 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86T1P TRIP IND | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN106 | Hard Wired Contacts | 793 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86T1P Coil Fail Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN107 | Hard Wired Contacts | 794 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_94T11 Trip Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN201 | Hard Wired Contacts | 795 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_94T12 Trip Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN202 | Hard Wired Contacts | 796 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 Breaker Status | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN203 | Hard Wired Contacts | 797 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86BFT1 Trip Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN204 | Hard Wired Contacts | 798 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_86BFT1 Coil Fail Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN205 | Hard Wired Contacts | 799 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_BFI | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN206 | Hard Wired Contacts | 800 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_DTT Received | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN207 | Hard Wired Contacts | 801 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 Remote/Local Ctl House | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN208 | Hard Wired Contacts | 802 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 Low SF6 Gas Critical | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN211 | Hard Wired Contacts | 803 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_89T1 Switch Ind | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN212 | Hard Wired Contacts | 804 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_89T1 Remote/Local Ctl House | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN213 | Hard Wired Contacts | 805 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 TCM1 | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN214 | Hard Wired Contacts | 806 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52T1 TCM2 | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN215 | Hard Wired Contacts | 807 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F1 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN216 | Hard Wired Contacts | 808 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F2 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN217 | Hard Wired Contacts | 809 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F3 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN218 | Hard Wired Contacts | 810 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F4 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN219 | Hard Wired Contacts | 811 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F5 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN220 | Hard Wired Contacts | 812 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F6 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN221 | Hard Wired Contacts | 813 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F7 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN222 | Hard Wired Contacts | 814 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F8 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN223 | Hard Wired Contacts | 815 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F9 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN224 | Hard Wired Contacts | 816 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F10 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN301 | Hard Wired Contacts | 817 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_52F11 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN302 | Hard Wired Contacts | 818 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_87C1 Relay Fail | Transformer Relay | SEL_487E_87T1P_SEL.FM_INST_IN303 | Hard Wired Contacts | 819 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Communication Status | Transformer Relay | SEL_387A_87T1S_SEL_POU.Offline | Communication Status | 820 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Relay Enabled | Transformer Relay | SEL_387A_87T1S_SEL.FM_INST_EN | Relay Online | 821 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Software Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_NOTALM_SW | Software Alarm | 822 | 0 = Alarm 1 = Normal | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Hardware Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_NOTALM_HW | Hardware Alarm | 823 | 0 = Alarm 1 = Normal | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Breaker Fail Initiate | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_BFI | Breaker Fail Initiate | 824 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_86T1S Trip Ind | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN101 | Hard Wired Contacts | 825 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_86T1S Coil Fail Ind | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN102 | Hard Wired Contacts | 826 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_AC-DC Supply Alarms | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN103 | Hard Wired Contacts | 827 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Oil Level High Alarm Main | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN104 | Hard Wired Contacts | 828 | 4 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Oil Level High Alarm LTC | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN105 | Hard Wired Contacts | 829 | 5 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Top Oil Temp Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN106 | Hard Wired Contacts | 830 | 6 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Winding Temp Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN201 | Hard Wired Contacts | 831 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Sudden Pressure Relay Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN202 | Hard Wired Contacts | 832 | 8 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Communication Status | Transformer Relay | SEL_487E_87T2P_SEL_POU.Offline | Communication Status | 833 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Relay Enabled | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_EN | Relay Online | 834 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Software Alarm | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_SALARM | Software Alarm | 835 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Hardware Alarm | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_HALARM | Hardware Alarm | 836 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Breaker Fail Initiate | Transformer Relay | SEL_487E_87T2P_SEL.FM_INST_IN206 | Breaker Fail Initiate | 837 | 0 = Normal, 1 = BFI | Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Rapid Pressure Rise Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN101 | Hard Wired Contacts | 838 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Pressure Relief Device Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN102 | Hard Wired Contacts | 839 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Buchholz Relay Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN103 | Hard Wired Contacts | 840 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_LTC Protective Relay Trip | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN104 | Hard Wired Contacts | 841 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86T2P Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN106 | Hard Wired Contacts | 842 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86T2P Coil Fail Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN107 | Hard Wired Contacts | 843 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_94T21 Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 844 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 Breaker Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 845 | 0 = Close, 1 = Open | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86BFT2 Trip Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 846 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_86BFT2 Coil Fail Status | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 847 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_DTT Received | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 848 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 Remote/Local Ctl House | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN208 | Hard Wired Contacts | 849 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 Low SF6 Gas Critical | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN211 | Hard Wired Contacts | 850 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_89T2 switch Ind | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN212 | Hard Wired Contacts | 851 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_89T2 Remote/Local Ctl House | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN213 | Hard Wired Contacts | 852 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 TCM1 | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN214 | Hard Wired Contacts | 853 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_52T2 TCM2 | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN215 | Hard Wired Contacts | 854 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F12 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN216 | Hard Wired Contacts | 855 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F13 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN217 | Hard Wired Contacts | 856 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F14 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN218 | Hard Wired Contacts | 857 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F15 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN219 | Hard Wired Contacts | 858 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_51F16 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN220 | Hard Wired Contacts | 859 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_87C2 Relay Fail | Transformer Relay | SEL_487E_87T2P_SEL.F_TARGET2_IN221 | Hard Wired Contacts | 860 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Communication Status | Transformer Relay | SEL_387A_87T2S_SEL_POU.Offline | Communication Status | 861 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_ Relay Enabled | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_EN | Relay Online | 862 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Software Alarm | Transformer Relay |  | Software Alarm |  | 0 = Alarm 1 = Normal | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Hardware Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_NOTALM | Hardware Alarm | 863 | 0 = Alarm 1 = Normal | Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Breaker Fail Initiate | Transformer Relay |  | Breaker Fail Initiate |  | 0 = Normal, 1 = BFI | Requested-Not Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_86T2S Trip Status | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN101 | Hard Wired Contacts | 864 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_86T2S Coil Fail Satus | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN102 | Hard Wired Contacts | 865 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_LTC Tank LO LVL Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN103 | Hard Wired Contacts | 866 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Main Tank LO LVL Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN104 | Hard Wired Contacts | 867 | 4 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Cool Control Loss of AC Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN105 | Hard Wired Contacts | 868 | 5 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Stage 1 Cooling Failure Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN106 | Hard Wired Contacts | 869 | 6 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Stage 2 Cooling Failure Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN201 | Hard Wired Contacts | 870 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Conservitor Tank LO LVL Alarm | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN202 | Hard Wired Contacts | 871 | 8 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Liquid Temp Trip | Transformer Relay | SEL_387A_87T2S_SEL.FM_INST_IN203 | Hard Wired Contacts | 872 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Communication Status | Bus Relay | SEL_587Z_87BT1_SEL_POU.Offline | Communication Status | 873 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Relay Enabled | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_EN | Relay Online | 874 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Software Alarm | Bus Relay |  | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_Hardware Alarm | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_ALARM | Hardware Alarm | 875 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_86BT1 Trip Status | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_IN1 | Hard Wired Contacts | 876 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-587Z-87BT1 | DAGGETT3_SUB1_SEL-587Z-87BT1_86BT1 Coil Fail Status | Bus Relay | SEL_587Z_87BT1_SEL.FM_INST_IN2 | Hard Wired Contacts | 877 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Communication Status | Bus Relay | SEL_587Z_87BT2_SEL_POU.Offline | Communication Status | 878 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Relay Enabled | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_EN | Relay Online | 879 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Software Alarm | Bus Relay |  | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_Hardware Alarm | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_ALARM | Hardware Alarm | 880 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_86BT1 Trip Status | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_IN1 | Hard Wired Contacts | 881 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-587Z-87BT2 | DAGGETT3_SUB1_SEL-587Z-87BT2_86BT1 Coil Fail Status | Bus Relay | SEL_587Z_87BT2_SEL.FM_INST_IN2 | Hard Wired Contacts | 882 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Communication Status | Breaker Relay | SEL_351S_51BFL1_SEL_POU.Offline | Communication Status | 883 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Relay Enabled | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_TLED11 | Relay Online | 884 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Software Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_SALARM | Software Alarm | 885 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Hardware Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_HALARM | Hardware Alarm | 886 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52L1 Breaker Status | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN101 | Hard Wired Contacts | 887 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_86BFL1 Trip Ind | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN102 | Hard Wired Contacts | 888 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_BFI | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN104 | Hard Wired Contacts | 889 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_DTT Received | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN105 | Hard Wired Contacts | 890 | 1 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52L1 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 891 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52L1 Remote/Local Ctl House | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN201 | Hard Wired Contacts | 892 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52BFL1 Loss of AC Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN204 | Hard Wired Contacts | 893 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52BFL1 Loss of DC Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN204 | Hard Wired Contacts | 894 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52BFL1 Spring Charge Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN204 | Hard Wired Contacts | 895 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52BFL1 Low SF6 Alarm | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN204 | Hard Wired Contacts | 896 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52L1 TCM1 | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN207 | Hard Wired Contacts | 897 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_52L1 TCM2 | Breaker Relay | SEL_351S_51BFL1_SEL.FM_INST_IN208 | Hard Wired Contacts | 898 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Communication Status | Breaker Relay |  | Communication Status |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Relay Enabled | Breaker Relay |  | Relay Online |  | 0 = Disabled, 1 = Enabled | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Software Alarm | Breaker Relay |  | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Hardware Alarm | Breaker Relay |  | Hardware Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52L1 Breaker Status | Breaker Relay |  | Hard Wired Contacts | 899 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_86BFL1 Trip Ind | Breaker Relay |  | Hard Wired Contacts | 900 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_BFI | Breaker Relay |  | Hard Wired Contacts | 901 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_DTT Received | Breaker Relay |  | Hard Wired Contacts | 902 | 1 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52L1 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 903 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52L1 Remote/Local Ctl House | Breaker Relay |  | Hard Wired Contacts | 904 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52BFL1 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts | 905 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52BFL1 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts | 906 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52BFL1 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts | 907 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52BFL1 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts | 908 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52L1 TCM1 | Breaker Relay |  | Hard Wired Contacts | 909 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_52L1 TCM2 | Breaker Relay |  | Hard Wired Contacts | 910 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Communication Status | Breaker Relay | SEL_351S_51F1_SEL_POU.Offline | Communication Status | 911 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Relay Enabled | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_TLED11 | Relay Online | 912 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Software Alarm | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_SALARM | Software Alarm | 913 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Hardware Alarm | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_HALARM | Hardware Alarm | 914 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Breaker Status | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN101 | Hard Wired Contacts | 915 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 916 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN102 | Hard Wired Contacts | 917 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Trip Ind | Breaker Relay |  | Hard Wired Contacts | 918 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 TCM1 | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN105 | Hard Wired Contacts | 919 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_52F1 TCM2 | Breaker Relay | SEL_351S_51F1_SEL.FM_INST_IN106 | Hard Wired Contacts | 920 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Communication Status | Breaker Relay | SEL_351S_51F2_SEL_POU.Offline | Communication Status | 921 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Relay Enabled | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_TLED11 | Relay Online | 922 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Software Alarm | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_SALARM | Software Alarm |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Hardware Alarm | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_HALARM | Hardware Alarm | 923 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Breaker Status | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN101 | Hard Wired Contacts | 924 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 925 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN102 | Hard Wired Contacts | 926 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 TCM1 | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN105 | Hard Wired Contacts | 927 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_52F2 TCM2 | Breaker Relay | SEL_351S_51F2_SEL.FM_INST_IN106 | Hard Wired Contacts | 928 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Communication Status | Breaker Relay | SEL_351S_51F3_SEL_POU.Offline | Communication Status | 929 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Relay Enabled | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_TLED11 | Relay Online | 930 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Software Alarm | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_SALARM | Software Alarm | 931 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Hardware Alarm | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_HALARM | Hardware Alarm | 932 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Breaker Status | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN101 | Hard Wired Contacts | 933 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F2 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 934 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN102 | Hard Wired Contacts | 935 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 TCM1 | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN105 | Hard Wired Contacts | 936 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_52F3 TCM2 | Breaker Relay | SEL_351S_51F3_SEL.FM_INST_IN106 | Hard Wired Contacts | 937 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Communication Status | Breaker Relay | SEL_351S_51F4_SEL_POU.Offline | Communication Status | 938 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Relay Enabled | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_TLED11 | Relay Online | 939 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Software Alarm | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_SALARM | Software Alarm | 940 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Hardware Alarm | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_HALARM | Hardware Alarm | 941 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Breaker Status | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN101 | Hard Wired Contacts | 942 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F2 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 943 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN102 | Hard Wired Contacts | 944 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 TCM1 | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN105 | Hard Wired Contacts | 945 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_52F4 TCM2 | Breaker Relay | SEL_351S_51F4_SEL.FM_INST_IN106 | Hard Wired Contacts | 946 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Communication Status | Breaker Relay | SEL_351S_51F5_SEL_POU.Offline | Hard Wired Contacts | 947 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Relay Enabled | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_TLED11 | Hard Wired Contacts | 948 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Software Alarm | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_SALARM | Hard Wired Contacts | 949 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Hardware Alarm | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_HALARM | Hard Wired Contacts | 950 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Breaker Status | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN101 | Hard Wired Contacts | 951 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 952 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN102 | Hard Wired Contacts | 953 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 TCM1 | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN105 | Hard Wired Contacts | 954 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_52F5 TCM2 | Breaker Relay | SEL_351S_51F5_SEL.FM_INST_IN106 | Hard Wired Contacts | 955 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Communication Status | Breaker Relay | SEL_351S_51F6_SEL_POU.Offline | Communication Status | 956 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Relay Enabled | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_TLED11 | Relay Online | 957 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Software Alarm | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_SALARM | Software Alarm | 958 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Hardware Alarm | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_HALARM | Hardware Alarm | 959 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Breaker Status | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN101 | Hard Wired Contacts | 960 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 961 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN102 | Hard Wired Contacts | 962 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 TCM1 | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN105 | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_52F6 TCM2 | Breaker Relay | SEL_351S_51F6_SEL.FM_INST_IN106 | Hard Wired Contacts | 963 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Communication Status | Breaker Relay | SEL_351S_51F7_SEL_POU.Offline | Communication Status | 964 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Relay Enabled | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_TLED11 | Relay Online | 965 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Software Alarm | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_SALARM | Software Alarm | 966 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Hardware Alarm | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_HALARM | Hardware Alarm | 967 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Breaker Status | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN101 | Hard Wired Contacts | 968 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 969 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN102 | Hard Wired Contacts | 970 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 TCM1 | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN105 | Hard Wired Contacts | 971 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_52F7 TCM2 | Breaker Relay | SEL_351S_51F7_SEL.FM_INST_IN106 | Hard Wired Contacts | 972 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Communication Status | Breaker Relay | SEL_351S_51F8_SEL_POU.Offline | Communication Status | 973 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Relay Enabled | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_TLED11 | Relay Online | 974 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Software Alarm | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_SALARM | Software Alarm | 975 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Hardware Alarm | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_HALARM | Hardware Alarm | 976 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Breaker Status | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN101 | Hard Wired Contacts | 977 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 978 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN102 | Hard Wired Contacts | 979 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 TCM1 | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN105 | Hard Wired Contacts | 980 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_52F8 TCM2 | Breaker Relay | SEL_351S_51F8_SEL.FM_INST_IN106 | Hard Wired Contacts | 981 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Communication Status | Breaker Relay | SEL_351S_51F9_SEL_POU.Offline | Communication Status | 982 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Relay Enabled | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_TLED11 | Relay Online | 983 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Software Alarm | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_SALARM | Software Alarm | 984 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Hardware Alarm | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_HALARM | Hardware Alarm | 985 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Breaker Status | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN101 | Hard Wired Contacts | 986 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 987 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN102 | Hard Wired Contacts | 988 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 TCM1 | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN105 | Hard Wired Contacts | 989 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_52F9 TCM2 | Breaker Relay | SEL_351S_51F9_SEL.FM_INST_IN106 | Hard Wired Contacts | 990 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Communication Status | Breaker Relay | SEL_351S_51F10_SEL_POU.Offline | Communication Status | 991 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Relay Enabled | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_TLED11 | Relay Online | 992 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Software Alarm | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_SALARM | Software Alarm | 993 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Hardware Alarm | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_HALARM | Hardware Alarm | 994 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Breaker Status | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN101 | Hard Wired Contacts | 995 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 996 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN102 | Hard Wired Contacts | 997 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 TCM1 | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN105 | Hard Wired Contacts | 998 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_52F10 TCM2 | Breaker Relay | SEL_351S_51F10_SEL.FM_INST_IN106 | Hard Wired Contacts | 999 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Communication Status | Breaker Relay | SEL_351S_51F11_SEL_POU.Offline | Communication Status | 1000 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Relay Enabled | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_TLED11 | Relay Online | 1001 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Software Alarm | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_SALARM | Software Alarm | 1002 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Hardware Alarm | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_HALARM | Hardware Alarm | 1003 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Breaker Status | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN101 | Hard Wired Contacts | 1004 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1005 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN102 | Hard Wired Contacts | 1006 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 TCM1 | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN105 | Hard Wired Contacts | 1007 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_52F11 TCM2 | Breaker Relay | SEL_351S_51F11_SEL.FM_INST_IN106 | Hard Wired Contacts | 1008 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Communication Status | Breaker Relay | SEL_351S_51F12_SEL_POU.Offline | Communication Status | 1009 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Relay Enabled | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_TLED11 | Relay Online | 1010 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Software Alarm | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_SALARM | Software Alarm | 1011 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Hardware Alarm | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_HALARM | Hardware Alarm | 1012 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Breaker Status | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN101 | Hard Wired Contacts | 1013 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1014 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN102 | Hard Wired Contacts | 1015 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 TCM1 | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN105 | Hard Wired Contacts | 1016 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_52F12 TCM2 | Breaker Relay | SEL_351S_51F12_SEL.FM_INST_IN106 | Hard Wired Contacts | 1017 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Communication Status | Breaker Relay | SEL_351S_51F13_SEL_POU.Offline | Communication Status | 1018 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Relay Enabled | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_TLED11 | Relay Online | 1019 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Software Alarm | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_SALARM | Software Alarm | 1020 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Hardware Alarm | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_HALARM | Hardware Alarm | 1021 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Breaker Status | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN101 | Hard Wired Contacts | 1022 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1023 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN102 | Hard Wired Contacts | 1024 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 TCM1 | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN105 | Hard Wired Contacts | 1025 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_52F13 TCM2 | Breaker Relay | SEL_351S_51F13_SEL.FM_INST_IN106 | Hard Wired Contacts | 1026 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Communication Status | Breaker Relay | SEL_351S_51F14_SEL_POU.Offline | Communication Status | 1027 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Relay Enabled | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_TLED11 | Relay Online | 1028 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Software Alarm | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_SALARM | Software Alarm | 1029 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Hardware Alarm | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_HALARM | Hardware Alarm | 1030 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Breaker Status | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN101 | Hard Wired Contacts | 1031 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1032 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN102 | Hard Wired Contacts | 1033 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 TCM1 | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN105 | Hard Wired Contacts | 1034 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_52F14 TCM2 | Breaker Relay | SEL_351S_51F14_SEL.FM_INST_IN106 | Hard Wired Contacts | 1035 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Communication Status | Breaker Relay | SEL_351S_51F15_SEL_POU.Offline | Communication Status | 1036 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Relay Enabled | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_TLED11 | Relay Online | 1037 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Software Alarm | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_SALARM | Software Alarm | 1038 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Hardware Alarm | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_HALARM | Hardware Alarm | 1039 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Breaker Status | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN101 | Hard Wired Contacts | 1040 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1041 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN102 | Hard Wired Contacts | 1042 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 TCM1 | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN105 | Hard Wired Contacts | 1043 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_52F15 TCM2 | Breaker Relay | SEL_351S_51F15_SEL.FM_INST_IN106 | Hard Wired Contacts | 1044 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Communication Status | Breaker Relay | SEL_351S_51F16_SEL_POU.Offline | Communication Status | 1045 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Relay Enabled | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_TLED11 | Relay Online | 1046 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Software Alarm | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_SALARM | Software Alarm | 1047 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Hardware Alarm | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_HALARM | Hardware Alarm | 1048 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Breaker Status | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN101 | Hard Wired Contacts | 1049 | 0 = Open, 1 = Closed | Not Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Remote/Local At Breaker | Breaker Relay |  | Hard Wired Contacts | 1050 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Remote/Local Ctl House | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN102 | Hard Wired Contacts | 1051 | 0 = Remote, 1 = Local | Not Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Loss of AC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Loss of DC Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Spring Charge Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 Low SF6 Alarm | Breaker Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 TCM1 | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN105 | Hard Wired Contacts | 1052 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_52F16 TCM2 | Breaker Relay | SEL_351S_51F16_SEL.FM_INST_IN106 | Hard Wired Contacts | 1053 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Communication Status | Discrete I/O | SEL_2440_DPAC_1_SEL_POU.Offline | Communication Status | 1054 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 2 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN101 | Hard Wired Contacts | 1055 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 3 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN102 | Hard Wired Contacts | 1056 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 7 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN103 | Hard Wired Contacts | 1057 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 8 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN104 | Hard Wired Contacts | 1058 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 9 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN105 | Hard Wired Contacts | 1059 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 10 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN106 | Hard Wired Contacts | 1060 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 11 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN107 | Hard Wired Contacts | 1061 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Rack 12 Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN108 | Hard Wired Contacts | 1062 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_Comm Rack Alarms | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN109 | Hard Wired Contacts | 1063 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F1 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN110 | Hard Wired Contacts | 1064 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F2 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN111 | Hard Wired Contacts | 1065 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F3 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN112 | Hard Wired Contacts | 1066 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F4 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN113 | Hard Wired Contacts | 1067 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F5 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN114 | Hard Wired Contacts | 1068 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F6 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN115 | Hard Wired Contacts | 1069 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F7 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN116 | Hard Wired Contacts | 1070 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F8 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN201 | Hard Wired Contacts | 1071 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F9 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN202 | Hard Wired Contacts | 1072 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F10 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN203 | Hard Wired Contacts | 1073 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F11 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN204 | Hard Wired Contacts | 1074 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52C1 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN205 | Hard Wired Contacts | 1075 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F12 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN206 | Hard Wired Contacts | 1076 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F13 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN207 | Hard Wired Contacts | 1077 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F14 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN208 | Hard Wired Contacts | 1078 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F15 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN209 | Hard Wired Contacts | 1079 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_52F16 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN210 | Hard Wired Contacts | 1080 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_87C2 Alarm | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN211 | Hard Wired Contacts | 1081 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1B Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN212 | Hard Wired Contacts | 1082 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1B Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN213 | Hard Wired Contacts | 1083 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_RAS-1B Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN214 | Hard Wired Contacts | 1084 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_RAS-1B Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN215 | Hard Wired Contacts | 1085 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1A Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN216 | Hard Wired Contacts | 1086 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_CRAS-1A Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN301 | Hard Wired Contacts | 1087 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_RAS-1A Channel Failure | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN302 | Hard Wired Contacts | 1088 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_RAS-1A Trip | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN303 | Hard Wired Contacts | 1089 | 0 = Normal, 1 = Trip | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L11 89a Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN304 | Hard Wired Contacts | 1090 | Close = 1, Open = 0 | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L12 89a Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN305 | Hard Wired Contacts | 1091 | Close = 1, Open = 0 | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89T1 89a Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN306 | Hard Wired Contacts | 1092 | Close = 1, Open = 0 | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89L21 89a Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN307 | Hard Wired Contacts | 1093 | Close = 1, Open = 0 | Not Requested-Available
SUB1 | SEL-2440-DPAC1 | DAGGETT3_SUB1_SEL-2440-DPAC1_89T2 89a Status | Discrete I/O | SEL_2440_DPAC_1_SEL.FM_INST_IN308 | Hard Wired Contacts | 1094 | Close = 1, Open = 0 | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Communication Status | Discrete I/O | SEL_2440_DPAC_2_SEL_POU.Offline | Communication Status | 1095 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Smoke/Heat Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN101 | Hard Wired Contacts | 1096 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Hydrogen 1 Percent Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN102 | Hard Wired Contacts | 1097 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_Door Alarms | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN103 | Hard Wired Contacts | 1098 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC 1 and 2 Trouble Alarm | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN104 | Hard Wired Contacts | 1099 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC Low Temp | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN105 | Hard Wired Contacts | 1100 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_HVAC High Temp | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN106 | Hard Wired Contacts | 1101 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_ATS Normal Source Available 1 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN107 | Hard Wired Contacts | 1102 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_ATS Normal Source Available 2 | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN108 | Hard Wired Contacts | 1103 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_ATS Normal | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN109 | Hard Wired Contacts | 1104 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2440-DPAC2 | DAGGETT3_SUB1_SEL-2440-DPAC2_ATS Emergency | Discrete I/O | SEL_2440_DPAC_2_SEL.FM_INST_IN110 | Hard Wired Contacts | 1105 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_Communication Status | Discrete I/O | SEL_2523_ANN_1_SEL_POU.Offline | Communication Status | 1106 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A1 | Hard Wired Contacts | 1107 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Low SF6 Pressure Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A2 | Hard Wired Contacts | 1108 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52L1 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A3 | Hard Wired Contacts | 1109 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A4 | Hard Wired Contacts | 1110 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Low SF6 Pressure Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A5 | Hard Wired Contacts | 1111 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52T1 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_A6 | Hard Wired Contacts | 1112 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_XFMR T1 Trouble | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B1 | Hard Wired Contacts | 1113 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B2 | Hard Wired Contacts | 1114 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F1 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B3 | Hard Wired Contacts | 1115 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F2 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B4 | Hard Wired Contacts | 1116 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F2 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B5 | Hard Wired Contacts | 1117 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F3 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_B6 | Hard Wired Contacts | 1118 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F3 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C1 | Hard Wired Contacts | 1119 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F4 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C2 | Hard Wired Contacts | 1120 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F4 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C3 | Hard Wired Contacts | 1121 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F5 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C4 | Hard Wired Contacts | 1122 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F5 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C5 | Hard Wired Contacts | 1123 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F6 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_C6 | Hard Wired Contacts | 1124 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F6 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D1 | Hard Wired Contacts | 1125 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F7 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D2 | Hard Wired Contacts | 1126 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F7 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D3 | Hard Wired Contacts | 1127 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F8 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D4 | Hard Wired Contacts | 1128 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F8 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D5 | Hard Wired Contacts | 1129 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F9 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_D6 | Hard Wired Contacts | 1130 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F9 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E1 | Hard Wired Contacts | 1131 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F10 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E2 | Hard Wired Contacts | 1132 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F10 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E3 | Hard Wired Contacts | 1133 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F11 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E4 | Hard Wired Contacts | 1134 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52F11 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E5 | Hard Wired Contacts | 1135 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52C1 Loss of Power | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_E6 | Hard Wired Contacts | 1136 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN1 | DAGGETT3_SUB1_SEL-2523-ANN1_52C1 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_1_SEL.FM_INST_IN_F1 | Hard Wired Contacts | 1137 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_Communication Status | Discrete I/O | SEL_2523_ANN_2_SEL_POU.Offline | Communication Status | 1138 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A1 | Hard Wired Contacts | 1139 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Low SF6 Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A2 | Hard Wired Contacts | 1140 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52T2 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A3 | Hard Wired Contacts | 1141 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_XFMR T2 Trouble | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A4 | Hard Wired Contacts | 1142 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F12 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A5 | Hard Wired Contacts | 1143 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F12 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_A6 | Hard Wired Contacts | 1144 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F13 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B1 | Hard Wired Contacts | 1145 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F13 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B2 | Hard Wired Contacts | 1146 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F14 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B3 | Hard Wired Contacts | 1147 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F14 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B4 | Hard Wired Contacts | 1148 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F15 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B5 | Hard Wired Contacts | 1149 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F15 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_B6 | Hard Wired Contacts | 1150 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F16 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C1 | Hard Wired Contacts | 1151 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52F16 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C2 | Hard Wired Contacts | 1152 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52C2 Loss of Power | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C3 | Hard Wired Contacts | 1153 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2523-ANN2 | DAGGETT3_SUB1_SEL-2523-ANN2_52C2 Spring Discharge Alarm | Discrete I/O | SEL_2523_ANN_2_SEL.FM_INST_IN_C4 | Hard Wired Contacts | 1154 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Communication Status | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1155 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Relay Enabled | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1156 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Software Alarm | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1157 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Hardware Alarm | Meter | SEL_735_OCM1_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1158 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Communication Status | Meter | SEL_735_OCM2_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1159 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Relay Enabled | Meter | SEL_735_OCM2_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1160 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Software Alarm | Meter | SEL_735_OCM2_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1161 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Hardware Alarm | Meter | SEL_735_OCM2_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1162 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Communication Status | Meter | SEL_735_OCM3_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1163 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Relay Enabled | Meter | SEL_735_OCM3_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1164 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Software Alarm | Meter | SEL_735_OCM3_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1165 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Hardware Alarm | Meter | SEL_735_OCM3_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1166 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Communication Status | Meter | SEL_735_OCM4_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1167 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Relay Enabled | Meter | SEL_735_OCM4_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1168 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Software Alarm | Meter | SEL_735_OCM4_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1169 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Hardware Alarm | Meter | SEL_735_OCM4_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1170 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Communication Status | Meter | SEL_735_OCM5_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1171 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Relay Enabled | Meter | SEL_735_OCM5_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1172 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Software Alarm | Meter | SEL_735_OCM5_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1173 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Hardware Alarm | Meter | SEL_735_OCM5_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1174 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Communication Status | Meter | SEL_735_OCM6_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1175 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Relay Enabled | Meter | SEL_735_OCM6_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1176 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Software Alarm | Meter | SEL_735_OCM6_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1177 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Hardware Alarm | Meter | SEL_735_OCM6_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1178 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Communication Status | Meter | SEL_735_OCM7_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1179 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Relay Enabled | Meter | SEL_735_OCM7_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1180 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Software Alarm | Meter | SEL_735_OCM7_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1181 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Hardware Alarm | Meter | SEL_735_OCM7_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1182 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Communication Status | Meter | SEL_735_OCM8_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1183 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Relay Enabled | Meter | SEL_735_OCM8_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1184 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Software Alarm | Meter | SEL_735_OCM8_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1185 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Hardware Alarm | Meter | SEL_735_OCM8_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1186 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Communication Status | Meter | SEL_735_OCM9_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1187 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Relay Enabled | Meter | SEL_735_OCM9_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1188 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Software Alarm | Meter | SEL_735_OCM9_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1189 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Hardware Alarm | Meter | SEL_735_OCM9_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1190 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Communication Status | Meter | SEL_735_OCM10_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1191 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Relay Enabled | Meter | SEL_735_OCM10_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1192 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Software Alarm | Meter | SEL_735_OCM10_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1193 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Hardware Alarm | Meter | SEL_735_OCM10_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1194 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Communication Status | Meter | SEL_735_OCM11_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1195 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Relay Enabled | Meter | SEL_735_OCM11_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1196 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Software Alarm | Meter | SEL_735_OCM11_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1197 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Hardware Alarm | Meter | SEL_735_OCM11_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1198 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Communication Status | Meter | SEL_735_OCM12_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1199 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Relay Enabled | Meter | SEL_735_OCM12_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1200 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Software Alarm | Meter | SEL_735_OCM12_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1201 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Hardware Alarm | Meter | SEL_735_OCM12_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1202 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Communication Status | Meter | SEL_735_OCM13_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1203 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Relay Enabled | Meter | SEL_735_OCM13_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1204 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Software Alarm | Meter | SEL_735_OCM13_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1205 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Hardware Alarm | Meter | SEL_735_OCM13_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1206 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Communication Status | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1207 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Oil Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00001_Oil_Temperature_High_Alarm | Transformer Alarms | 1208 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Winding Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00002_Winding_Temperature_High_Alarm | Transformer Alarms | 1209 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_High Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00003_High_Pressure_Alarm | Transformer Alarms | 1210 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Low Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00004_Low_Pressure_Alarm | Transformer Alarms | 1211 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Low Vacuum Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00005_Low_Vacuum_Alarm | Transformer Alarms | 1212 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Oil Level Low Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00006_Oil_Level_Low_Alarm | Transformer Alarms | 1213 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Sudden Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00007_Sudden_Pressure_Alarm | Transformer Alarms | 1214 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Loss Of Cooling Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00008_Loss_Of_Cooling_Alarm | Transformer Alarms | 1215 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Pressure Relief Device | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00010_Pressure_Relief_Device | Pressure Relief Device | 1216 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_AC Supply Fail | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00011_AC_Supply_Fail | AC Supply Fail | 1217 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_DC Supply Fail | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00012_DC_Supply_Fail | DC Supply Fail | 1218 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Buchholz Relay Alarm | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00013_Buchholz_Relay_Alarm | Buchholz Relay Alarm | 1219 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_OLTC Protect Relay | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00014_OLTC_Protect_Relay | OLTC Protect Relay | 1220 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Fans Failure | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00015_Fans_Failure | Fans Failure | 1221 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Fan Stage | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00016_Fan_Stage | Fan Stage | 1222 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Temperature Winding | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00017_Temperature_Winding | Temperature Winding | 1223 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Temperature Oil | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00018_Temperature_Oil | Temperature Oil | 1224 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T1 | DAGGETT3_SUB1_SEL-2414-49T1_Tap Position | Medium-High Voltage Transformer | SEL_2414_49T1_DNP.BINARY_INPUT_00019_Tap_Position | Tap Position | 1225 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Communication Status | Medium-High Voltage Transformer | _TAPCON_T1_90_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1226 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Oil Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Winding Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_High Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Low Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Low Vacuum Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Oil Level Low Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Sudden Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Fan Stage | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Temperature Winding | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Temperature Oil | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Tap Position | Medium-High Voltage Transformer | TAPCON_T1_90_DNP.BINARY_INPUT_00001_Tap_Position | Transformer Alarms | 1227 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | TAPCON-90T1 | DAGGETT3_SUB1_ TAPCON-90T1_Loss Of Cooling Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Communication Status | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1228 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Oil Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00001_Oil_Temperature_High_Alarm | Transformer Alarms | 1229 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Winding Temperature High Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00002_Winding_Temperature_High_Alarm | Transformer Alarms | 1230 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_High Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00003_High_Pressure_Alarm | Transformer Alarms | 1231 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Low Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00004_Low_Pressure_Alarm | Transformer Alarms | 1232 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Low Vacuum Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00005_Low_Vacuum_Alarm | Transformer Alarms | 1233 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Oil Level Low Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00006_Oil_Level_Low_Alarm | Transformer Alarms | 1234 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Sudden Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00007_Sudden_Pressure_Alarm | Transformer Alarms | 1235 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Loss Of Cooling Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00008_Loss_Of_Cooling_Alarm | Transformer Alarms | 1236 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Buchholz Relay Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00009_Buchholz_Relay_Alarm | Transformer Alarms | 1237 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_OLTC Protect Relay | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00010_OLTC_Protect_Relay | Transformer Alarms | 1238 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_LTC Tank Over Pressure Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00011_LTC_Tank_Over_Pressure_Alarm | Transformer Alarms | 1239 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_LTC Tank Low Level Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00012_LTC_Tank_Low_Level_Alarm | Transformer Alarms | 1240 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Cooling Control Loss of AC Alarm | Medium-High Voltage Transformer | SEL_2414_49T2_DNP.BINARY_INPUT_00013_Cooling_Control_Loss_of_VAC_Alarm | Transformer Alarms | 1241 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Fan Stage | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Temperature Winding | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Temperature Oil | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-2414-49T2 | DAGGETT3_SUB1_SEL-2414-49T2_Tap Position | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Communication Status | Medium-High Voltage Transformer | M2001C_T2_90_DNP.BINARY_INPUT_00000_Communications_Status | Communication Status | 1242 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Oil Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms | 1243 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Winding Temperature High Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_High Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Low Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Low Vacuum Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Oil Level Low Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Sudden Pressure Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Loss Of Cooling Alarm | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Fan Stage | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Temperature Winding | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Temperature Oil | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_Tap Position | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Communication Status | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00000_Communication_Status | Hard Wired Contacts | 1244 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_52T1 Status | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00001_INH5a | Hard Wired Contacts | 1245 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_52T2 Status | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00001_INH5c | Hard Wired Contacts | 1246 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_CRAS-1ACS On Ind | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00001_INH7a | Hard Wired Contacts | 1247 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_CRAS-1B Critical Failure | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00002_INH8a | Hard Wired Contacts | 1248 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_CRAS-1BCS On Ind | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00003_INH8c | Hard Wired Contacts | 1249 | 0= Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Hardware Alarm | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00004_NA | Hard Wired Contacts | 1250 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Software Alarm | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00005_NA | Hard Wired Contacts | 1251 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Breaker Fail Initiate | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00006_NA | Hard Wired Contacts | 1252 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Direct Transfer Trip | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00008_NA | Hard Wired Contacts | 1253 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Line Comm Cutout | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00009_NA | Hard Wired Contacts | 1254 | 0 = Normal, 1 = Cutout | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Line Comm Failure | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00010_NA | Hard Wired Contacts | 1255 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1A | DAGGETT3_SUB1_CRAS-1A_Relay Enabled | Line Relay | GE_N60_CRAS_1A_DNP.BINARY_INPUT_00011_NA | Hard Wired Contacts | 1256 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Communication Status | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00000_Communication_Status | Hard Wired Contacts | 1257 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_52T1 Status | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00001_INH5a | Hard Wired Contacts | 1258 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_52T2 Status | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00001_INH5c | Hard Wired Contacts | 1259 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_CRAS-1BCS On Ind | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00002_INH7a | Hard Wired Contacts | 1260 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_CRAS-1A Critical Failure | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00003_INH8a | Hard Wired Contacts | 1261 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_CRAS-1ACS On Ind | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00004_INH8c | Hard Wired Contacts | 1262 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Breaker Fail Initiate | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00005_NA | Hard Wired Contacts | 1263 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Direct Transfer Trip | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00007_NA | Hard Wired Contacts | 1264 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Hardware Alarm | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00008_NA | Hard Wired Contacts | 1265 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Line Comm Cutout | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00009_NA | Hard Wired Contacts | 1266 | 0 = Normal, 1 = Cutout | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Line Comm Failure | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00010_NA | Hard Wired Contacts | 1267 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Relay Enabled | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00011_NA | Hard Wired Contacts | 1268 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | CRAS-1B | DAGGETT3_SUB1_CRAS-1B_Software Alarm | Line Relay | GE_N60_CRAS_1B_DNP.BINARY_INPUT_00012_NA | Hard Wired Contacts | 1269 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Communication Status | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00001_NA | Hard Wired Contacts | 1270 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Relay Enabled | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00002_NA | Hard Wired Contacts | 1271 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Direct Transfer Trip | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00003_NA | Hard Wired Contacts | 1272 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Breaker Fail Initiate | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00004_NA | Hard Wired Contacts | 1273 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Hardware Alarm | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00005_NA | Hard Wired Contacts | 1274 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Software Alarm | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00006_NA | Hard Wired Contacts | 1275 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Line Comm Cutout | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00007_NA | Hard Wired Contacts | 1276 | 0 = Normal, 1 = Cutout | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_Line Comm Failure | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00008_NA | Hard Wired Contacts | 1277 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1A | DAGGETT3_SUB1_RAS-1A_RAS-1ACS On Ind | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00009_INH7a | Hard Wired Contacts | 1278 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Communication Status | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00001_NA | Hard Wired Contacts | 1279 | 0 = Offline, 1 = Online | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Relay Enabled | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00002_NA | Hard Wired Contacts | 1280 | 0 = Disabled, 1 = Enabled | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Direct Transfer Trip | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00003_NA | Hard Wired Contacts | 1281 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Breaker Fail Initiate | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00004_NA | Hard Wired Contacts | 1282 | 0 = Normal, 1 = BFI | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Hardware Alarm | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00005_NA | Hard Wired Contacts | 1283 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Software Alarm | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00006_NA | Hard Wired Contacts | 1284 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Line Comm Cutout | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00007_NA | Hard Wired Contacts | 1285 | 0 = Normal, 1 = Cutout | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_Line Comm Failure | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00008_NA | Hard Wired Contacts | 1286 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | RAS-1B | DAGGETT3_SUB1_RAS-1B_RAS-1BCS On Ind | Line Relay | GE_N60_RAS_1A_DNP.BINARY_INPUT_00009_INH7a | Hard Wired Contacts | 1287 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Communication Status | Medium-High Voltage Transformer |  | Transformer Alarms |  | 0 = Offline, 1 = Online | Requested-Not Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Gas | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00000_Gas | Transformer Alarms | 1288 | 1 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Moisture | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00001_Moisture | Transformer Alarms | 1289 | 2 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Gas HI | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00002_Gas_HI | Transformer Alarms | 1290 | 3 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Gas HI HI | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00003_Gas_HI_HI | Transformer Alarms | 1291 | 4 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Moisture HI | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00004_Moisture_HI | Transformer Alarms | 1292 | 5 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Moisture HI HI | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00005_Moisture_HI_HI | Transformer Alarms | 1293 | 6 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Fan Stage | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00006_Fan_Stage | Transformer Alarms | 1294 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_High Pressure Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00007_High_Pressure_Alarm | Transformer Alarms | 1295 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Loss Of Cooling Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00008_Loss_Of_Cooling_Alarm | Transformer Alarms | 1296 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Low Pressure Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00009_Low_Pressure_Alarm | Transformer Alarms | 1297 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Low Vacuum Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00010_Low_Vacuum_Alarm | Transformer Alarms | 1298 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Oil Level | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00011_Oil_Level | Transformer Alarms | 1299 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Oil Level Low Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00012_Oil_Level_Low_Alarm | Transformer Alarms | 1300 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Oil Temperature High Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00013_Oil_Temperature_High_Alarm | Transformer Alarms | 1301 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Pressure | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00014_Pressure | Transformer Alarms | 1302 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Sudden Pressure Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00015_Sudden_Pressure_Alarm | Transformer Alarms | 1303 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Tap Position | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00016_Tap_Position | Transformer Alarms | 1304 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Temperature Oil | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00017_Temperature_Oil | Transformer Alarms | 1305 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Temperature Winding | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00018_Temperature_Winding | Transformer Alarms | 1306 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | HYDRAN-M2 | DAGGETT3_SUB1_HYDRAN-M2_Winding Temperature High Alarm | Medium-High Voltage Transformer | HYDRAN_M2_DNP.BINARY_INPUT_00019_Winding_Temperature_High_Alarm | Transformer Alarms | 1307 | 7 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_Communication Status | Reactive Power Relay | SEL_487V_87C1_SEL_POU.Offline | Communication Status | 1308 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_Relay Enabled | Reactive Power Relay | SEL_487V_87C1_SEL_POU.EN | Relay Online | 1309 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_Software Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_SALARM | Software Alarm | 1310 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_Hardware Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.FM_INST_HALARM | Hardware Alarm | 1311 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Breaker Status | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN101 | Hard Wired Contacts | 1312 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Remote/Local Ctl House | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN102 | Hard Wired Contacts | 1313 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Switch Status | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 1314 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Remote/Local Ctl House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 1315 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 1316 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN303 | Hard Wired Contacts | 1317 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 1318 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN208 | Hard Wired Contacts | 1319 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 1320 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN302 | Hard Wired Contacts | 1321 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 Low SF6 Lockout | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 1322 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Low SF6 Lockout | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN301 | Hard Wired Contacts | 1323 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 TCM1 | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN103 | Hard Wired Contacts | 1324 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_52C1 TCM2 | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN104 | Hard Wired Contacts | 1325 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 TCM | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN105 | Hard Wired Contacts | 1326 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Switch Status | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN207 | Hard Wired Contacts | 1327 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Remote/Local Ctl House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN303 | Hard Wired Contacts | 1328 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 TCM | Reactive Power Relay | SEL_487V_87C1_SEL.F_TARGET2_IN201 | Hard Wired Contacts | 1329 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Communication Status | Reactive Power Relay | SEL_487V_87C2_SEL_POU.Offline | Communication Status | 1330 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Relay Enabled | Reactive Power Relay | SEL_487V_87C2_SEL_POU.EN | Relay Online | 1331 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Software Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_SALARM | Software Alarm | 1332 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Hardware Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.FM_INST_HALARM | Hardware Alarm | 1333 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Breaker Status | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN101 | Hard Wired Contacts | 1334 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Remote/Local Ctl House | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN102 | Hard Wired Contacts | 1335 | 0 = Remote, 1 = Local | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Loss of AC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Loss of DC Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Spring Charge Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 Low SF6 Alarm | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Normal, 1 = Alarm | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Switch Status | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN202 | Hard Wired Contacts | 1336 | 0 = Open, 1 = Closed | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Remote/Local At Breaker | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Remote/Local Ctl House | Reactive Power Relay |  | Hard Wired Contacts |  | 0 = Remote, 1 = Local | Requested-Not Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Loss of AC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 1337 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Loss of DC Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN206 | Hard Wired Contacts | 1338 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Spring Charge Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN203 | Hard Wired Contacts | 1339 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 Low SF6 Alarm | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN205 | Hard Wired Contacts | 1340 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 TCM1 | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN103 | Hard Wired Contacts | 1341 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_52C2 TCM2 | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN104 | Hard Wired Contacts | 1342 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 TCM | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN105 | Hard Wired Contacts | 1343 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_Low SF6 lockout | Reactive Power Relay | SEL_487V_87C2_SEL.F_TARGET2_IN204 | Hard Wired Contacts | 1344 | 0 = Normal, 1 = Alarm | Not Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Communication Status | Meter | ION_8650_CAISO_1A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1345 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Relay Enabled | Meter | ION_8650_CAISO_1A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1346 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Software Alarm | Meter | ION_8650_CAISO_1A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1347 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Hardware Alarm | Meter | ION_8650_CAISO_1A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1348 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Communication Status | Meter | ION_8650_CAISO_1B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1349 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Relay Enabled | Meter | ION_8650_CAISO_1B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1350 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Software Alarm | Meter | ION_8650_CAISO_1B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1351 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Hardware Alarm | Meter | ION_8650_CAISO_1B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1352 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Communication Status | Meter | ION_8650_CAISO_1C_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1353 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Relay Enabled | Meter | ION_8650_CAISO_1C_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1354 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Software Alarm | Meter | ION_8650_CAISO_1C_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1355 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Hardware Alarm | Meter | ION_8650_CAISO_1C_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1356 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Communication Status | Meter | ION_8650_CAISO_1D_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1357 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Relay Enabled | Meter | ION_8650_CAISO_1D_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1358 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Software Alarm | Meter | ION_8650_CAISO_1D_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1359 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Hardware Alarm | Meter | ION_8650_CAISO_1D_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1360 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Communication Status | Meter | ION_8650_CAISO_2A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1361 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Relay Enabled | Meter | ION_8650_CAISO_2A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1362 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Software Alarm | Meter | ION_8650_CAISO_2A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1363 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Hardware Alarm | Meter | ION_8650_CAISO_2A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1364 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Communication Status | Meter | ION_8650_CAISO_2B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1365 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Relay Enabled | Meter | ION_8650_CAISO_2B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1366 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Software Alarm | Meter | ION_8650_CAISO_2B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1367 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Hardware Alarm | Meter | ION_8650_CAISO_2B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1368 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Communication Status | Meter | ION_8650_CAISO_3A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1369 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Relay Enabled | Meter | ION_8650_CAISO_3A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1370 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Software Alarm | Meter | ION_8650_CAISO_3A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1371 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Hardware Alarm | Meter | ION_8650_CAISO_3A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1372 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Communication Status | Meter | ION_8650_CAISO_3B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1373 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Relay Enabled | Meter | ION_8650_CAISO_3B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1374 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Software Alarm | Meter | ION_8650_CAISO_3B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1375 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Hardware Alarm | Meter | ION_8650_CAISO_3B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1376 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Communication Status | Meter | ION_8650_CAISO_4A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1377 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Relay Enabled | Meter | ION_8650_CAISO_4A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1378 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Software Alarm | Meter | ION_8650_CAISO_4A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1379 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Hardware Alarm | Meter | ION_8650_CAISO_4A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1380 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Communication Status | Meter | ION_8650_CAISO_4B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1381 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Relay Enabled | Meter | ION_8650_CAISO_4B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1382 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Software Alarm | Meter | ION_8650_CAISO_4B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1383 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Hardware Alarm | Meter | ION_8650_CAISO_4B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1384 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Communication Status | Meter | ION_8650_CAISO_5A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1385 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Relay Enabled | Meter | ION_8650_CAISO_5A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1386 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Software Alarm | Meter | ION_8650_CAISO_5A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1387 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Hardware Alarm | Meter | ION_8650_CAISO_5A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1388 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Communication Status | Meter | ION_8650_CAISO_5B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1389 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Relay Enabled | Meter | ION_8650_CAISO_5B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1390 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Software Alarm | Meter | ION_8650_CAISO_5B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1391 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Hardware Alarm | Meter | ION_8650_CAISO_5B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1392 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Communication Status | Meter | ION_8650_CAISO_6A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1393 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Relay Enabled | Meter | ION_8650_CAISO_6A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1394 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Software Alarm | Meter | ION_8650_CAISO_6A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1395 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Hardware Alarm | Meter | ION_8650_CAISO_6A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1396 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Communication Status | Meter | ION_8650_CAISO_6B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1397 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Relay Enabled | Meter | ION_8650_CAISO_6B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1398 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Software Alarm | Meter | ION_8650_CAISO_6B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1399 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Hardware Alarm | Meter | ION_8650_CAISO_6B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1400 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Communication Status | Meter | ION_8650_CAISO_7A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1401 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Relay Enabled | Meter | ION_8650_CAISO_7A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1402 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Software Alarm | Meter | ION_8650_CAISO_7A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1403 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Hardware Alarm | Meter | ION_8650_CAISO_7A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1404 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Communication Status | Meter | ION_8650_CAISO_7B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1405 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Relay Enabled | Meter | ION_8650_CAISO_7B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1406 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Software Alarm | Meter | ION_8650_CAISO_7B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1407 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Hardware Alarm | Meter | ION_8650_CAISO_7B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1408 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Communication Status | Meter | ION_8650_CAISO_8A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1409 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Relay Enabled | Meter | ION_8650_CAISO_8A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1410 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Software Alarm | Meter | ION_8650_CAISO_8A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1411 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Hardware Alarm | Meter | ION_8650_CAISO_8A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1412 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Communication Status | Meter | ION_8650_CAISO_8B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1413 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Relay Enabled | Meter | ION_8650_CAISO_8B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1414 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Software Alarm | Meter | ION_8650_CAISO_8B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1415 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Hardware Alarm | Meter | ION_8650_CAISO_8B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1416 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Communication Status | Meter | ION_8650_CAISO_9A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1417 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Relay Enabled | Meter | ION_8650_CAISO_9A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1418 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Software Alarm | Meter | ION_8650_CAISO_9A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1419 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Hardware Alarm | Meter | ION_8650_CAISO_9A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1420 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Communication Status | Meter | ION_8650_CAISO_9B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1421 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Relay Enabled | Meter | ION_8650_CAISO_9B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1422 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Software Alarm | Meter | ION_8650_CAISO_9B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1423 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Hardware Alarm | Meter | ION_8650_CAISO_9B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1424 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Communication Status | Meter | ION_8650_CAISO_10A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1425 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Relay Enabled | Meter | ION_8650_CAISO_10A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1426 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Software Alarm | Meter | ION_8650_CAISO_10A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1427 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Hardware Alarm | Meter | ION_8650_CAISO_10A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1428 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Communication Status | Meter | ION_8650_CAISO_10B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1429 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Relay Enabled | Meter | ION_8650_CAISO_10B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1430 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Software Alarm | Meter | ION_8650_CAISO_10B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1431 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Hardware Alarm | Meter | ION_8650_CAISO_10B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1432 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Communication Status | Meter | ION_8650_CAISO_11A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1433 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Relay Enabled | Meter | ION_8650_CAISO_11A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1434 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Software Alarm | Meter | ION_8650_CAISO_11A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1435 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Hardware Alarm | Meter | ION_8650_CAISO_11A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1436 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Communication Status | Meter | ION_8650_CAISO_11B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1437 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Relay Enabled | Meter | ION_8650_CAISO_11B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1438 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Software Alarm | Meter | ION_8650_CAISO_11B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1439 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Hardware Alarm | Meter | ION_8650_CAISO_11B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1440 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Communication Status | Meter | ION_8650_CAISO_12A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1441 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Relay Enabled | Meter | ION_8650_CAISO_12A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1442 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Software Alarm | Meter | ION_8650_CAISO_12A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1443 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Hardware Alarm | Meter | ION_8650_CAISO_12A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1444 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Communication Status | Meter | ION_8650_CAISO_12B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1445 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Relay Enabled | Meter | ION_8650_CAISO_12B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1446 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Software Alarm | Meter | ION_8650_CAISO_12B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1447 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Hardware Alarm | Meter | ION_8650_CAISO_12B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1448 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Communication Status | Meter | ION_8650_CAISO_13A_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1449 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Relay Enabled | Meter | ION_8650_CAISO_13A_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1450 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Software Alarm | Meter | ION_8650_CAISO_13A_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1451 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Hardware Alarm | Meter | ION_8650_CAISO_13A_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1452 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Communication Status | Meter | ION_8650_CAISO_13B_DNP.BINARY_INPUT_00000_Communication_Status | Communication Status | 1453 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Relay Enabled | Meter | ION_8650_CAISO_13B_DNP.BINARY_INPUT_00001_Relay_Online | Relay Online | 1454 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Software Alarm | Meter | ION_8650_CAISO_13B_DNP.BINARY_INPUT_00002_Software_Alarm | Software Alarm | 1455 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Hardware Alarm | Meter | ION_8650_CAISO_13B_DNP.BINARY_INPUT_00003_Hardware_Alarm | Hardware Alarm | 1456 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_Communication Status | Discrete I/O | SEL_2515_FAA_STR47_SEL_POU.Offline | Communication Status | 1457 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_Relay Enabled | Discrete I/O | SEL_2515_FAA_STR47_SEL_POU.EN | Relay Online | 1458 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_Relay Alarm | Discrete I/O | SEL_2515_STR_47_SEL.FM_INST_ALARM | Hardware Alarm | 1459 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_ J4-3 Mode | Discrete I/O | SEL_2515_FAA_STR47_SEL.FM_INST_IN1 | Hardware Alarm | 1460 | 0 = Day, 1 = Night | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_ J4-6 Beacon Alarm | Discrete I/O | SEL_2515_FAA_STR47_SEL.FM_INST_IN2 | Hardware Alarm | 1461 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_ J5-3 Marker Alarm | Discrete I/O | SEL_2515_FAA_STR47_SEL.FM_INST_IN3 | Hardware Alarm | 1462 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR47 | DAGGETT3_SUB1_SEL-2515-FAA-STR47_ J5-5 Photodiode Alarm | Discrete I/O | SEL_2515_FAA_STR47_SEL.FM_INST_IN4 | Hardware Alarm | 1463 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_Communication Status | Discrete I/O | SEL_2515_FAA_STR48_SEL_POU.Offline | Communication Status | 1464 | 0 = Offline, 1 = Online | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_Relay Enabled | Discrete I/O | SEL_2515_FAA_STR48_SEL_POU.EN | Relay Online | 1465 | 0 = Disabled, 1 = Enabled | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_Relay Alarm | Discrete I/O | SEL_2515_STR_48_SEL.FM_INST_ALARM | Hardware Alarm | 1466 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_ J4-3 Mode | Discrete I/O | SEL_2515_FAA_STR48_SEL.FM_INST_IN1 | Hardware Alarm | 1467 | 0 = Day, 1 = Night | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_ J4-6 Beacon Alarm | Discrete I/O | SEL_2515_FAA_STR48_SEL.FM_INST_IN2 | Hardware Alarm | 1468 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_ J5-3 Marker Alarm | Discrete I/O | SEL_2515_FAA_STR48_SEL.FM_INST_IN3 | Hardware Alarm | 1469 | 0 = Normal, 1 = Alarm | Requested-Available
SUB1 | SEL-2515-FAA-STR48 | DAGGETT3_SUB1_SEL-2515-FAA-STR48_ J5-5 Photodiode Alarm | Discrete I/O | SEL_2515_FAA_STR48_SEL.FM_INST_IN4 | Hardware Alarm | 1470 | 0 = Normal, 1 = Alarm | Requested-Available
Counters
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | ROLLOVER VALUE
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site Total Energy Chrg | PPC | PPC.bessStatus.totalSiteEnergyChg_kwh | Total Power Plant Energy Charged To Date | 0 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site Ttl Energy Dischrg | PPC | PPC.bessStatus.totalSiteEnergyDischg_kwh | Total Power Plant Energy Discharged To Date | 1 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Aux Total Energy Used | PPC | PPC.bessStatus.totalAuxEnergy_kwh | Total Power Plant Auxiliary Energy Used to Date | 2 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS Total Energy Chrg | PPC | PPC.bessStatus.totalEssEnergyChg_kwh | Total Site ESS Energy Charged To Date | 3 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS Ttl Energy Dischrg | PPC | PPC.bessStatus.totalEssEnergyDischg_kwh | Total Site ESS Energy Discharged To Date | 4 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Total Energy Chrg | PPC | PPC.bessStatus.ess01_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 5 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess01_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 6 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Total Energy Chrg | PPC | PPC.bessStatus.ess02_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 7 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess02_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 8 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Total Energy Chrg | PPC | PPC.bessStatus.ess03_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 9 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess03_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 10 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Total Energy Chrg | PPC | PPC.bessStatus.ess04_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 11 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess04_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 12 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Total Energy Chrg | PPC | PPC.bessStatus.ess05_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 13 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess05_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 14 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Total Energy Chrg | PPC | PPC.bessStatus.ess06_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 15 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess06_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 16 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Total Energy Chrg | PPC | PPC.bessStatus.ess07_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 17 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess07_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 18 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Total Energy Chrg | PPC | PPC.bessStatus.ess08_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 19 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess08_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 20 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Total Energy Chrg | PPC | PPC.bessStatus.ess09_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 21 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess09_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 22 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Total Energy Chrg | PPC | PPC.bessStatus.ess10_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 23 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess10_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 24 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Total Energy Chrg | PPC | PPC.bessStatus.ess11_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 25 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess11_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 26 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Total Energy Chrg | PPC | PPC.bessStatus.ess12_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 27 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess12_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 28 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Total Energy Chrg | PPC | PPC.bessStatus.ess13_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 29 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess13_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 30 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Total Energy Chrg | PPC | PPC.bessStatus.ess14_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 31 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess14_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 32 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Total Energy Chrg | PPC | PPC.bessStatus.ess15_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 33 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess15_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 34 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Total Energy Chrg | PPC | PPC.bessStatus.ess16_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 35 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess16_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 36 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Total Energy Chrg | PPC | PPC.bessStatus.ess17_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 37 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess17_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 38 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Total Energy Chrg | PPC | PPC.bessStatus.ess18_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 39 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess18_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 40 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Total Energy Chrg | PPC | PPC.bessStatus.ess19_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 41 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess19_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 42 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Total Energy Chrg | PPC | PPC.bessStatus.ess20_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 43 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess20_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 44 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site Total Energy Chrg | PPC | PPC.bessStatus.totalSiteEnergyChg_kwh | Total Power Plant Energy Charged To Date | 45 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site Ttl Energy Dischrg | PPC | PPC.bessStatus.totalSiteEnergyDischg_kwh | Total Power Plant Energy Discharged To Date | 46 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Aux Total Energy Used | PPC | PPC.bessStatus.totalAuxEnergy_kwh | Total Power Plant Auxiliary Energy Used to Date | 47 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS Total Energy Chrg | PPC | PPC.bessStatus.totalEssEnergyChg_kwh | Total Site ESS Energy Charged To Date | 48 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS Ttl Energy Dischrg | PPC | PPC.bessStatus.totalEssEnergyDischg_kwh | Total Site ESS Energy Discharged To Date | 49 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Total Energy Chrg | PPC | PPC.bessStatus.ess01_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 50 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess01_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 51 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Total Energy Chrg | PPC | PPC.bessStatus.ess02_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 52 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess02_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 53 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Total Energy Chrg | PPC | PPC.bessStatus.ess03_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 54 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess03_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 55 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Total Energy Chrg | PPC | PPC.bessStatus.ess04_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 56 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess04_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 57 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site Total Energy Chrg | PPC | PPC.bessStatus.totalSiteEnergyChg_kwh | Total Power Plant Energy Charged To Date | 58 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site Ttl Energy Dischrg | PPC | PPC.bessStatus.totalSiteEnergyDischg_kwh | Total Power Plant Energy Discharged To Date | 59 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Aux Total Energy Used | PPC | PPC.bessStatus.totalAuxEnergy_kwh | Total Power Plant Auxiliary Energy Used to Date | 60 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS Total Energy Chrg | PPC | PPC.bessStatus.totalEssEnergyChg_kwh | Total Site ESS Energy Charged To Date | 61 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS Ttl Energy Dischrg | PPC | PPC.bessStatus.totalEssEnergyDischg_kwh | Total Site ESS Energy Discharged To Date | 62 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Total Energy Chrg | PPC | PPC.bessStatus.ess01_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 63 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess01_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 64 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Total Energy Chrg | PPC | PPC.bessStatus.ess02_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 65 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess02_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 66 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Total Energy Chrg | PPC | PPC.bessStatus.ess03_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 67 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess03_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 68 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Total Energy Chrg | PPC | PPC.bessStatus.ess04_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 69 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess04_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 70 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Total Energy Chrg | PPC | PPC.bessStatus.ess05_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 71 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess05_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 72 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site Total Energy Chrg | PPC | PPC.bessStatus.totalSiteEnergyChg_kwh | Total Power Plant Energy Charged To Date | 73 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site Ttl Energy Dischrg | PPC | PPC.bessStatus.totalSiteEnergyDischg_kwh | Total Power Plant Energy Discharged To Date | 74 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Aux Total Energy Used | PPC | PPC.bessStatus.totalAuxEnergy_kwh | Total Power Plant Auxiliary Energy Used to Date | 75 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS Total Energy Chrg | PPC | PPC.bessStatus.totalEssEnergyChg_kwh | Total Site ESS Energy Charged To Date | 76 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS Ttl Energy Dischrg | PPC | PPC.bessStatus.totalEssEnergyDischg_kwh | Total Site ESS Energy Discharged To Date | 77 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Total Energy Chrg | PPC | PPC.bessStatus.ess01_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 78 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess01_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 79 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Total Energy Chrg | PPC | PPC.bessStatus.ess02_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 80 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess02_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 81 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Total Energy Chrg | PPC | PPC.bessStatus.ess03_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 82 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess03_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 83 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Total Energy Chrg | PPC | PPC.bessStatus.ess04_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 84 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess04_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 85 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Total Energy Chrg | PPC | PPC.bessStatus.ess05_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 86 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess05_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 87 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Total Energy Chrg | PPC | PPC.bessStatus.ess06_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 88 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess06_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 89 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Total Energy Chrg | PPC | PPC.bessStatus.ess07_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 90 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess07_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 91 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Total Energy Chrg | PPC | PPC.bessStatus.ess08_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 92 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess08_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 93 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Total Energy Chrg | PPC | PPC.bessStatus.ess09_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 94 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess09_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 95 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Total Energy Chrg | PPC | PPC.bessStatus.ess10_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 96 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess10_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 97 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Total Energy Chrg | PPC | PPC.bessStatus.ess11_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 98 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess11_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 99 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Total Energy Chrg | PPC | PPC.bessStatus.ess12_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 100 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess12_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 101 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Total Energy Chrg | PPC | PPC.bessStatus.ess13_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 102 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess13_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 103 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Total Energy Chrg | PPC | PPC.bessStatus.ess14_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 104 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess14_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 105 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Total Energy Chrg | PPC | PPC.bessStatus.ess15_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 106 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess15_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 107 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Total Energy Chrg | PPC | PPC.bessStatus.ess16_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 108 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess16_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 109 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Total Energy Chrg | PPC | PPC.bessStatus.ess17_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 110 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess17_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 111 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Total Energy Chrg | PPC | PPC.bessStatus.ess18_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 112 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess18_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 113 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Total Energy Chrg | PPC | PPC.bessStatus.ess19_totalEnergyChg_kwh | Total ESS Unit Energy Charged To Date | 114 | KWh | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Ttl Energy Dischrg | PPC | PPC.bessStatus.ess19_totalEnergyDischg_kwh | Total ESS Unit Energy Discharged To Date | 115 | KWh | Not Requested-Available
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Energy Received | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3PWP_MWH | Energy Received | 116 | MWh | Requested-Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Energy Delivered | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3PXP_MWH | Energy Delivered | 117 | MWh | Requested-Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Energy Received | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3QWP_MVARH | Reactive Energy Received | 118 | MVARh | Requested-Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_Reactive Energy Delivered | Transformer Relay | SEL_487E_87T1P_SEL.F_METER2_3QWXP_MVARH | Reactive Energy Delivered | 119 | MVARh | Requested-Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T1P | DAGGETT3_SUB1_SEL-487E-87T1P_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Energy Received | Transformer Relay |  | Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Energy Delivered | Transformer Relay |  | Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Energy Received | Transformer Relay |  | Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_Reactive Energy Delivered | Transformer Relay |  | Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T1S | DAGGETT3_SUB1_SEL-387A-87T1S_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Energy Received | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3PWP_MWH | Energy Received | 120 | MWh | Requested-Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Energy Delivered | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3PXP_MWH | Energy Delivered | 121 | MWh | Requested-Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Energy Received | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3QWP_MVARH | Reactive Energy Received | 122 | MVARh | Requested-Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_Reactive Energy Delivered | Transformer Relay | SEL_487E_87T2P_SEL.F_METER2_3QWXP_MVARH | Reactive Energy Delivered | 123 | MVARh | Requested-Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-487E-87T2P | DAGGETT3_SUB1_SEL-487E-87T2P_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Energy Received | Transformer Relay |  | Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Energy Delivered | Transformer Relay |  | Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Energy Received | Transformer Relay |  | Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_Reactive Energy Delivered | Transformer Relay |  | Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Energy Received | Transformer Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Energy Delivered | Transformer Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Reactive Energy Received | Transformer Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_A Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_B Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-387A-87T2S | DAGGETT3_SUB1_SEL-387A-87T2S_C Phase Reactive Energy Delivered | Transformer Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_004_MWH3_REC | Energy Received | 124 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 125 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Reactive Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 126 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_Reactive Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 127 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 128 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 129 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 130 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 131 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 132 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 133 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 134 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 135 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 136 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 137 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 138 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL1 | DAGGETT3_SUB1_SEL-351S-50BFL1_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_50BFL1_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 139 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Energy Received | Breaker Relay |  | Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Energy Delivered | Breaker Relay |  | Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Reactive Energy Received | Breaker Relay |  | Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_Reactive Energy Delivered | Breaker Relay |  | Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Energy Received | Breaker Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Energy Received | Breaker Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Energy Received | Breaker Relay |  | Phase Energy Received |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Energy Delivered | Breaker Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Energy Delivered | Breaker Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Energy Delivered | Breaker Relay |  | Phase Energy Delivered |  | MWh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Reactive Energy Received | Breaker Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Reactive Energy Received | Breaker Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Reactive Energy Received | Breaker Relay |  | Phase Reactive Energy Received |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_A Phase Reactive Energy Delivered | Breaker Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_B Phase Reactive Energy Delivered | Breaker Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-50BFL2 | DAGGETT3_SUB1_SEL-351S-50BFL2_C Phase Reactive Energy Delivered | Breaker Relay |  | Phase Reactive Energy Delivered |  | MVARh | Requested-Not Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_004_MWH3_REC | Energy Received | 140 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 141 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 142 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 143 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 144 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 145 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 146 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 147 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 148 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 149 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 150 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 151 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F1_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 152 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 153 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 154 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F1 | DAGGETT3_SUB1_SEL-351S-52F1_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F1_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 155 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_004_MWH3_REC | Energy Received | 156 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 157 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 158 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 159 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 160 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 161 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 162 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 163 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 164 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 165 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 166 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 167 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F2_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 168 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 169 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 170 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F2 | DAGGETT3_SUB1_SEL-351S-52F2_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F2_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 171 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_004_MWH3_REC | Energy Received | 172 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 173 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 174 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 175 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_A Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 176 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_B Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 177 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_C Phase Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 178 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 179 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 180 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 181 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 182 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 183 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F3_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 184 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 185 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 186 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F3 | DAGGETT3_SUB1_SEL-351S-52F3_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F3_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 187 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_004_MWH3_REC | Energy Received | 188 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 189 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 190 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 191 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 192 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 193 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 194 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 195 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 196 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 197 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 198 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 199 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F4_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 200 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 201 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 202 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F4 | DAGGETT3_SUB1_SEL-351S-52F4_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F4_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 203 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_004_MWH3_REC | Energy Received | 204 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 205 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 206 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 207 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_A Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 208 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_B Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 209 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_C Phase Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 210 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 211 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 212 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 213 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 214 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 215 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F5_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 216 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 217 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 218 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F5 | DAGGETT3_SUB1_SEL-351S-52F5_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F5_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 219 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_004_MWH3_REC | Energy Received | 220 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 221 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 222 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 223 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_A Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 224 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_B Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 225 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_C Phase Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 226 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 227 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 228 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 229 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 230 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 231 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F6_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 232 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 233 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 234 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F6 | DAGGETT3_SUB1_SEL-351S-52F6_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F6_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 235 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_004_MWH3_REC | Energy Received | 236 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 237 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 238 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 239 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 240 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 241 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 242 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 243 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 244 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 245 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 246 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 247 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F7_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 248 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 249 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 250 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F7 | DAGGETT3_SUB1_SEL-351S-52F7_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F7_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 251 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_004_MWH3_REC | Energy Received | 252 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 253 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 254 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 255 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 256 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 257 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 258 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 259 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 260 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 261 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 262 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 263 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F8_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 264 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 265 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 266 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F8 | DAGGETT3_SUB1_SEL-351S-52F8_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F8_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 267 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_004_MWH3_REC | Energy Received | 268 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 269 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 270 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 271 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 272 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 273 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 274 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 275 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 276 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 277 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 278 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 279 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F9_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 280 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 281 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 282 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F9 | DAGGETT3_SUB1_SEL-351S-52F9_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F9_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 283 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_004_MWH3_REC | Energy Received | 284 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 285 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 286 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 287 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 288 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 289 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 290 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 291 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 292 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 293 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 294 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 295 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F10_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 296 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 297 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 298 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F10 | DAGGETT3_SUB1_SEL-351S-52F10_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F10_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 299 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_004_MWH3_REC | Energy Received | 300 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 301 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 302 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 303 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 304 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 305 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 306 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 307 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 308 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 309 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 310 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 311 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F11_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 312 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 313 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 314 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F11 | DAGGETT3_SUB1_SEL-351S-52F11_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F11_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 315 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_004_MWH3_REC | Energy Received | 316 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 317 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 318 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 319 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 320 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 321 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 322 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 323 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 324 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 325 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 326 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 327 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F12_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 328 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 329 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 330 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F12 | DAGGETT3_SUB1_SEL-351S-52F12_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F12_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 331 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_004_MWH3_REC | Energy Received | 332 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 333 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 334 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 335 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 336 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 337 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 338 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 339 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 340 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 341 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 342 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 343 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F13_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 344 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 345 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 346 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F13 | DAGGETT3_SUB1_SEL-351S-52F13_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F13_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 347 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_004_MWH3_REC | Energy Received | 348 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 349 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 350 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 351 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 352 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 353 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 354 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 355 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 356 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 357 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 358 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 359 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F14_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 360 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 361 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 362 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F14 | DAGGETT3_SUB1_SEL-351S-52F14_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F14_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 363 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_004_MWH3_REC | Energy Received | 364 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 365 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 366 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 367 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 368 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 369 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 370 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 371 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 372 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 373 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 374 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 375 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F15_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 376 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 377 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 378 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F15 | DAGGETT3_SUB1_SEL-351S-52F15_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F15_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 379 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_004_MWH3_REC | Energy Received | 380 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_004_MWH3_DEL | Energy Delivered | 381 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_008_MVARH3_REC | Reactive Energy Received | 382 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_008_MVARH3_DEL | Reactive Energy Delivered | 383 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_001_MWHA_REC | Phase Energy Received | 384 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_002_MHWB_REC | Phase Energy Received | 385 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_003_WWHC_REC | Phase Energy Received | 386 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_001_MWHA_DEL | Phase Energy Delivered | 387 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_002_MWHB_DEL | Phase Energy Delivered | 388 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_003_WHHC_DEL | Phase Energy Delivered | 389 | MWh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_005_MVARHA_REC | Phase Reactive Energy Received | 390 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_006_MVARHB_REC | Phase Reactive Energy Received | 391 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Reactive Energy Received | Breaker Relay | SEL_351S_51F16_SEL.FPP_1_007_MVARHC_REC | Phase Reactive Energy Received | 392 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_A Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_005_MVARHA_DEL | Phase Reactive Energy Delivered | 393 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_B Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_006_MVARHB_DEL | Phase Reactive Energy Delivered | 394 | MVARh | Requested-Available | 9999999
SUB1 | SEL-351S-52F16 | DAGGETT3_SUB1_SEL-351S-52F16_C Phase Reactive Energy Delivered | Breaker Relay | SEL_351S_51F16_SEL.FPP_2_007_MVARHC_DEL | Phase Reactive Energy Delivered | 395 | MVARh | Requested-Available | 9999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 396 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 397 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 398 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 399 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 400 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 401 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 402 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 403 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 404 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 405 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 406 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 407 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00012_MWH3_REC | Energy Received | 408 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 409 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Energy Received | Meter | SEL_735_OCM1_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 410 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM1 LS | DAGGETT3_SUB1_SEL-735-OCM1 LS_Reactive Energy Delivered | Meter | SEL_735_OCM1_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 411 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 412 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 413 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 414 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 415 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 416 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 417 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 418 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 419 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 420 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 421 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 422 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 423 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00012_MWH3_REC | Energy Received | 424 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 425 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Energy Received | Meter | SEL_735_OCM2_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 426 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM2 LS | DAGGETT3_SUB1_SEL-735-OCM2 LS_Reactive Energy Delivered | Meter | SEL_735_OCM2_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 427 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 428 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 429 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 430 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 431 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 432 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 433 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 434 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 435 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 436 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 437 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 438 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 439 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00012_MWH3_REC | Energy Received | 440 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 441 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Energy Received | Meter | SEL_735_OCM3_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 442 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM3 LS | DAGGETT3_SUB1_SEL-735-OCM3 LS_Reactive Energy Delivered | Meter | SEL_735_OCM3_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 443 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 444 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 445 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 446 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 447 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 448 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 449 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 450 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 451 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 452 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 453 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 454 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 455 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00012_MWH3_REC | Energy Received | 456 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 457 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Energy Received | Meter | SEL_735_OCM4_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 458 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM4 LS | DAGGETT3_SUB1_SEL-735-OCM4 LS_Reactive Energy Delivered | Meter | SEL_735_OCM4_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 459 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 460 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 461 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 462 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 463 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 464 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 465 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 466 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 467 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 468 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 469 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 470 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 471 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00012_MWH3_REC | Energy Received | 472 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 473 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Energy Received | Meter | SEL_735_OCM5_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 474 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM5 LS | DAGGETT3_SUB1_SEL-735-OCM5 LS_Reactive Energy Delivered | Meter | SEL_735_OCM5_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 475 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 476 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 477 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 478 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 479 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 480 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 481 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 482 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 483 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 484 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 485 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 486 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 487 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00012_MWH3_REC | Energy Received | 488 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 489 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Energy Received | Meter | SEL_735_OCM6_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 490 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM6 LS | DAGGETT3_SUB1_SEL-735-OCM6 LS_Reactive Energy Delivered | Meter | SEL_735_OCM6_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 491 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 492 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 493 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 494 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 495 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 496 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 497 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 498 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 499 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 500 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 501 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 502 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 503 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00012_MWH3_REC | Energy Received | 504 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 505 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Energy Received | Meter | SEL_735_OCM7_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 506 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM7 LS | DAGGETT3_SUB1_SEL-735-OCM7 LS_Reactive Energy Delivered | Meter | SEL_735_OCM7_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 507 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 508 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 509 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 510 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 511 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 512 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 513 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 514 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 515 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 516 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 517 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 518 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 519 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00012_MWH3_REC | Energy Received | 520 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 521 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Energy Received | Meter | SEL_735_OCM8_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 522 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM8 LS | DAGGETT3_SUB1_SEL-735-OCM8 LS_Reactive Energy Delivered | Meter | SEL_735_OCM8_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 523 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00000_MWHA_REC | Energy Received | 524 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00001_MWHB_REC | Energy Delivered | 525 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00002_MWHC_REC | Reactive Energy Received | 526 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_Reactive Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00003_MWHA_DEL | Reactive Energy Delivered | 527 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Received | 528 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Received | 529 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00006_MVARHA_REC | Phase Energy Received | 530 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00007_MVARHB_REC | Phase Energy Delivered | 531 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00008_MVARHC_REC | Phase Energy Delivered | 532 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00009_MVARHA_DEL | Phase Energy Delivered | 533 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Received | 534 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Received | 535 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM9_DNP.COUNTER_00012_MWH3_REC | Phase Reactive Energy Received | 536 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00013_MWH3_DEL | Phase Reactive Energy Delivered | 537 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00014_MVARH3_REC | Phase Reactive Energy Delivered | 538 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM9 LS | DAGGETT3_SUB1_SEL-735-OCM9 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM9_DNP.COUNTER_00015_MVARH3_DEL | Phase Reactive Energy Delivered | 539 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00000_MWHA_REC | Energy Received | 540 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00001_MWHB_REC | Energy Delivered | 541 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00002_MWHC_REC | Reactive Energy Received | 542 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_Reactive Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00003_MWHA_DEL | Reactive Energy Delivered | 543 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Received | 544 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Received | 545 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00006_MVARHA_REC | Phase Energy Received | 546 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00007_MVARHB_REC | Phase Energy Delivered | 547 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00008_MVARHC_REC | Phase Energy Delivered | 548 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00009_MVARHA_DEL | Phase Energy Delivered | 549 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Received | 550 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Received | 551 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM10_DNP.COUNTER_00012_MWH3_REC | Phase Reactive Energy Received | 552 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00013_MWH3_DEL | Phase Reactive Energy Delivered | 553 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00014_MVARH3_REC | Phase Reactive Energy Delivered | 554 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM10 LS | DAGGETT3_SUB1_SEL-735-OCM10 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM10_DNP.COUNTER_00015_MVARH3_DEL | Phase Reactive Energy Delivered | 555 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00000_MWHA_REC | Energy Received | 556 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00001_MWHB_REC | Energy Delivered | 557 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00002_MWHC_REC | Reactive Energy Received | 558 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_Reactive Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00003_MWHA_DEL | Reactive Energy Delivered | 559 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Received | 560 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Received | 561 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00006_MVARHA_REC | Phase Energy Received | 562 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00007_MVARHB_REC | Phase Energy Delivered | 563 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00008_MVARHC_REC | Phase Energy Delivered | 564 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00009_MVARHA_DEL | Phase Energy Delivered | 565 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Received | 566 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Received | 567 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM11_DNP.COUNTER_00012_MWH3_REC | Phase Reactive Energy Received | 568 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00013_MWH3_DEL | Phase Reactive Energy Delivered | 569 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00014_MVARH3_REC | Phase Reactive Energy Delivered | 570 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM11 LS | DAGGETT3_SUB1_SEL-735-OCM11 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM11_DNP.COUNTER_00015_MVARH3_DEL | Phase Reactive Energy Delivered | 571 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00000_MWHA_REC | Energy Received | 572 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00001_MWHB_REC | Energy Delivered | 573 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00002_MWHC_REC | Reactive Energy Received | 574 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_Reactive Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00003_MWHA_DEL | Reactive Energy Delivered | 575 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Received | 576 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Received | 577 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00006_MVARHA_REC | Phase Energy Received | 578 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00007_MVARHB_REC | Phase Energy Delivered | 579 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00008_MVARHC_REC | Phase Energy Delivered | 580 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00009_MVARHA_DEL | Phase Energy Delivered | 581 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Received | 582 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Received | 583 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM12_DNP.COUNTER_00012_MWH3_REC | Phase Reactive Energy Received | 584 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00013_MWH3_DEL | Phase Reactive Energy Delivered | 585 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00014_MVARH3_REC | Phase Reactive Energy Delivered | 586 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM12 LS | DAGGETT3_SUB1_SEL-735-OCM12 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM12_DNP.COUNTER_00015_MVARH3_DEL | Phase Reactive Energy Delivered | 587 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00000_MWHA_REC | Energy Received | 588 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00001_MWHB_REC | Energy Delivered | 589 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00002_MWHC_REC | Reactive Energy Received | 590 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_Reactive Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00003_MWHA_DEL | Reactive Energy Delivered | 591 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Received | 592 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Received | 593 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00006_MVARHA_REC | Phase Energy Received | 594 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00007_MVARHB_REC | Phase Energy Delivered | 595 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00008_MVARHC_REC | Phase Energy Delivered | 596 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00009_MVARHA_DEL | Phase Energy Delivered | 597 | MWh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Reactive Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Received | 598 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Reactive Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Received | 599 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Reactive Energy Received | Meter | SEL_735_OCM13_DNP.COUNTER_00012_MWH3_REC | Phase Reactive Energy Received | 600 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_A Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00013_MWH3_DEL | Phase Reactive Energy Delivered | 601 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_B Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00014_MVARH3_REC | Phase Reactive Energy Delivered | 602 | MVARh | Requested-Available | 99999999999999
SUB1 | SEL-735-OCM13 LS | DAGGETT3_SUB1_SEL-735-OCM13 LS_C Phase Reactive Energy Delivered | Meter | SEL_735_OCM13_DNP.COUNTER_00015_MVARH3_DEL | Phase Reactive Energy Delivered | 603 | MVARh | Requested-Available | 99999999999999
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 604 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 605 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 606 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 607 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 608 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 609 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 610 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 611 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 612 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 613 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 614 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 615 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 616 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 617 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Reactive Energy Received | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 618 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1A LS | DAGGETT3_SUB1_ION-8650-CAISO-1A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_1A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 619 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 620 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 621 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 622 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 623 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 624 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 625 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 626 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 627 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 628 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 629 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 630 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 631 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 632 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 633 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Reactive Energy Received | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 634 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1B LS | DAGGETT3_SUB1_ION-8650-CAISO-1B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_1B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 635 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 636 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 637 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 638 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 639 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 640 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 641 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 642 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 643 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 644 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 645 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 646 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 647 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00012_MWH3_REC | Energy Received | 648 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 649 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Reactive Energy Received | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 650 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1C LS | DAGGETT3_SUB1_ION-8650-CAISO-1C LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_1C_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 651 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 652 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 653 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 654 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 655 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 656 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 657 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 658 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 659 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 660 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 661 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 662 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 663 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00012_MWH3_REC | Energy Received | 664 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 665 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Reactive Energy Received | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 666 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-1D LS | DAGGETT3_SUB1_ION-8650-CAISO-1D LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_1D_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 667 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 668 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 669 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 670 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 671 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 672 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 673 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 674 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 675 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 676 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 677 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 678 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 679 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 680 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 681 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Reactive Energy Received | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 682 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2A LS | DAGGETT3_SUB1_ION-8650-CAISO-2A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_2A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 683 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 684 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 685 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 686 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 687 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 688 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 689 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 690 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 691 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 692 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 693 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 694 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 695 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 696 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 697 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Reactive Energy Received | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 698 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-2B LS | DAGGETT3_SUB1_ION-8650-CAISO-2B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_2B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 699 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 700 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 701 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 702 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 703 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 704 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 705 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 706 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 707 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 708 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 709 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 710 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 711 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 712 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 713 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Reactive Energy Received | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 714 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3A LS | DAGGETT3_SUB1_ION-8650-CAISO-3A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_3A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 715 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 716 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 717 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 718 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 719 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 720 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 721 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 722 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 723 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 724 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 725 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 726 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 727 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 728 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 729 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Reactive Energy Received | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 730 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-3B LS | DAGGETT3_SUB1_ION-8650-CAISO-3B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_3B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 731 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 732 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 733 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 734 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 735 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 736 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 737 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 738 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 739 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 740 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 741 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 742 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 743 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 744 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 745 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Reactive Energy Received | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 746 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4A LS | DAGGETT3_SUB1_ION-8650-CAISO-4A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_4A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 747 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 748 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 749 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 750 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 751 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 752 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 753 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 754 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 755 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 756 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 757 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 758 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 759 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 760 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 761 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Reactive Energy Received | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 762 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-4B LS | DAGGETT3_SUB1_ION-8650-CAISO-4B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_4B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 763 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 764 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 765 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 766 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 767 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 768 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 769 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 770 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 771 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 772 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 773 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 774 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 775 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 776 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 777 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Reactive Energy Received | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 778 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5A LS | DAGGETT3_SUB1_ION-8650-CAISO-5A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_5A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 779 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 780 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 781 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 782 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 783 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 784 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 785 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 786 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 787 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 788 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 789 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 790 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 791 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 792 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 793 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Reactive Energy Received | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 794 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-5B LS | DAGGETT3_SUB1_ION-8650-CAISO-5B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_5B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 795 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 796 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 797 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 798 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 799 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 800 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 801 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 802 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 803 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 804 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 805 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 806 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 807 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 808 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 809 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Reactive Energy Received | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 810 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6A LS | DAGGETT3_SUB1_ION-8650-CAISO-6A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_6A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 811 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 812 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 813 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 814 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 815 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 816 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 817 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 818 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 819 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 820 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 821 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 822 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 823 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 824 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 825 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Reactive Energy Received | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 826 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-6B LS | DAGGETT3_SUB1_ION-8650-CAISO-6B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_6B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 827 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 828 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 829 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 830 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 831 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 832 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 833 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 834 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 835 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 836 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 837 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 838 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 839 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 840 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 841 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Reactive Energy Received | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 842 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7A LS | DAGGETT3_SUB1_ION-8650-CAISO-7A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_7A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 843 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 844 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 845 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 846 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 847 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 848 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 849 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 850 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 851 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 852 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 853 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 854 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 855 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 856 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 857 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Reactive Energy Received | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 858 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-7B LS | DAGGETT3_SUB1_ION-8650-CAISO-7B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_7B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 859 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 860 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 861 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 862 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 863 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 864 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 865 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 866 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 867 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 868 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 869 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 870 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 871 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 872 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 873 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Reactive Energy Received | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 874 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8A LS | DAGGETT3_SUB1_ION-8650-CAISO-8A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_8A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 875 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 876 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 877 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 878 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 879 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 880 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 881 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 882 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 883 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 884 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 885 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 886 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 887 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 888 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 889 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Reactive Energy Received | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 890 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-8B LS | DAGGETT3_SUB1_ION-8650-CAISO-8B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_8B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 891 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 892 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 893 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 894 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 895 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 896 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 897 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 898 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 899 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 900 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 901 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 902 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 903 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 904 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 905 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Reactive Energy Received | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 906 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9A LS | DAGGETT3_SUB1_ION-8650-CAISO-9A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_9A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 907 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 908 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 909 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 910 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 911 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 912 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 913 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 914 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 915 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 916 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 917 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 918 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 919 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 920 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 921 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Reactive Energy Received | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 922 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-9B LS | DAGGETT3_SUB1_ION-8650-CAISO-9B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_9B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 923 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 924 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 925 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 926 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 927 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 928 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 929 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 930 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 931 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 932 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 933 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 934 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 935 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 936 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 937 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Reactive Energy Received | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 938 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10A LS | DAGGETT3_SUB1_ION-8650-CAISO-10A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_10A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 939 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 940 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 941 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 942 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 943 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 944 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 945 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 946 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 947 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 948 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 949 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 950 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 951 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 952 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 953 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Reactive Energy Received | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 954 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-10B LS | DAGGETT3_SUB1_ION-8650-CAISO-10B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_10B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 955 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 956 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 957 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 958 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 959 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 960 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 961 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 962 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 963 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 964 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 965 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 966 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 967 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 968 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 969 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Reactive Energy Received | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 970 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11A LS | DAGGETT3_SUB1_ION-8650-CAISO-11A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_11A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 971 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 972 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 973 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 974 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 975 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 976 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 977 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 978 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 979 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 980 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 981 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 982 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 983 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 984 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 985 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Reactive Energy Received | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 986 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-11B LS | DAGGETT3_SUB1_ION-8650-CAISO-11B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_11B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 987 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 988 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 989 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 990 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 991 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 992 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 993 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 994 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 995 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 996 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 997 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 998 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 999 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 1000 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 1001 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Reactive Energy Received | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 1002 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12A LS | DAGGETT3_SUB1_ION-8650-CAISO-12A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_12A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 1003 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 1004 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 1005 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 1006 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 1007 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 1008 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 1009 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 1010 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 1011 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 1012 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 1013 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 1014 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 1015 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 1016 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 1017 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Reactive Energy Received | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 1018 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-12B LS | DAGGETT3_SUB1_ION-8650-CAISO-12B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_12B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 1019 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 1020 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 1021 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 1022 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 1023 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 1024 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 1025 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 1026 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 1027 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 1028 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 1029 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 1030 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 1031 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00012_MWH3_REC | Energy Received | 1032 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 1033 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Reactive Energy Received | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 1034 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13A LS | DAGGETT3_SUB1_ION-8650-CAISO-13A LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_13A_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 1035 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00000_MWHA_REC | Phase Energy Received | 1036 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00001_MWHB_REC | Phase Energy Received | 1037 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00002_MWHC_REC | Phase Energy Received | 1038 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00003_MWHA_DEL | Phase Energy Delivered | 1039 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00004_MWHB_DEL | Phase Energy Delivered | 1040 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00005_MWHC_DEL | Phase Energy Delivered | 1041 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Reactive Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00006_MVARHA_REC | Phase Reactive Energy Received | 1042 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Reactive Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00007_MVARHB_REC | Phase Reactive Energy Received | 1043 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Reactive Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00008_MVARHC_REC | Phase Reactive Energy Received | 1044 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_A Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00009_MVARHA_DEL | Phase Reactive Energy Delivered | 1045 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_B Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00010_MVARHB_DEL | Phase Reactive Energy Delivered | 1046 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_C Phase Reactive Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00011_MVARHC_DEL | Phase Reactive Energy Delivered | 1047 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00012_MWH3_REC | Energy Received | 1048 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00013_MWH3_DEL | Energy Delivered | 1049 | MWh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Reactive Energy Received | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00014_MVARH3_REC | Reactive Energy Received | 1050 | MVARh | Requested-Available | 16777215
SUB1 | ION-8650-CAISO-13B LS | DAGGETT3_SUB1_ION-8650-CAISO-13B LS_Reactive Energy Delivered | Meter | ION_8650_CAISO_13B_DNP.COUNTER_00015_MVARH3_DEL | Reactive Energy Delivered | 1051 | MVARh | Requested-Available | 16777215
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19971 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 0 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 1 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 2 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site Real Power Command | PPC | PPC.gmsBess.ppa1_pSp_MW | BESS Site Real Power Command | 3 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site Reactive Power Cmd | PPC | PPC.gmsBess.ppa1_qSp_MW | BESS Site Reactive Power Command | 4 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site RTU Heartbeat | PPC | PPC.gmsBess.ppa1_rtuHeartbeat | BESS Site Rtu Heartbeat | 5 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS Site Operation Code | PPC | PPC.gmsBess.ppa1_opCode | BESS Site Operation Code | 6 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19975 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 7 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 8 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 9 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site Real Power Command | PPC | PPC.gmsBess.ppa2_pSp_MW | BESS Site Real Power Command | 10 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site Reactive Power Cmd | PPC | PPC.gmsBess.ppa2_qSp_MW | BESS Site Reactive Power Command | 11 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site RTU Heartbeat | PPC | PPC.gmsBess.ppa2_rtuHeartbeat | BESS Site Rtu Heartbeat | 12 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS Site Operation Code | PPC | PPC.gmsBess.ppa2_opCode | BESS Site Operation Code | 13 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19979 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 14 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 15 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 16 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site Real Power Command | PPC | PPC.gmsBess.ppa4_pSp_MW | BESS Site Real Power Command | 17 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site Reactive Power Cmd | PPC | PPC.gmsBess.ppa4_qSp_MW | BESS Site Reactive Power Command | 18 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site RTU Heartbeat | PPC | PPC.gmsBess.ppa4_rtuHeartbeat | BESS Site Rtu Heartbeat | 19 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS Site Operation Code | PPC | PPC.gmsBess.ppa4_opCode | BESS Site Operation Code | 20 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19973 MW Setpoint | PPC | PPC.gms.ppa1_pSp_MW | MW Setpoint | 21 | MW | Requested-Available | 0 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Up Rate Setpoint | PPC | PPC.gms.pUpSp_MWpMin | GMS Ramp Up Rate Setpoint | 22 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Down Rate Setpoint | PPC | PPC.gms.pDownSp_MWpMin | GMS Ramp Down Rate Setpoint | 23 | MW/min | Requested-Available | 0 | 30 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site Real Power Command | PPC | PPC.gmsBess.ppa5_pSp_MW | BESS Site Real Power Command | 24 | KW | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site Reactive Power Cmd | PPC | PPC.gmsBess.ppa5_qSp_MW | BESS Site Reactive Power Command | 25 | KVAR | Not Requested-Available | -300000 | 300000 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site RTU Heartbeat | PPC | PPC.gmsBess.ppa5_rtuHeartbeat | BESS Site Rtu Heartbeat | 26 | N/A | Not Requested-Available | 0 | 65535 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS Site Operation Code | PPC | PPC.gmsBess.ppa5_opCode | BESS Site Operation Code | 27 | N/A | Not Requested-Available | 0 | 16 | 1
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS POI PF Setpoint | PPC | PPC.gms.pfSp | GMS POI PF Setpoint | 28 | MVAR*100 | Requested-Available | -300 | 300 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS POI Voltage Setpoint | PPC | PPC.gms.vSp_kV | GMS POI Voltage Setpoint | 29 | PF*100 | Requested-Available | -1 | 1 | 100
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS POI VAR Setpoint | PPC | PPC.gms.qSp_Mvar | GMS POI VAR Setpoint | 30 | KV*100 | Requested-Available | 210 | 250 | 100
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F9 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 0 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F10 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 1 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F11 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 2 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 3 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F2 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 4 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52T1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 5 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52T2 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 6 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52L1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 7 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 89T1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 8 | Latch Off = Trip, Latch On = Close | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 89T2 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 9 | Latch Off = Trip, Latch On = Close | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 079 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 10 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 080 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 11 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 076 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 12 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 073 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 13 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 070 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 14 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 081 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 15 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 078 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 16 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 075 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 17 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 072 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 18 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 071 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 19 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 068 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 20 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 069 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 21 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 093 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 22 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 094 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 23 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 095 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 24 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 092 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 25 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 091 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 26 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 087 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 27 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 088 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 28 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 090 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 29 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 089 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 30 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 086 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 31 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 082 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 32 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 083 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 33 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 084 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 34 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 085 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 35 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 077 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 36 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 074 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 37 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 067 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 38 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 054 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 39 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 053 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 40 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 052 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 41 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 059 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 42 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 058 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 43 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 006 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 44 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 012 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 45 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 005 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 46 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 004 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 47 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Inverter 003 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 48 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Turbine 001 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS 89L11 MOD Control | PPC |  | Breaker Controls |  | Latch Off = Open, Latch On = Close | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19971 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 49 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 50 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 51 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 52 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 53 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19971 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 54 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Lock Control | PPC | PPC.gmsBess.ess01_lock | ESS Unit A Lock Control | 55 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Participate Control | PPC | PPC.gmsBess.ess01_participate | ESS Unit A Site Participation Control | 56 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS01 Fault Reset | PPC | PPC.gmsBess.ess01_faultReset | ESS Unit A Fault Reset | 57 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP01 Fault Reset | PPC | PPC.gmsBess.ess01_bopFaultReset | ESS BOP Fault Reset | 58 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Lock Control | PPC | PPC.gmsBess.ess02_lock | ESS Unit CD Lock Control | 59 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Participate Control | PPC | PPC.gmsBess.ess02_participate | ESS Unit CD Site Participation Control | 60 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS02 Fault Reset | PPC | PPC.gmsBess.ess02_faultReset | ESS Unit CD Fault Reset | 61 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP02 Fault Reset | PPC | PPC.gmsBess.ess02_bopFaultReset | ESS BOP Fault Reset | 62 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Lock Control | PPC | PPC.gmsBess.ess03_lock | ESS Unit CD Lock Control | 63 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Participate Control | PPC | PPC.gmsBess.ess03_participate | ESS Unit CD Site Participation Control | 64 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS03 Fault Reset | PPC | PPC.gmsBess.ess03_faultReset | ESS Unit CD Fault Reset | 65 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP03 Fault Reset | PPC | PPC.gmsBess.ess03_bopFaultReset | ESS BOP Fault Reset | 66 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Lock Control | PPC | PPC.gmsBess.ess04_lock | ESS Unit E Lock Control | 67 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Participate Control | PPC | PPC.gmsBess.ess04_participate | ESS Unit E Site Participation Control | 68 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS04 Fault Reset | PPC | PPC.gmsBess.ess04_faultReset | ESS Unit E Fault Reset | 69 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP04 Fault Reset | PPC | PPC.gmsBess.ess04_bopFaultReset | ESS BOP Fault Reset | 70 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Lock Control | PPC | PPC.gmsBess.ess05_lock | ESS Unit B Lock Control | 71 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Participate Control | PPC | PPC.gmsBess.ess05_participate | ESS Unit B Site Participation Control | 72 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS05 Fault Reset | PPC | PPC.gmsBess.ess05_faultReset | ESS Unit B Fault Reset | 73 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP05 Fault Reset | PPC | PPC.gmsBess.ess05_bopFaultReset | ESS BOP Fault Reset | 74 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Lock Control | PPC | PPC.gmsBess.ess06_lock | ESS Unit 6 Lock Control | 75 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Participate Control | PPC | PPC.gmsBess.ess06_participate | ESS Unit 6 Site Participation Control | 76 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS06 Fault Reset | PPC | PPC.gmsBess.ess06_faultReset | ESS Unit 6 Fault Reset | 77 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP06 Fault Reset | PPC | PPC.gmsBess.ess06_bopFaultReset | ESS BOP Fault Reset | 78 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Lock Control | PPC | PPC.gmsBess.ess07_lock | ESS Unit 7 Lock Control | 79 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Participate Control | PPC | PPC.gmsBess.ess07_participate | ESS Unit 7 Site Participation Control | 80 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS07 Fault Reset | PPC | PPC.gmsBess.ess07_faultReset | ESS Unit 7 Fault Reset | 81 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP07 Fault Reset | PPC | PPC.gmsBess.ess07_bopFaultReset | ESS BOP Fault Reset | 82 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Lock Control | PPC | PPC.gmsBess.ess08_lock | ESS Unit 8 Lock Control | 83 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Participate Control | PPC | PPC.gmsBess.ess08_participate | ESS Unit 8 Site Participation Control | 84 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS08 Fault Reset | PPC | PPC.gmsBess.ess08_faultReset | ESS Unit 8 Fault Reset | 85 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP08 Fault Reset | PPC | PPC.gmsBess.ess08_bopFaultReset | ESS BOP Fault Reset | 86 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Lock Control | PPC | PPC.gmsBess.ess09_lock | ESS Unit 9 Lock Control | 87 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Participate Control | PPC | PPC.gmsBess.ess09_participate | ESS Unit 9 Site Participation Control | 88 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS09 Fault Reset | PPC | PPC.gmsBess.ess09_faultReset | ESS Unit 9 Fault Reset | 89 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP09 Fault Reset | PPC | PPC.gmsBess.ess09_bopFaultReset | ESS BOP Fault Reset | 90 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Lock Control | PPC | PPC.gmsBess.ess10_lock | ESS Unit A0 Lock Control | 91 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Participate Control | PPC | PPC.gmsBess.ess10_participate | ESS Unit A0 Site Participation Control | 92 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS10 Fault Reset | PPC | PPC.gmsBess.ess10_faultReset | ESS Unit A0 Fault Reset | 93 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP10 Fault Reset | PPC | PPC.gmsBess.ess10_bopFaultReset | ESS BOP Fault Reset | 94 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Lock Control | PPC | PPC.gmsBess.ess11_lock | ESS Unit A1 Lock Control | 95 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Participate Control | PPC | PPC.gmsBess.ess11_participate | ESS Unit A1 Site Participation Control | 96 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS11 Fault Reset | PPC | PPC.gmsBess.ess11_faultReset | ESS Unit A1 Fault Reset | 97 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP11 Fault Reset | PPC | PPC.gmsBess.ess11_bopFaultReset | ESS BOP Fault Reset | 98 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Lock Control | PPC | PPC.gmsBess.ess12_lock | ESS Unit A2 Lock Control | 99 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Participate Control | PPC | PPC.gmsBess.ess12_participate | ESS Unit A2 Site Participation Control | 100 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS12 Fault Reset | PPC | PPC.gmsBess.ess12_faultReset | ESS Unit A2 Fault Reset | 101 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP12 Fault Reset | PPC | PPC.gmsBess.ess12_bopFaultReset | ESS BOP Fault Reset | 102 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Lock Control | PPC | PPC.gmsBess.ess13_lock | ESS Unit A3 Lock Control | 103 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Participate Control | PPC | PPC.gmsBess.ess13_participate | ESS Unit A3 Site Participation Control | 104 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS13 Fault Reset | PPC | PPC.gmsBess.ess13_faultReset | ESS Unit A3 Fault Reset | 105 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP13 Fault Reset | PPC | PPC.gmsBess.ess13_bopFaultReset | ESS BOP Fault Reset | 106 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Lock Control | PPC | PPC.gmsBess.ess14_lock | ESS Unit A4 Lock Control | 107 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Participate Control | PPC | PPC.gmsBess.ess14_participate | ESS Unit A4 Site Participation Control | 108 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS14 Fault Reset | PPC | PPC.gmsBess.ess14_faultReset | ESS Unit A4 Fault Reset | 109 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP14 Fault Reset | PPC | PPC.gmsBess.ess14_bopFaultReset | ESS BOP Fault Reset | 110 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Lock Control | PPC | PPC.gmsBess.ess15_lock | ESS Unit A5 Lock Control | 111 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Participate Control | PPC | PPC.gmsBess.ess15_participate | ESS Unit A5 Site Participation Control | 112 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS15 Fault Reset | PPC | PPC.gmsBess.ess15_faultReset | ESS Unit A5 Fault Reset | 113 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP15 Fault Reset | PPC | PPC.gmsBess.ess15_bopFaultReset | ESS BOP Fault Reset | 114 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Lock Control | PPC | PPC.gmsBess.ess16_lock | ESS Unit A6 Lock Control | 115 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Participate Control | PPC | PPC.gmsBess.ess16_participate | ESS Unit A6 Site Participation Control | 116 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS16 Fault Reset | PPC | PPC.gmsBess.ess16_faultReset | ESS Unit A6 Fault Reset | 117 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP16 Fault Reset | PPC | PPC.gmsBess.ess16_bopFaultReset | ESS BOP Fault Reset | 118 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Lock Control | PPC | PPC.gmsBess.ess17_lock | ESS Unit A7 Lock Control | 119 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Participate Control | PPC | PPC.gmsBess.ess17_participate | ESS Unit A7 Site Participation Control | 120 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS17 Fault Reset | PPC | PPC.gmsBess.ess17_faultReset | ESS Unit A7 Fault Reset | 121 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP17 Fault Reset | PPC | PPC.gmsBess.ess17_bopFaultReset | ESS BOP Fault Reset | 122 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Lock Control | PPC | PPC.gmsBess.ess18_lock | ESS Unit A8 Lock Control | 123 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Participate Control | PPC | PPC.gmsBess.ess18_participate | ESS Unit A8 Site Participation Control | 124 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS18 Fault Reset | PPC | PPC.gmsBess.ess18_faultReset | ESS Unit A8 Fault Reset | 125 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP18 Fault Reset | PPC | PPC.gmsBess.ess18_bopFaultReset | ESS BOP Fault Reset | 126 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Lock Control | PPC | PPC.gmsBess.ess19_lock | ESS Unit A9 Lock Control | 127 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Participate Control | PPC | PPC.gmsBess.ess19_participate | ESS Unit A9 Site Participation Control | 128 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS19 Fault Reset | PPC | PPC.gmsBess.ess19_faultReset | ESS Unit A9 Fault Reset | 129 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP19 Fault Reset | PPC | PPC.gmsBess.ess19_bopFaultReset | ESS BOP Fault Reset | 130 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Lock Control | PPC | PPC.gmsBess.ess20_lock | ESS Unit CD0 Lock Control | 131 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Participate Control | PPC | PPC.gmsBess.ess20_participate | ESS Unit CD0 Site Participation Control | 132 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS ESS20 Fault Reset | PPC | PPC.gmsBess.ess20_faultReset | ESS Unit CD0 Fault Reset | 133 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19972 BESS BOP20 Fault Reset | PPC | PPC.gmsBess.ess20_bopFaultReset | ESS BOP Fault Reset | 134 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F3 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 135 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F4 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 136 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 061 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 137 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 062 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 138 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 057 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 139 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 056 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 140 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 055 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 141 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 013 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 142 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 011 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 143 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 010 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 144 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Turbine 002 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 066 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 145 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 065 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 146 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 064 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 147 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 063 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 148 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 060 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 149 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 047 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 150 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 046 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 151 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Inverter 044 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 152 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Turbine 003 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19975 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 153 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 154 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 155 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 156 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 157 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19975 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 158 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Lock Control | PPC | PPC.gmsBess.ess01_lock | ESS Unit A Lock Control | 159 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Participate Control | PPC | PPC.gmsBess.ess01_participate | ESS Unit A Site Participation Control | 160 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS01 Fault Reset | PPC | PPC.gmsBess.ess01_faultReset | ESS Unit A Fault Reset | 161 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP01 Fault Reset | PPC | PPC.gmsBess.ess01_bopFaultReset | ESS BOP Fault Reset | 162 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Lock Control | PPC | PPC.gmsBess.ess02_lock | ESS Unit CD Lock Control | 163 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Participate Control | PPC | PPC.gmsBess.ess02_participate | ESS Unit CD Site Participation Control | 164 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS02 Fault Reset | PPC | PPC.gmsBess.ess02_faultReset | ESS Unit CD Fault Reset | 165 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP02 Fault Reset | PPC | PPC.gmsBess.ess02_bopFaultReset | ESS BOP Fault Reset | 166 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F6 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 167 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F7 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 168 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Lock Control | PPC | PPC.gmsBess.ess03_lock | ESS Unit CD Lock Control | 169 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Participate Control | PPC | PPC.gmsBess.ess03_participate | ESS Unit CD Site Participation Control | 170 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS03 Fault Reset | PPC | PPC.gmsBess.ess03_faultReset | ESS Unit CD Fault Reset | 171 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP03 Fault Reset | PPC | PPC.gmsBess.ess03_bopFaultReset | ESS BOP Fault Reset | 172 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Lock Control | PPC | PPC.gmsBess.ess04_lock | ESS Unit CD Lock Control | 173 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Participate Control | PPC | PPC.gmsBess.ess04_participate | ESS Unit CD Site Participation Control | 174 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS ESS04 Fault Reset | PPC | PPC.gmsBess.ess04_faultReset | ESS Unit CD Fault Reset | 175 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19978 BESS BOP04 Fault Reset | PPC | PPC.gmsBess.ess04_bopFaultReset | ESS BOP Fault Reset | 176 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F5 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 177 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F8 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 178 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Inverter 051 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 179 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Inverter 050 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 180 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Inverter 019 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 181 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Inverter 020 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 182 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Inverter 021 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 183 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Turbine 004 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19979 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 184 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 185 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 186 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 187 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 188 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19979 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 189 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Lock Control | PPC | PPC.gmsBess.ess01_lock | ESS Unit E Lock Control | 190 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Participate Control | PPC | PPC.gmsBess.ess01_participate | ESS Unit E Site Participation Control | 191 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS01 Fault Reset | PPC | PPC.gmsBess.ess01_faultReset | ESS Unit E Fault Reset | 192 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP01 Fault Reset | PPC | PPC.gmsBess.ess01_bopFaultReset | ESS BOP Fault Reset | 193 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Lock Control | PPC | PPC.gmsBess.ess02_lock | ESS Unit CD Lock Control | 194 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Participate Control | PPC | PPC.gmsBess.ess02_participate | ESS Unit CD Site Participation Control | 195 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS02 Fault Reset | PPC | PPC.gmsBess.ess02_faultReset | ESS Unit CD Fault Reset | 196 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP02 Fault Reset | PPC | PPC.gmsBess.ess02_bopFaultReset | ESS BOP Fault Reset | 197 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Lock Control | PPC | PPC.gmsBess.ess03_lock | ESS Unit CD Lock Control | 198 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Participate Control | PPC | PPC.gmsBess.ess03_participate | ESS Unit CD Site Participation Control | 199 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS03 Fault Reset | PPC | PPC.gmsBess.ess03_faultReset | ESS Unit CD Fault Reset | 200 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP03 Fault Reset | PPC | PPC.gmsBess.ess03_bopFaultReset | ESS BOP Fault Reset | 201 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Lock Control | PPC | PPC.gmsBess.ess04_lock | ESS Unit E Lock Control | 202 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Participate Control | PPC | PPC.gmsBess.ess04_participate | ESS Unit E Site Participation Control | 203 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS04 Fault Reset | PPC | PPC.gmsBess.ess04_faultReset | ESS Unit E Fault Reset | 204 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP04 Fault Reset | PPC | PPC.gmsBess.ess04_bopFaultReset | ESS BOP Fault Reset | 205 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Lock Control | PPC | PPC.gmsBess.ess05_lock | ESS Unit B Lock Control | 206 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Participate Control | PPC | PPC.gmsBess.ess05_participate | ESS Unit B Site Participation Control | 207 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS ESS05 Fault Reset | PPC | PPC.gmsBess.ess05_faultReset | ESS Unit B Fault Reset | 208 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19980 BESS BOP05 Fault Reset | PPC | PPC.gmsBess.ess05_bopFaultReset | ESS BOP Fault Reset | 209 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F12 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 210 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F13 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 211 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F14 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 212 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F15 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 213 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52F16 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 214 | Latch Off = Trip, Latch On = Close | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 018 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 215 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 017 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 216 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 007 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 217 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 001 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 218 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 002 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 219 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 008 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 220 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 009 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 221 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 027 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 222 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 026 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 223 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 025 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 224 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 024 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 225 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 016 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 226 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 015 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 227 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 014 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 228 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 045 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 229 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 023 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 230 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 022 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 231 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 028 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 232 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 033 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 233 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 034 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 234 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 036 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 235 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 049 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 236 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 048 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 237 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 032 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 238 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 031 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 239 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 030 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 240 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 029 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 241 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 035 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 242 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 037 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 243 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 038 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 244 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 039 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 245 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 040 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 246 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 041 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 247 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 042 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 248 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Inverter 043 Control | PPC | PPC.gms.inv_reset | Inverter Controls | 249 | Latch On = Reset | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Turbine 005 Control | PPC |  | Turbine Controls |  | Latch On = Reset | Requested-Not Applicable
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS Unit 21GEN19973 Curtailment Disable/Enable | PPC | PPC.gms.ppa1CurtailmentEn | Curtailment Disable/Enable | 250 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Voltage Mode Disable/Enable | PPC | PPC.gms.vModeEN | GMS Voltage Mode Disable/Enable | 251 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS PF Mode Disable/Enable | PPC | PPC.gms.pfModeEn | GMS PF Mode Disable/Enable | 252 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS MVAR Mode Disable/Enable | PPC | PPC.gms.qModeEn | GMS MVAR Mode Disable/Enable | 253 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Up Rate Setpoint Disable/Enable | PPC | PPC.gms.pUpSpEn | GMS Ramp Up Rate Setpoint Disable/Enable | 254 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19973 GMS Ramp Down Rate Setpoint Disable/Enable | PPC | PPC.gms.pDownSpEn | GMS Ramp Down Rate Setpoint Disable/Enable | 255 | Latch Off = Disable, Latch On = Enable | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Lock Control | PPC | PPC.gmsBess.ess01_lock | ESS Unit B Lock Control | 256 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Participate Control | PPC | PPC.gmsBess.ess01_participate | ESS Unit B Site Participation Control | 257 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS01 Fault Reset | PPC | PPC.gmsBess.ess01_faultReset | ESS Unit B Fault Reset | 258 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP01 Fault Reset | PPC | PPC.gmsBess.ess01_bopFaultReset | ESS BOP Fault Reset | 259 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Lock Control | PPC | PPC.gmsBess.ess02_lock | ESS Unit CD Lock Control | 260 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Participate Control | PPC | PPC.gmsBess.ess02_participate | ESS Unit CD Site Participation Control | 261 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS02 Fault Reset | PPC | PPC.gmsBess.ess02_faultReset | ESS Unit CD Fault Reset | 262 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP02 Fault Reset | PPC | PPC.gmsBess.ess02_bopFaultReset | ESS BOP Fault Reset | 263 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Lock Control | PPC | PPC.gmsBess.ess03_lock | ESS Unit CD Lock Control | 264 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Participate Control | PPC | PPC.gmsBess.ess03_participate | ESS Unit CD Site Participation Control | 265 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS03 Fault Reset | PPC | PPC.gmsBess.ess03_faultReset | ESS Unit CD Fault Reset | 266 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP03 Fault Reset | PPC | PPC.gmsBess.ess03_bopFaultReset | ESS BOP Fault Reset | 267 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Lock Control | PPC | PPC.gmsBess.ess04_lock | ESS Unit E Lock Control | 268 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Participate Control | PPC | PPC.gmsBess.ess04_participate | ESS Unit E Site Participation Control | 269 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS04 Fault Reset | PPC | PPC.gmsBess.ess04_faultReset | ESS Unit E Fault Reset | 270 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP04 Fault Reset | PPC | PPC.gmsBess.ess04_bopFaultReset | ESS BOP Fault Reset | 271 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Lock Control | PPC | PPC.gmsBess.ess05_lock | ESS Unit B Lock Control | 272 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Participate Control | PPC | PPC.gmsBess.ess05_participate | ESS Unit B Site Participation Control | 273 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS05 Fault Reset | PPC | PPC.gmsBess.ess05_faultReset | ESS Unit B Fault Reset | 274 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP05 Fault Reset | PPC | PPC.gmsBess.ess05_bopFaultReset | ESS BOP Fault Reset | 275 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Lock Control | PPC | PPC.gmsBess.ess06_lock | ESS Unit 6 Lock Control | 276 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Participate Control | PPC | PPC.gmsBess.ess06_participate | ESS Unit 6 Site Participation Control | 277 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS06 Fault Reset | PPC | PPC.gmsBess.ess06_faultReset | ESS Unit 6 Fault Reset | 278 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP06 Fault Reset | PPC | PPC.gmsBess.ess06_bopFaultReset | ESS BOP Fault Reset | 279 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Lock Control | PPC | PPC.gmsBess.ess07_lock | ESS Unit 7 Lock Control | 280 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Participate Control | PPC | PPC.gmsBess.ess07_participate | ESS Unit 7 Site Participation Control | 281 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS07 Fault Reset | PPC | PPC.gmsBess.ess07_faultReset | ESS Unit 7 Fault Reset | 282 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP07 Fault Reset | PPC | PPC.gmsBess.ess07_bopFaultReset | ESS BOP Fault Reset | 283 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Lock Control | PPC | PPC.gmsBess.ess08_lock | ESS Unit 8 Lock Control | 284 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Participate Control | PPC | PPC.gmsBess.ess08_participate | ESS Unit 8 Site Participation Control | 285 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS08 Fault Reset | PPC | PPC.gmsBess.ess08_faultReset | ESS Unit 8 Fault Reset | 286 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP08 Fault Reset | PPC | PPC.gmsBess.ess08_bopFaultReset | ESS BOP Fault Reset | 287 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Lock Control | PPC | PPC.gmsBess.ess09_lock | ESS Unit 9 Lock Control | 288 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Participate Control | PPC | PPC.gmsBess.ess09_participate | ESS Unit 9 Site Participation Control | 289 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS09 Fault Reset | PPC | PPC.gmsBess.ess09_faultReset | ESS Unit 9 Fault Reset | 290 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP09 Fault Reset | PPC | PPC.gmsBess.ess09_bopFaultReset | ESS BOP Fault Reset | 291 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Lock Control | PPC | PPC.gmsBess.ess10_lock | ESS Unit B0 Lock Control | 292 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Participate Control | PPC | PPC.gmsBess.ess10_participate | ESS Unit B0 Site Participation Control | 293 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS10 Fault Reset | PPC | PPC.gmsBess.ess10_faultReset | ESS Unit B0 Fault Reset | 294 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP10 Fault Reset | PPC | PPC.gmsBess.ess10_bopFaultReset | ESS BOP Fault Reset | 295 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Lock Control | PPC | PPC.gmsBess.ess11_lock | ESS Unit B1 Lock Control | 296 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Participate Control | PPC | PPC.gmsBess.ess11_participate | ESS Unit B1 Site Participation Control | 297 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS11 Fault Reset | PPC | PPC.gmsBess.ess11_faultReset | ESS Unit B1 Fault Reset | 298 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP11 Fault Reset | PPC | PPC.gmsBess.ess11_bopFaultReset | ESS BOP Fault Reset | 299 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Lock Control | PPC | PPC.gmsBess.ess12_lock | ESS Unit B2 Lock Control | 300 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Participate Control | PPC | PPC.gmsBess.ess12_participate | ESS Unit B2 Site Participation Control | 301 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS12 Fault Reset | PPC | PPC.gmsBess.ess12_faultReset | ESS Unit B2 Fault Reset | 302 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP12 Fault Reset | PPC | PPC.gmsBess.ess12_bopFaultReset | ESS BOP Fault Reset | 303 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Lock Control | PPC | PPC.gmsBess.ess13_lock | ESS Unit B3 Lock Control | 304 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Participate Control | PPC | PPC.gmsBess.ess13_participate | ESS Unit B3 Site Participation Control | 305 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS13 Fault Reset | PPC | PPC.gmsBess.ess13_faultReset | ESS Unit B3 Fault Reset | 306 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP13 Fault Reset | PPC | PPC.gmsBess.ess13_bopFaultReset | ESS BOP Fault Reset | 307 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Lock Control | PPC | PPC.gmsBess.ess14_lock | ESS Unit B4 Lock Control | 308 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Participate Control | PPC | PPC.gmsBess.ess14_participate | ESS Unit B4 Site Participation Control | 309 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS14 Fault Reset | PPC | PPC.gmsBess.ess14_faultReset | ESS Unit B4 Fault Reset | 310 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP14 Fault Reset | PPC | PPC.gmsBess.ess14_bopFaultReset | ESS BOP Fault Reset | 311 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Lock Control | PPC | PPC.gmsBess.ess15_lock | ESS Unit B5 Lock Control | 312 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Participate Control | PPC | PPC.gmsBess.ess15_participate | ESS Unit B5 Site Participation Control | 313 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS15 Fault Reset | PPC | PPC.gmsBess.ess15_faultReset | ESS Unit B5 Fault Reset | 314 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP15 Fault Reset | PPC | PPC.gmsBess.ess15_bopFaultReset | ESS BOP Fault Reset | 315 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Lock Control | PPC | PPC.gmsBess.ess16_lock | ESS Unit B6 Lock Control | 316 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Participate Control | PPC | PPC.gmsBess.ess16_participate | ESS Unit B6 Site Participation Control | 317 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS16 Fault Reset | PPC | PPC.gmsBess.ess16_faultReset | ESS Unit B6 Fault Reset | 318 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP16 Fault Reset | PPC | PPC.gmsBess.ess16_bopFaultReset | ESS BOP Fault Reset | 319 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Lock Control | PPC | PPC.gmsBess.ess17_lock | ESS Unit B7 Lock Control | 320 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Participate Control | PPC | PPC.gmsBess.ess17_participate | ESS Unit B7 Site Participation Control | 321 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS17 Fault Reset | PPC | PPC.gmsBess.ess17_faultReset | ESS Unit B7 Fault Reset | 322 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP17 Fault Reset | PPC | PPC.gmsBess.ess17_bopFaultReset | ESS BOP Fault Reset | 323 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Lock Control | PPC | PPC.gmsBess.ess18_lock | ESS Unit B8 Lock Control | 324 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Participate Control | PPC | PPC.gmsBess.ess18_participate | ESS Unit B8 Site Participation Control | 325 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS18 Fault Reset | PPC | PPC.gmsBess.ess18_faultReset | ESS Unit B8 Fault Reset | 326 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP18 Fault Reset | PPC | PPC.gmsBess.ess18_bopFaultReset | ESS BOP Fault Reset | 327 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Lock Control | PPC | PPC.gmsBess.ess19_lock | ESS Unit B8 Lock Control | 328 | Off = Unlock, On = Lock | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Participate Control | PPC | PPC.gmsBess.ess19_participate | ESS Unit B8 Site Participation Control | 329 | Off = Not Participate, On = Participate | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS ESS19 Fault Reset | PPC | PPC.gmsBess.ess19_faultReset | ESS Unit B8 Fault Reset | 330 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_21GEN19974 BESS BOP19 Fault Reset | PPC | PPC.gmsBess.ess19_bopFaultReset | ESS BOP Fault Reset | 331 | Off = False, On = Reset | Not Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52C1 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 332 | LatchOff/LatchOn | Requested-Available
SUB1 | PPC | Daggett 3_SUB1_PPC_GMS 52C2 Breaker Control | PPC | PPC.gms.cb52 | Breaker Controls | 333 | LatchOff/LatchOn | Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L11 MOD CONTROL | Line Relay | SEL_411L_87L1S_SEL.FO_RB_RB3:RB4.operPulse | SCADA OPEN/CLOSE | 334 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L1S | DAGGETT3_SUB1_SEL-411L-87L1S_89L12 MOD CONTROL | Line Relay | SEL_411L_87L1S_SEL.FO_RB_RB5:RB6.operPulse | SCADA OPEN/CLOSE | 335 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-411L-87L2S | DAGGETT3_SUB1_SEL-411L-87L2S_89L21 MOD CONTROL | Line Relay | SEL_411L_87L2S_SEL.FO_RB_RB1:RB2.operPulse | SCADA OPEN/CLOSE | 336 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC11 SCADA TRIP-CLOSE | Reactive Power Relay | SEL_487V_87C1_SEL.FO_RB_RB3:RB4.operPulse | SCADA TRIP/CLOSE | 337 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87C1 | DAGGETT3_SUB1_SEL-487V-87C1_CSC12 SCADA TRIP-CLOSE | Reactive Power Relay | SEL_487V_87C1_SEL.FO_RB_RB5:RB6.operPulse | SCADA TRIP/CLOSE | 338 | LatchOff/LatchOn | Not Requested-Available
SUB1 | SEL-487V-87C2 | DAGGETT3_SUB1_SEL-487V-87C2_CSC21 SCADA TRIP-CLOSE | Reactive Power Relay | SEL_487V_87C2_SEL.FO_RB_RB3:RB4.operPulse | SCADA TRIP/CLOSE | 339 | LatchOff/LatchOn | Not Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_TAP POSITION RAISE | Medium-High Voltage Transformer | M2001C_T2_90_DNP.BO_00000.operLatchOn | TAP RAISE | 340 | LatchOff/LatchOn | Not Requested-Available
SUB1 | BECKWITH M-2001C-90T2 | DAGGETT3_SUB1_BECKWITH M-2001C-90T2_TAP POSITION LOWER | Medium-High Voltage Transformer | M2001C_T2_90_DNP.BO_00001.operLatchOff | TAP LOWER | 341 | LatchOff/LatchOn | Not Requested-Available

## DNP3.0 Server#2 (INV1-47)
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | 10.75.32.2 |  | DNP Server | 10.75.32.2
DNP Server Port# | 20002 |  | DNP Server Port# | 20012 (PROD); 20013 (QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 2 |  | RTAC DNP Server address | 1
| Data Type | DNP Event Class | Event Obj/Var | Static Obj/Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30/5
Digitals | Status with Flags | 1 | 2/2 | 1/2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20/1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband of 0.01 for all points except 0.001 for Frequency and Power Factor
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | INV001 | Daggett 3_SUB1_INV001_A Phase Current | Inverter | Inverter001_MODBUS.HR1004_i1_A | A Phase Current | 0 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_B Phase Current | Inverter | Inverter001_MODBUS.HR1005_i2_A | B Phase Current | 1 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_C Phase Current | Inverter | Inverter001_MODBUS.HR1006_i3_A | C Phase Current | 2 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Bus Voltage | Inverter | Inverter001_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV001 | Daggett 3_SUB1_INV001_Apparent Power | Inverter | Inverter001_MODBUS.HR1010_s3_VA | Apparent Power | 4 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 1 | Inverter | Inverter001_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC Input 1 | Inverter | Inverter001_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 2 | Inverter | Inverter001_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 2 | Inverter | Inverter001_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 8 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 3 | Inverter | Inverter001_MODBUS.HR5817_du3_idc_A | Current DC Input# | 9 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 3 | Inverter | Inverter001_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 10 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 4 | Inverter | Inverter001_MODBUS.HR5823_du4_idc_A | Current DC Input# | 11 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 4 | Inverter | Inverter001_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 12 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 5 | Inverter | Inverter001_MODBUS.HR5829_du5_idc_A | Current DC Input# | 13 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 5 | Inverter | Inverter001_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 14 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 6 | Inverter | Inverter001_MODBUS.HR5835_du6_idc_A | Current DC Input# | 15 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 6 | Inverter | Inverter001_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 16 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 7 | Inverter | Inverter001_MODBUS.HR5841_du7_idc_A | Current DC Input# | 17 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 7 | Inverter | Inverter001_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 18 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 8 | Inverter | Inverter001_MODBUS.HR5847_du8_idc_A | Current DC Input# | 19 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 8 | Inverter | Inverter001_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 20 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 9 | Inverter | Inverter001_MODBUS.HR5853_du9_idc_A | Current DC Input# | 21 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 9 | Inverter | Inverter001_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 22 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 10 | Inverter | Inverter001_MODBUS.HR5859_du10_idc_A | Current DC Input# | 23 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 10 | Inverter | Inverter001_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 24 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 11 | Inverter | Inverter001_MODBUS.HR5865_du11_idc_A | Current DC Input# | 25 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 11 | Inverter | Inverter001_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 26 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 12 | Inverter | Inverter001_MODBUS.HR5871_du12_idc_A | Current DC Input# | 27 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 12 | Inverter | Inverter001_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 28 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 13 | Inverter | Inverter001_MODBUS.HR5877_du13_idc_A | Current DC Input# | 29 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 13 | Inverter | Inverter001_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 30 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 14 | Inverter | Inverter001_MODBUS.HR5883_du14_idc_A | Current DC Input# | 31 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 14 | Inverter | Inverter001_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 32 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 15 | Inverter | Inverter001_MODBUS.HR5889_du15_idc_A | Current DC Input# | 33 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 15 | Inverter | Inverter001_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 34 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 16 | Inverter | Inverter001_MODBUS.HR5895_du16_idc_A | Current DC Input# | 35 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 16 | Inverter | Inverter001_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 36 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 17 | Inverter | Inverter001_MODBUS.HR5901_du17_idc_A | Current DC Input# | 37 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 17 | Inverter | Inverter001_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 38 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 18 | Inverter | Inverter001_MODBUS.HR5907_du18_idc_A | Current DC Input# | 39 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 18 | Inverter | Inverter001_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 40 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 19 | Inverter | Inverter001_MODBUS.HR5913_du19_idc_A | Current DC Input# | 41 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 19 | Inverter | Inverter001_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 42 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current DC Input 20 | Inverter | Inverter001_MODBUS.HR5919_du20_idc_A | Current DC Input# | 43 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC input 20 | Inverter | Inverter001_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 44 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current-AC | Inverter | Inverter001_MODBUS.HR1007_i3Avg_A | Current-AC | 45 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Current-DC | Inverter | Inverter001_MODBUS.HR1062_idcInput_A | Current-DC | 46 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Daily Energy Delivered | Inverter | Inverter001_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 47 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power Set Point | Inverter | Inverter001_MODBUS.HR0553_pRef | Real Power Set Point | 48 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Reactive Power Set Point | Inverter | Inverter001_MODBUS.HR0558_qRef | Reactive Power Set Point | 49 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Frequency | Inverter | Inverter001_MODBUS.HR1012_f3_Hz | Frequency | 50 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV001 | Daggett 3_SUB1_INV001_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Insulation Resistance | Inverter | Inverter001_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 51 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Number of DU Channels | Inverter | Inverter001_MODBUS.HR0653_duChannels | Number of DU Channels | 52 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Number of Running Modules | Inverter | Inverter001_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 53 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Operating State | Inverter | Inverter001_MODBUS.HR1123_currentStatus | Operating State | 54 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Power Factor | Inverter | Inverter001_MODBUS.HR1011_pf3 | Power Factor | 55 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV001 | Daggett 3_SUB1_INV001_Ramp Down | Inverter | Inverter001_MODBUS.HR0286_dropGradient_p | Ramp Down | 56 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Ramp Up | Inverter | Inverter001_MODBUS.HR0282_riseGradient_p | Ramp Up | 57 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power Delivered | Inverter | Inverter001_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 58 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Reactive Power Delivered | Inverter | Inverter001_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 59 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power | 60 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Reactive Power | Inverter | Inverter001_MODBUS.HR1009_q3_kvar | Reactive Power | 61 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Reactive Power Mode | Inverter | Inverter001_MODBUS.HR0552_qControlMode | Reactive Power Mode | 62 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Reactive Power Set Point Percent | Inverter | Inverter001_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 63 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power AC Percent | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power AC Percent | 64 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power-AC | Inverter | Inverter001_MODBUS.HR1008_p3_kW | Real Power-AC | 65 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power-DC | Inverter | Inverter001_MODBUS.HR1061_pdcInput_W | Real Power-DC | 66 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Air Intake | Inverter | Inverter001_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 67 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Cabinet | Inverter | Inverter001_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 68 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-IGBT | Inverter | Inverter001_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 69 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Temperature-Module | Inverter | Inverter001_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 70 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage A-B | Inverter | Inverter001_MODBUS.HR1001_vRS_V | Voltage A-B | 71 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage B-C | Inverter | Inverter001_MODBUS.HR1002_vST_V | Voltage B-C | 72 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage C-A | Inverter | Inverter001_MODBUS.HR1003_vTR_V | Voltage C-A | 73 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Voltage DC | Inverter | Inverter001_MODBUS.HR1051_vdcBus_V | Voltage DC | 74 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV001 | Daggett 3_SUB1_INV001_Fault Code 1 | Inverter | Inverter001_MODBUS.HRxxxx_currentFault | Fault Code 1 | 75 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Warning | Inverter | Inverter001_MODBUS.HRxxxx_currentWarning | Warning | 76 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Internal Input Status | Inverter | Inverter001_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 77 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Internal Output Status | Inverter | Inverter001_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 78 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Module Fault Code | Inverter | Inverter001_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 79 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Internal Humidity | Inverter | Inverter001_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 80 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Humidity | Inverter | Inverter001_MODBUS.HRxxxx_humidity | Humidity | 81 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_Comms Fault Time | Inverter | Inverter001_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 82 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Status | Inverter | Inverter001_MODBUS.HRxxxx_M1_status | Module Status | 83 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 IR | Inverter | Inverter001_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 84 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 IS | Inverter | Inverter001_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 85 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 IT | Inverter | Inverter001_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 86 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 87 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 88 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 89 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 90 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 P | Inverter | Inverter001_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 91 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Q | Inverter | Inverter001_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 92 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 93 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 94 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 95 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 96 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M1 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 97 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Status | Inverter | Inverter001_MODBUS.HRxxxx_M2_status | Module Status | 98 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 IR | Inverter | Inverter001_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 99 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 IS | Inverter | Inverter001_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 IT | Inverter | Inverter001_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 103 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 104 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 P | Inverter | Inverter001_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 106 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Q | Inverter | Inverter001_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 107 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 108 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 109 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 110 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 111 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M2 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Status | Inverter | Inverter001_MODBUS.HRxxxx_M3_status | Module Status | 113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 IR | Inverter | Inverter001_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 114 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 IS | Inverter | Inverter001_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 115 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 IT | Inverter | Inverter001_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 118 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 119 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 120 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 P | Inverter | Inverter001_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 121 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Q | Inverter | Inverter001_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 122 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 123 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 124 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 125 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 126 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M3 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 127 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Status | Inverter | Inverter001_MODBUS.HRxxxx_M4_status | Module Status | 128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 IR | Inverter | Inverter001_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 129 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 IS | Inverter | Inverter001_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 130 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 IT | Inverter | Inverter001_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 133 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 134 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 135 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 P | Inverter | Inverter001_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 136 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Q | Inverter | Inverter001_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 137 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 138 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 139 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 140 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 141 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M4 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 142 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Status | Inverter | Inverter001_MODBUS.HRxxxx_M5_status | Module Status | 143 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 IR | Inverter | Inverter001_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 144 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 IS | Inverter | Inverter001_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 145 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 IT | Inverter | Inverter001_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 146 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 148 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 149 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 150 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 P | Inverter | Inverter001_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 151 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Q | Inverter | Inverter001_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 152 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 153 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 154 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 155 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 156 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M5 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 157 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Status | Inverter | Inverter001_MODBUS.HRxxxx_M6_status | Module Status | 158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 IR | Inverter | Inverter001_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 159 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 IS | Inverter | Inverter001_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 160 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 IT | Inverter | Inverter001_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 IDC | Inverter | Inverter001_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 VDCP | Inverter | Inverter001_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 163 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 VDCN | Inverter | Inverter001_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 164 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 VDC | Inverter | Inverter001_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 P | Inverter | Inverter001_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 166 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Q | Inverter | Inverter001_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 167 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Ambient Temp | Inverter | Inverter001_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 168 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Max IGBT Temp | Inverter | Inverter001_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 169 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 IO Status | Inverter | Inverter001_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 170 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Hardware Version | Inverter | Inverter001_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV001 | Daggett 3_SUB1_INV001_M6 Software Version | Inverter | Inverter001_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_A Phase Current | Inverter | Inverter002_MODBUS.HR1004_i1_A | A Phase Current | 173 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_B Phase Current | Inverter | Inverter002_MODBUS.HR1005_i2_A | B Phase Current | 174 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_C Phase Current | Inverter | Inverter002_MODBUS.HR1006_i3_A | C Phase Current | 175 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Bus Voltage | Inverter | Inverter002_MODBUS.HR1051_vdcBus_V | Bus Voltage | 176 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV002 | Daggett 3_SUB1_INV002_Apparent Power | Inverter | Inverter002_MODBUS.HR1010_s3_VA | Apparent Power | 177 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 1 | Inverter | Inverter002_MODBUS.HR5805_du1_idc_A | Current DC Input# | 178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC Input 1 | Inverter | Inverter002_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 179 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 2 | Inverter | Inverter002_MODBUS.HR5811_du2_idc_A | Current DC Input# | 180 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 2 | Inverter | Inverter002_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 181 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 3 | Inverter | Inverter002_MODBUS.HR5817_du3_idc_A | Current DC Input# | 182 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 3 | Inverter | Inverter002_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 183 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 4 | Inverter | Inverter002_MODBUS.HR5823_du4_idc_A | Current DC Input# | 184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 4 | Inverter | Inverter002_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 185 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 5 | Inverter | Inverter002_MODBUS.HR5829_du5_idc_A | Current DC Input# | 186 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 5 | Inverter | Inverter002_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 187 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 6 | Inverter | Inverter002_MODBUS.HR5835_du6_idc_A | Current DC Input# | 188 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 6 | Inverter | Inverter002_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 189 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 7 | Inverter | Inverter002_MODBUS.HR5841_du7_idc_A | Current DC Input# | 190 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 7 | Inverter | Inverter002_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 191 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 8 | Inverter | Inverter002_MODBUS.HR5847_du8_idc_A | Current DC Input# | 192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 8 | Inverter | Inverter002_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 193 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 9 | Inverter | Inverter002_MODBUS.HR5853_du9_idc_A | Current DC Input# | 194 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 9 | Inverter | Inverter002_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 195 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 10 | Inverter | Inverter002_MODBUS.HR5859_du10_idc_A | Current DC Input# | 196 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 10 | Inverter | Inverter002_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 197 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 11 | Inverter | Inverter002_MODBUS.HR5865_du11_idc_A | Current DC Input# | 198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 11 | Inverter | Inverter002_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 199 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 12 | Inverter | Inverter002_MODBUS.HR5871_du12_idc_A | Current DC Input# | 200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 12 | Inverter | Inverter002_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 201 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 13 | Inverter | Inverter002_MODBUS.HR5877_du13_idc_A | Current DC Input# | 202 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 13 | Inverter | Inverter002_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 203 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 14 | Inverter | Inverter002_MODBUS.HR5883_du14_idc_A | Current DC Input# | 204 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 14 | Inverter | Inverter002_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 205 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 15 | Inverter | Inverter002_MODBUS.HR5889_du15_idc_A | Current DC Input# | 206 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 15 | Inverter | Inverter002_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 207 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 16 | Inverter | Inverter002_MODBUS.HR5895_du16_idc_A | Current DC Input# | 208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 16 | Inverter | Inverter002_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 209 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 17 | Inverter | Inverter002_MODBUS.HR5901_du17_idc_A | Current DC Input# | 210 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 17 | Inverter | Inverter002_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 211 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 18 | Inverter | Inverter002_MODBUS.HR5907_du18_idc_A | Current DC Input# | 212 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 18 | Inverter | Inverter002_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 213 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 19 | Inverter | Inverter002_MODBUS.HR5913_du19_idc_A | Current DC Input# | 214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 19 | Inverter | Inverter002_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 215 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current DC Input 20 | Inverter | Inverter002_MODBUS.HR5919_du20_idc_A | Current DC Input# | 216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC input 20 | Inverter | Inverter002_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 217 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current-AC | Inverter | Inverter002_MODBUS.HR1007_i3Avg_A | Current-AC | 218 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Current-DC | Inverter | Inverter002_MODBUS.HR1062_idcInput_A | Current-DC | 219 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Daily Energy Delivered | Inverter | Inverter002_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 220 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power Set Point | Inverter | Inverter002_MODBUS.HR0553_pRef | Real Power Set Point | 221 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Reactive Power Set Point | Inverter | Inverter002_MODBUS.HR0558_qRef | Reactive Power Set Point | 222 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Frequency | Inverter | Inverter002_MODBUS.HR1012_f3_Hz | Frequency | 223 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV002 | Daggett 3_SUB1_INV002_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Insulation Resistance | Inverter | Inverter002_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 224 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Number of DU Channels | Inverter | Inverter002_MODBUS.HR0653_duChannels | Number of DU Channels | 225 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Number of Running Modules | Inverter | Inverter002_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 226 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Operating State | Inverter | Inverter002_MODBUS.HR1123_currentStatus | Operating State | 227 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Power Factor | Inverter | Inverter002_MODBUS.HR1011_pf3 | Power Factor | 228 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV002 | Daggett 3_SUB1_INV002_Ramp Down | Inverter | Inverter002_MODBUS.HR0286_dropGradient_p | Ramp Down | 229 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Ramp Up | Inverter | Inverter002_MODBUS.HR0282_riseGradient_p | Ramp Up | 230 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power Delivered | Inverter | Inverter002_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 231 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Reactive Power Delivered | Inverter | Inverter002_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 232 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power | 233 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Reactive Power | Inverter | Inverter002_MODBUS.HR1009_q3_kvar | Reactive Power | 234 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Reactive Power Mode | Inverter | Inverter002_MODBUS.HR0552_qControlMode | Reactive Power Mode | 235 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Reactive Power Set Point Percent | Inverter | Inverter002_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 236 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power AC Percent | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power AC Percent | 237 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power-AC | Inverter | Inverter002_MODBUS.HR1008_p3_kW | Real Power-AC | 238 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power-DC | Inverter | Inverter002_MODBUS.HR1061_pdcInput_W | Real Power-DC | 239 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Air Intake | Inverter | Inverter002_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 240 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Cabinet | Inverter | Inverter002_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 241 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-IGBT | Inverter | Inverter002_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 242 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Temperature-Module | Inverter | Inverter002_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 243 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage A-B | Inverter | Inverter002_MODBUS.HR1002_vRS_V | Voltage A-B | 244 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage B-C | Inverter | Inverter002_MODBUS.HR1002_vST_V | Voltage B-C | 245 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage C-A | Inverter | Inverter002_MODBUS.HR1003_vTR_V | Voltage C-A | 246 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Voltage DC | Inverter | Inverter002_MODBUS.HR1051_vdcBus_V | Voltage DC | 247 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV002 | Daggett 3_SUB1_INV002_Fault Code 1 | Inverter | Inverter002_MODBUS.HRxxxx_currentFault | Fault Code 1 | 248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Warning | Inverter | Inverter002_MODBUS.HRxxxx_currentWarning | Warning | 249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Internal Input Status | Inverter | Inverter002_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Internal Output Status | Inverter | Inverter002_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 251 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Module Fault Code | Inverter | Inverter002_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 252 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Internal Humidity | Inverter | Inverter002_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 253 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Humidity | Inverter | Inverter002_MODBUS.HRxxxx_humidity | Humidity | 254 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_Comms Fault Time | Inverter | Inverter002_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 255 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Status | Inverter | Inverter002_MODBUS.HRxxxx_M1_status | Module Status | 256 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 IR | Inverter | Inverter002_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 257 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 IS | Inverter | Inverter002_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 IT | Inverter | Inverter002_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 261 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 262 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 263 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 P | Inverter | Inverter002_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 264 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Q | Inverter | Inverter002_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 265 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 266 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 267 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 268 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M1 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 270 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Status | Inverter | Inverter002_MODBUS.HRxxxx_M2_status | Module Status | 271 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 IR | Inverter | Inverter002_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 272 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 IS | Inverter | Inverter002_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 IT | Inverter | Inverter002_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 276 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 277 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 P | Inverter | Inverter002_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 279 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Q | Inverter | Inverter002_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 280 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 281 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 282 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 283 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 284 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M2 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Status | Inverter | Inverter002_MODBUS.HRxxxx_M3_status | Module Status | 286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 IR | Inverter | Inverter002_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 287 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 IS | Inverter | Inverter002_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 288 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 IT | Inverter | Inverter002_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 291 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 292 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 293 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 P | Inverter | Inverter002_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 294 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Q | Inverter | Inverter002_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 295 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 296 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 297 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 298 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 299 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M3 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 300 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Status | Inverter | Inverter002_MODBUS.HRxxxx_M4_status | Module Status | 301 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 IR | Inverter | Inverter002_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 302 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 IS | Inverter | Inverter002_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 303 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 IT | Inverter | Inverter002_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 306 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 307 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 308 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 P | Inverter | Inverter002_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 309 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Q | Inverter | Inverter002_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 310 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 311 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 312 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 313 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 314 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M4 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 315 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Status | Inverter | Inverter002_MODBUS.HRxxxx_M5_status | Module Status | 316 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 IR | Inverter | Inverter002_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 317 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 IS | Inverter | Inverter002_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 318 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 IT | Inverter | Inverter002_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 319 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 321 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 322 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 323 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 P | Inverter | Inverter002_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 324 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Q | Inverter | Inverter002_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 325 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 326 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 327 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 328 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 329 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M5 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 330 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Status | Inverter | Inverter002_MODBUS.HRxxxx_M6_status | Module Status | 331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 IR | Inverter | Inverter002_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 332 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 IS | Inverter | Inverter002_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 333 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 IT | Inverter | Inverter002_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 IDC | Inverter | Inverter002_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 VDCP | Inverter | Inverter002_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 336 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 VDCN | Inverter | Inverter002_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 337 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 VDC | Inverter | Inverter002_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 P | Inverter | Inverter002_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 339 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Q | Inverter | Inverter002_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 340 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Ambient Temp | Inverter | Inverter002_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 341 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Max IGBT Temp | Inverter | Inverter002_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 342 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 IO Status | Inverter | Inverter002_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 343 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Hardware Version | Inverter | Inverter002_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV002 | Daggett 3_SUB1_INV002_M6 Software Version | Inverter | Inverter002_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_A Phase Current | Inverter | Inverter003_MODBUS.HR1004_i1_A | A Phase Current | 346 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_B Phase Current | Inverter | Inverter003_MODBUS.HR1005_i2_A | B Phase Current | 347 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_C Phase Current | Inverter | Inverter003_MODBUS.HR1006_i3_A | C Phase Current | 348 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Bus Voltage | Inverter | Inverter003_MODBUS.HR1051_vdcBus_V | Bus Voltage | 349 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV003 | Daggett 3_SUB1_INV003_Apparent Power | Inverter | Inverter003_MODBUS.HR1010_s3_VA | Apparent Power | 350 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 1 | Inverter | Inverter003_MODBUS.HR5805_du1_idc_A | Current DC Input# | 351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC Input 1 | Inverter | Inverter003_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 352 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 2 | Inverter | Inverter003_MODBUS.HR5811_du2_idc_A | Current DC Input# | 353 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 2 | Inverter | Inverter003_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 354 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 3 | Inverter | Inverter003_MODBUS.HR5817_du3_idc_A | Current DC Input# | 355 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 3 | Inverter | Inverter003_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 356 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 4 | Inverter | Inverter003_MODBUS.HR5823_du4_idc_A | Current DC Input# | 357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 4 | Inverter | Inverter003_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 358 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 5 | Inverter | Inverter003_MODBUS.HR5829_du5_idc_A | Current DC Input# | 359 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 5 | Inverter | Inverter003_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 360 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 6 | Inverter | Inverter003_MODBUS.HR5835_du6_idc_A | Current DC Input# | 361 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 6 | Inverter | Inverter003_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 362 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 7 | Inverter | Inverter003_MODBUS.HR5841_du7_idc_A | Current DC Input# | 363 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 7 | Inverter | Inverter003_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 364 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 8 | Inverter | Inverter003_MODBUS.HR5847_du8_idc_A | Current DC Input# | 365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 8 | Inverter | Inverter003_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 366 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 9 | Inverter | Inverter003_MODBUS.HR5853_du9_idc_A | Current DC Input# | 367 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 9 | Inverter | Inverter003_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 368 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 10 | Inverter | Inverter003_MODBUS.HR5859_du10_idc_A | Current DC Input# | 369 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 10 | Inverter | Inverter003_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 370 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 11 | Inverter | Inverter003_MODBUS.HR5865_du11_idc_A | Current DC Input# | 371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 11 | Inverter | Inverter003_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 372 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 12 | Inverter | Inverter003_MODBUS.HR5871_du12_idc_A | Current DC Input# | 373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 12 | Inverter | Inverter003_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 374 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 13 | Inverter | Inverter003_MODBUS.HR5877_du13_idc_A | Current DC Input# | 375 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 13 | Inverter | Inverter003_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 376 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 14 | Inverter | Inverter003_MODBUS.HR5883_du14_idc_A | Current DC Input# | 377 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 14 | Inverter | Inverter003_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 378 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 15 | Inverter | Inverter003_MODBUS.HR5889_du15_idc_A | Current DC Input# | 379 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 15 | Inverter | Inverter003_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 380 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 16 | Inverter | Inverter003_MODBUS.HR5895_du16_idc_A | Current DC Input# | 381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 16 | Inverter | Inverter003_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 382 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 17 | Inverter | Inverter003_MODBUS.HR5901_du17_idc_A | Current DC Input# | 383 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 17 | Inverter | Inverter003_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 384 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 18 | Inverter | Inverter003_MODBUS.HR5907_du18_idc_A | Current DC Input# | 385 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 18 | Inverter | Inverter003_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 386 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 19 | Inverter | Inverter003_MODBUS.HR5913_du19_idc_A | Current DC Input# | 387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 19 | Inverter | Inverter003_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 388 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current DC Input 20 | Inverter | Inverter003_MODBUS.HR5919_du20_idc_A | Current DC Input# | 389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC input 20 | Inverter | Inverter003_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 390 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current-AC | Inverter | Inverter003_MODBUS.HR1007_i3Avg_A | Current-AC | 391 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Current-DC | Inverter | Inverter003_MODBUS.HR1062_idcInput_A | Current-DC | 392 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Daily Energy Delivered | Inverter | Inverter003_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 393 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power Set Point | Inverter | Inverter003_MODBUS.HR0553_pRef | Real Power Set Point | 394 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Reactive Power Set Point | Inverter | Inverter003_MODBUS.HR0558_qRef | Reactive Power Set Point | 395 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Frequency | Inverter | Inverter003_MODBUS.HR1012_f3_Hz | Frequency | 396 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV003 | Daggett 3_SUB1_INV003_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Insulation Resistance | Inverter | Inverter003_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 397 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Number of DU Channels | Inverter | Inverter003_MODBUS.HR0653_duChannels | Number of DU Channels | 398 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Number of Running Modules | Inverter | Inverter003_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 399 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Operating State | Inverter | Inverter003_MODBUS.HR1123_currentStatus | Operating State | 400 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Power Factor | Inverter | Inverter003_MODBUS.HR1011_pf3 | Power Factor | 401 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV003 | Daggett 3_SUB1_INV003_Ramp Down | Inverter | Inverter003_MODBUS.HR0286_dropGradient_p | Ramp Down | 402 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Ramp Up | Inverter | Inverter003_MODBUS.HR0282_riseGradient_p | Ramp Up | 403 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power Delivered | Inverter | Inverter003_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 404 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Reactive Power Delivered | Inverter | Inverter003_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 405 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power | 406 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Reactive Power | Inverter | Inverter003_MODBUS.HR1009_q3_kvar | Reactive Power | 407 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Reactive Power Mode | Inverter | Inverter003_MODBUS.HR0552_qControlMode | Reactive Power Mode | 408 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Reactive Power Set Point Percent | Inverter | Inverter003_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 409 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power AC Percent | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power AC Percent | 410 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power-AC | Inverter | Inverter003_MODBUS.HR1008_p3_kW | Real Power-AC | 411 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power-DC | Inverter | Inverter003_MODBUS.HR1061_pdcInput_W | Real Power-DC | 412 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Air Intake | Inverter | Inverter003_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 413 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Cabinet | Inverter | Inverter003_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 414 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-IGBT | Inverter | Inverter003_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 415 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Temperature-Module | Inverter | Inverter003_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 416 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage A-B | Inverter | Inverter003_MODBUS.HR1003_vRS_V | Voltage A-B | 417 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage B-C | Inverter | Inverter003_MODBUS.HR1002_vST_V | Voltage B-C | 418 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage C-A | Inverter | Inverter003_MODBUS.HR1003_vTR_V | Voltage C-A | 419 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Voltage DC | Inverter | Inverter003_MODBUS.HR1051_vdcBus_V | Voltage DC | 420 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV003 | Daggett 3_SUB1_INV003_Fault Code 1 | Inverter | Inverter003_MODBUS.HRxxxx_currentFault | Fault Code 1 | 421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Warning | Inverter | Inverter003_MODBUS.HRxxxx_currentWarning | Warning | 422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Internal Input Status | Inverter | Inverter003_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Internal Output Status | Inverter | Inverter003_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 424 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Module Fault Code | Inverter | Inverter003_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 425 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Internal Humidity | Inverter | Inverter003_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 426 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Humidity | Inverter | Inverter003_MODBUS.HRxxxx_humidity | Humidity | 427 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_Comms Fault Time | Inverter | Inverter003_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 428 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Status | Inverter | Inverter003_MODBUS.HRxxxx_M1_status | Module Status | 429 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 IR | Inverter | Inverter003_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 430 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 IS | Inverter | Inverter003_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 IT | Inverter | Inverter003_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 434 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 435 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 436 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 P | Inverter | Inverter003_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 437 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Q | Inverter | Inverter003_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 438 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 439 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 440 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 441 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M1 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 443 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Status | Inverter | Inverter003_MODBUS.HRxxxx_M2_status | Module Status | 444 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 IR | Inverter | Inverter003_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 445 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 IS | Inverter | Inverter003_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 IT | Inverter | Inverter003_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 449 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 450 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 P | Inverter | Inverter003_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 452 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Q | Inverter | Inverter003_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 453 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 454 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 455 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 456 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 457 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M2 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Status | Inverter | Inverter003_MODBUS.HRxxxx_M3_status | Module Status | 459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 IR | Inverter | Inverter003_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 460 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 IS | Inverter | Inverter003_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 461 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 IT | Inverter | Inverter003_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 464 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 465 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 466 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 P | Inverter | Inverter003_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 467 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Q | Inverter | Inverter003_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 468 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 469 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 470 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 471 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 472 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M3 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 473 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Status | Inverter | Inverter003_MODBUS.HRxxxx_M4_status | Module Status | 474 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 IR | Inverter | Inverter003_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 475 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 IS | Inverter | Inverter003_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 476 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 IT | Inverter | Inverter003_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 479 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 480 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 481 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 P | Inverter | Inverter003_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 482 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Q | Inverter | Inverter003_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 483 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 484 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 485 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 486 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 487 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M4 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 488 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Status | Inverter | Inverter003_MODBUS.HRxxxx_M5_status | Module Status | 489 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 IR | Inverter | Inverter003_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 490 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 IS | Inverter | Inverter003_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 491 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 IT | Inverter | Inverter003_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 492 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 494 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 495 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 496 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 P | Inverter | Inverter003_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 497 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Q | Inverter | Inverter003_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 498 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 499 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 500 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 501 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 502 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M5 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 503 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Status | Inverter | Inverter003_MODBUS.HRxxxx_M6_status | Module Status | 504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 IR | Inverter | Inverter003_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 505 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 IS | Inverter | Inverter003_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 506 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 IT | Inverter | Inverter003_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 IDC | Inverter | Inverter003_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 VDCP | Inverter | Inverter003_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 509 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 VDCN | Inverter | Inverter003_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 510 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 VDC | Inverter | Inverter003_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 P | Inverter | Inverter003_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 512 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Q | Inverter | Inverter003_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 513 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Ambient Temp | Inverter | Inverter003_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 514 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Max IGBT Temp | Inverter | Inverter003_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 515 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 IO Status | Inverter | Inverter003_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 516 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Hardware Version | Inverter | Inverter003_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV003 | Daggett 3_SUB1_INV003_M6 Software Version | Inverter | Inverter003_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_A Phase Current | Inverter | Inverter004_MODBUS.HR1004_i1_A | A Phase Current | 519 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_B Phase Current | Inverter | Inverter004_MODBUS.HR1005_i2_A | B Phase Current | 520 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_C Phase Current | Inverter | Inverter004_MODBUS.HR1006_i3_A | C Phase Current | 521 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Bus Voltage | Inverter | Inverter004_MODBUS.HR1051_vdcBus_V | Bus Voltage | 522 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV004 | Daggett 3_SUB1_INV004_Apparent Power | Inverter | Inverter004_MODBUS.HR1010_s3_VA | Apparent Power | 523 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 1 | Inverter | Inverter004_MODBUS.HR5805_du1_idc_A | Current DC Input# | 524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC Input 1 | Inverter | Inverter004_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 525 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 2 | Inverter | Inverter004_MODBUS.HR5811_du2_idc_A | Current DC Input# | 526 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 2 | Inverter | Inverter004_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 527 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 3 | Inverter | Inverter004_MODBUS.HR5817_du3_idc_A | Current DC Input# | 528 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 3 | Inverter | Inverter004_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 529 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 4 | Inverter | Inverter004_MODBUS.HR5823_du4_idc_A | Current DC Input# | 530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 4 | Inverter | Inverter004_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 531 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 5 | Inverter | Inverter004_MODBUS.HR5829_du5_idc_A | Current DC Input# | 532 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 5 | Inverter | Inverter004_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 533 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 6 | Inverter | Inverter004_MODBUS.HR5835_du6_idc_A | Current DC Input# | 534 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 6 | Inverter | Inverter004_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 535 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 7 | Inverter | Inverter004_MODBUS.HR5841_du7_idc_A | Current DC Input# | 536 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 7 | Inverter | Inverter004_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 537 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 8 | Inverter | Inverter004_MODBUS.HR5847_du8_idc_A | Current DC Input# | 538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 8 | Inverter | Inverter004_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 539 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 9 | Inverter | Inverter004_MODBUS.HR5853_du9_idc_A | Current DC Input# | 540 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 9 | Inverter | Inverter004_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 541 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 10 | Inverter | Inverter004_MODBUS.HR5859_du10_idc_A | Current DC Input# | 542 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 10 | Inverter | Inverter004_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 543 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 11 | Inverter | Inverter004_MODBUS.HR5865_du11_idc_A | Current DC Input# | 544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 11 | Inverter | Inverter004_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 545 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 12 | Inverter | Inverter004_MODBUS.HR5871_du12_idc_A | Current DC Input# | 546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 12 | Inverter | Inverter004_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 547 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 13 | Inverter | Inverter004_MODBUS.HR5877_du13_idc_A | Current DC Input# | 548 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 13 | Inverter | Inverter004_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 549 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 14 | Inverter | Inverter004_MODBUS.HR5883_du14_idc_A | Current DC Input# | 550 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 14 | Inverter | Inverter004_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 551 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 15 | Inverter | Inverter004_MODBUS.HR5889_du15_idc_A | Current DC Input# | 552 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 15 | Inverter | Inverter004_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 553 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 16 | Inverter | Inverter004_MODBUS.HR5895_du16_idc_A | Current DC Input# | 554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 16 | Inverter | Inverter004_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 555 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 17 | Inverter | Inverter004_MODBUS.HR5901_du17_idc_A | Current DC Input# | 556 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 17 | Inverter | Inverter004_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 557 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 18 | Inverter | Inverter004_MODBUS.HR5907_du18_idc_A | Current DC Input# | 558 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 18 | Inverter | Inverter004_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 559 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 19 | Inverter | Inverter004_MODBUS.HR5913_du19_idc_A | Current DC Input# | 560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 19 | Inverter | Inverter004_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 561 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current DC Input 20 | Inverter | Inverter004_MODBUS.HR5919_du20_idc_A | Current DC Input# | 562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC input 20 | Inverter | Inverter004_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 563 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current-AC | Inverter | Inverter004_MODBUS.HR1007_i3Avg_A | Current-AC | 564 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Current-DC | Inverter | Inverter004_MODBUS.HR1062_idcInput_A | Current-DC | 565 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Daily Energy Delivered | Inverter | Inverter004_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 566 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power Set Point | Inverter | Inverter004_MODBUS.HR0553_pRef | Real Power Set Point | 567 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Reactive Power Set Point | Inverter | Inverter004_MODBUS.HR0558_qRef | Reactive Power Set Point | 568 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Frequency | Inverter | Inverter004_MODBUS.HR1012_f3_Hz | Frequency | 569 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV004 | Daggett 3_SUB1_INV004_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Insulation Resistance | Inverter | Inverter004_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 570 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Number of DU Channels | Inverter | Inverter004_MODBUS.HR0653_duChannels | Number of DU Channels | 571 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Number of Running Modules | Inverter | Inverter004_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 572 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Operating State | Inverter | Inverter004_MODBUS.HR1123_currentStatus | Operating State | 573 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Power Factor | Inverter | Inverter004_MODBUS.HR1011_pf3 | Power Factor | 574 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV004 | Daggett 3_SUB1_INV004_Ramp Down | Inverter | Inverter004_MODBUS.HR0286_dropGradient_p | Ramp Down | 575 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Ramp Up | Inverter | Inverter004_MODBUS.HR0282_riseGradient_p | Ramp Up | 576 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power Delivered | Inverter | Inverter004_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 577 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Reactive Power Delivered | Inverter | Inverter004_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 578 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power | 579 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Reactive Power | Inverter | Inverter004_MODBUS.HR1009_q3_kvar | Reactive Power | 580 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Reactive Power Mode | Inverter | Inverter004_MODBUS.HR0552_qControlMode | Reactive Power Mode | 581 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Reactive Power Set Point Percent | Inverter | Inverter004_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 582 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power AC Percent | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power AC Percent | 583 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power-AC | Inverter | Inverter004_MODBUS.HR1008_p3_kW | Real Power-AC | 584 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power-DC | Inverter | Inverter004_MODBUS.HR1061_pdcInput_W | Real Power-DC | 585 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Air Intake | Inverter | Inverter004_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 586 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Cabinet | Inverter | Inverter004_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 587 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-IGBT | Inverter | Inverter004_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 588 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Temperature-Module | Inverter | Inverter004_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 589 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage A-B | Inverter | Inverter004_MODBUS.HR1004_vRS_V | Voltage A-B | 590 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage B-C | Inverter | Inverter004_MODBUS.HR1002_vST_V | Voltage B-C | 591 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage C-A | Inverter | Inverter004_MODBUS.HR1003_vTR_V | Voltage C-A | 592 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Voltage DC | Inverter | Inverter004_MODBUS.HR1051_vdcBus_V | Voltage DC | 593 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV004 | Daggett 3_SUB1_INV004_Fault Code 1 | Inverter | Inverter004_MODBUS.HRxxxx_currentFault | Fault Code 1 | 594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Warning | Inverter | Inverter004_MODBUS.HRxxxx_currentWarning | Warning | 595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Internal Input Status | Inverter | Inverter004_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Internal Output Status | Inverter | Inverter004_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 597 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Module Fault Code | Inverter | Inverter004_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 598 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Internal Humidity | Inverter | Inverter004_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 599 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Humidity | Inverter | Inverter004_MODBUS.HRxxxx_humidity | Humidity | 600 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_Comms Fault Time | Inverter | Inverter004_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 601 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Status | Inverter | Inverter004_MODBUS.HRxxxx_M1_status | Module Status | 602 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 IR | Inverter | Inverter004_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 603 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 IS | Inverter | Inverter004_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 IT | Inverter | Inverter004_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 607 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 608 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 609 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 P | Inverter | Inverter004_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 610 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Q | Inverter | Inverter004_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 611 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 612 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 613 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 614 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M1 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 616 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Status | Inverter | Inverter004_MODBUS.HRxxxx_M2_status | Module Status | 617 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 IR | Inverter | Inverter004_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 618 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 IS | Inverter | Inverter004_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 IT | Inverter | Inverter004_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 622 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 623 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 P | Inverter | Inverter004_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 625 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Q | Inverter | Inverter004_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 626 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 627 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 628 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 629 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 630 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M2 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Status | Inverter | Inverter004_MODBUS.HRxxxx_M3_status | Module Status | 632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 IR | Inverter | Inverter004_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 633 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 IS | Inverter | Inverter004_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 634 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 IT | Inverter | Inverter004_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 637 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 638 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 639 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 P | Inverter | Inverter004_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 640 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Q | Inverter | Inverter004_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 641 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 642 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 643 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 644 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 645 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M3 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 646 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Status | Inverter | Inverter004_MODBUS.HRxxxx_M4_status | Module Status | 647 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 IR | Inverter | Inverter004_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 648 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 IS | Inverter | Inverter004_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 649 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 IT | Inverter | Inverter004_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 652 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 653 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 654 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 P | Inverter | Inverter004_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 655 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Q | Inverter | Inverter004_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 656 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 657 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 658 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 659 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 660 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M4 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 661 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Status | Inverter | Inverter004_MODBUS.HRxxxx_M5_status | Module Status | 662 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 IR | Inverter | Inverter004_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 663 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 IS | Inverter | Inverter004_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 664 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 IT | Inverter | Inverter004_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 665 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 667 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 668 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 669 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 P | Inverter | Inverter004_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 670 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Q | Inverter | Inverter004_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 671 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 672 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 673 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 674 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 675 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M5 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 676 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Status | Inverter | Inverter004_MODBUS.HRxxxx_M6_status | Module Status | 677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 IR | Inverter | Inverter004_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 678 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 IS | Inverter | Inverter004_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 679 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 IT | Inverter | Inverter004_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 IDC | Inverter | Inverter004_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 VDCP | Inverter | Inverter004_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 682 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 VDCN | Inverter | Inverter004_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 683 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 VDC | Inverter | Inverter004_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 P | Inverter | Inverter004_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 685 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Q | Inverter | Inverter004_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 686 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Ambient Temp | Inverter | Inverter004_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 687 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Max IGBT Temp | Inverter | Inverter004_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 688 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 IO Status | Inverter | Inverter004_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 689 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Hardware Version | Inverter | Inverter004_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV004 | Daggett 3_SUB1_INV004_M6 Software Version | Inverter | Inverter004_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_A Phase Current | Inverter | Inverter005_MODBUS.HR1004_i1_A | A Phase Current | 692 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_B Phase Current | Inverter | Inverter005_MODBUS.HR1005_i2_A | B Phase Current | 693 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_C Phase Current | Inverter | Inverter005_MODBUS.HR1006_i3_A | C Phase Current | 694 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Bus Voltage | Inverter | Inverter005_MODBUS.HR1051_vdcBus_V | Bus Voltage | 695 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV005 | Daggett 3_SUB1_INV005_Apparent Power | Inverter | Inverter005_MODBUS.HR1010_s3_VA | Apparent Power | 696 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 1 | Inverter | Inverter005_MODBUS.HR5805_du1_idc_A | Current DC Input# | 697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC Input 1 | Inverter | Inverter005_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 698 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 2 | Inverter | Inverter005_MODBUS.HR5811_du2_idc_A | Current DC Input# | 699 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 2 | Inverter | Inverter005_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 700 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 3 | Inverter | Inverter005_MODBUS.HR5817_du3_idc_A | Current DC Input# | 701 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 3 | Inverter | Inverter005_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 702 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 4 | Inverter | Inverter005_MODBUS.HR5823_du4_idc_A | Current DC Input# | 703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 4 | Inverter | Inverter005_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 704 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 5 | Inverter | Inverter005_MODBUS.HR5829_du5_idc_A | Current DC Input# | 705 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 5 | Inverter | Inverter005_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 706 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 6 | Inverter | Inverter005_MODBUS.HR5835_du6_idc_A | Current DC Input# | 707 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 6 | Inverter | Inverter005_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 708 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 7 | Inverter | Inverter005_MODBUS.HR5841_du7_idc_A | Current DC Input# | 709 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 7 | Inverter | Inverter005_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 710 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 8 | Inverter | Inverter005_MODBUS.HR5847_du8_idc_A | Current DC Input# | 711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 8 | Inverter | Inverter005_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 712 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 9 | Inverter | Inverter005_MODBUS.HR5853_du9_idc_A | Current DC Input# | 713 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 9 | Inverter | Inverter005_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 714 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 10 | Inverter | Inverter005_MODBUS.HR5859_du10_idc_A | Current DC Input# | 715 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 10 | Inverter | Inverter005_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 716 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 11 | Inverter | Inverter005_MODBUS.HR5865_du11_idc_A | Current DC Input# | 717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 11 | Inverter | Inverter005_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 718 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 12 | Inverter | Inverter005_MODBUS.HR5871_du12_idc_A | Current DC Input# | 719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 12 | Inverter | Inverter005_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 720 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 13 | Inverter | Inverter005_MODBUS.HR5877_du13_idc_A | Current DC Input# | 721 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 13 | Inverter | Inverter005_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 722 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 14 | Inverter | Inverter005_MODBUS.HR5883_du14_idc_A | Current DC Input# | 723 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 14 | Inverter | Inverter005_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 724 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 15 | Inverter | Inverter005_MODBUS.HR5889_du15_idc_A | Current DC Input# | 725 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 15 | Inverter | Inverter005_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 726 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 16 | Inverter | Inverter005_MODBUS.HR5895_du16_idc_A | Current DC Input# | 727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 16 | Inverter | Inverter005_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 728 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 17 | Inverter | Inverter005_MODBUS.HR5901_du17_idc_A | Current DC Input# | 729 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 17 | Inverter | Inverter005_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 730 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 18 | Inverter | Inverter005_MODBUS.HR5907_du18_idc_A | Current DC Input# | 731 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 18 | Inverter | Inverter005_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 732 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 19 | Inverter | Inverter005_MODBUS.HR5913_du19_idc_A | Current DC Input# | 733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 19 | Inverter | Inverter005_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 734 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current DC Input 20 | Inverter | Inverter005_MODBUS.HR5919_du20_idc_A | Current DC Input# | 735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC input 20 | Inverter | Inverter005_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 736 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current-AC | Inverter | Inverter005_MODBUS.HR1007_i3Avg_A | Current-AC | 737 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Current-DC | Inverter | Inverter005_MODBUS.HR1062_idcInput_A | Current-DC | 738 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Daily Energy Delivered | Inverter | Inverter005_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 739 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power Set Point | Inverter | Inverter005_MODBUS.HR0553_pRef | Real Power Set Point | 740 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Reactive Power Set Point | Inverter | Inverter005_MODBUS.HR0558_qRef | Reactive Power Set Point | 741 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Frequency | Inverter | Inverter005_MODBUS.HR1012_f3_Hz | Frequency | 742 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV005 | Daggett 3_SUB1_INV005_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Insulation Resistance | Inverter | Inverter005_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 743 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Number of DU Channels | Inverter | Inverter005_MODBUS.HR0653_duChannels | Number of DU Channels | 744 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Number of Running Modules | Inverter | Inverter005_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 745 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Operating State | Inverter | Inverter005_MODBUS.HR1123_currentStatus | Operating State | 746 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Power Factor | Inverter | Inverter005_MODBUS.HR1011_pf3 | Power Factor | 747 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV005 | Daggett 3_SUB1_INV005_Ramp Down | Inverter | Inverter005_MODBUS.HR0286_dropGradient_p | Ramp Down | 748 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Ramp Up | Inverter | Inverter005_MODBUS.HR0282_riseGradient_p | Ramp Up | 749 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power Delivered | Inverter | Inverter005_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 750 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Reactive Power Delivered | Inverter | Inverter005_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 751 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power | 752 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Reactive Power | Inverter | Inverter005_MODBUS.HR1009_q3_kvar | Reactive Power | 753 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Reactive Power Mode | Inverter | Inverter005_MODBUS.HR0552_qControlMode | Reactive Power Mode | 754 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Reactive Power Set Point Percent | Inverter | Inverter005_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 755 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power AC Percent | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power AC Percent | 756 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power-AC | Inverter | Inverter005_MODBUS.HR1008_p3_kW | Real Power-AC | 757 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power-DC | Inverter | Inverter005_MODBUS.HR1061_pdcInput_W | Real Power-DC | 758 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Air Intake | Inverter | Inverter005_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 759 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Cabinet | Inverter | Inverter005_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 760 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-IGBT | Inverter | Inverter005_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 761 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Temperature-Module | Inverter | Inverter005_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 762 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage A-B | Inverter | Inverter005_MODBUS.HR1005_vRS_V | Voltage A-B | 763 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage B-C | Inverter | Inverter005_MODBUS.HR1002_vST_V | Voltage B-C | 764 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage C-A | Inverter | Inverter005_MODBUS.HR1003_vTR_V | Voltage C-A | 765 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Voltage DC | Inverter | Inverter005_MODBUS.HR1051_vdcBus_V | Voltage DC | 766 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV005 | Daggett 3_SUB1_INV005_Fault Code 1 | Inverter | Inverter005_MODBUS.HRxxxx_currentFault | Fault Code 1 | 767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Warning | Inverter | Inverter005_MODBUS.HRxxxx_currentWarning | Warning | 768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Internal Input Status | Inverter | Inverter005_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Internal Output Status | Inverter | Inverter005_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 770 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Module Fault Code | Inverter | Inverter005_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 771 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Internal Humidity | Inverter | Inverter005_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 772 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Humidity | Inverter | Inverter005_MODBUS.HRxxxx_humidity | Humidity | 773 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_Comms Fault Time | Inverter | Inverter005_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 774 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Status | Inverter | Inverter005_MODBUS.HRxxxx_M1_status | Module Status | 775 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 IR | Inverter | Inverter005_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 776 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 IS | Inverter | Inverter005_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 IT | Inverter | Inverter005_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 780 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 781 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 782 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 P | Inverter | Inverter005_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 783 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Q | Inverter | Inverter005_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 784 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 785 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 786 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 787 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M1 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 789 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Status | Inverter | Inverter005_MODBUS.HRxxxx_M2_status | Module Status | 790 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 IR | Inverter | Inverter005_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 791 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 IS | Inverter | Inverter005_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 IT | Inverter | Inverter005_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 795 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 796 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 P | Inverter | Inverter005_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 798 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Q | Inverter | Inverter005_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 799 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 800 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 801 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 802 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 803 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M2 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Status | Inverter | Inverter005_MODBUS.HRxxxx_M3_status | Module Status | 805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 IR | Inverter | Inverter005_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 806 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 IS | Inverter | Inverter005_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 807 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 IT | Inverter | Inverter005_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 810 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 811 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 812 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 P | Inverter | Inverter005_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 813 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Q | Inverter | Inverter005_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 814 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 815 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 816 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 817 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 818 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M3 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 819 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Status | Inverter | Inverter005_MODBUS.HRxxxx_M4_status | Module Status | 820 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 IR | Inverter | Inverter005_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 821 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 IS | Inverter | Inverter005_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 822 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 IT | Inverter | Inverter005_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 825 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 826 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 827 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 P | Inverter | Inverter005_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 828 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Q | Inverter | Inverter005_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 829 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 830 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 831 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 832 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 833 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M4 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 834 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Status | Inverter | Inverter005_MODBUS.HRxxxx_M5_status | Module Status | 835 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 IR | Inverter | Inverter005_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 836 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 IS | Inverter | Inverter005_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 837 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 IT | Inverter | Inverter005_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 838 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 840 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 841 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 842 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 P | Inverter | Inverter005_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 843 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Q | Inverter | Inverter005_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 844 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 845 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 846 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 847 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 848 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M5 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 849 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Status | Inverter | Inverter005_MODBUS.HRxxxx_M6_status | Module Status | 850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 IR | Inverter | Inverter005_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 851 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 IS | Inverter | Inverter005_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 852 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 IT | Inverter | Inverter005_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 IDC | Inverter | Inverter005_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 VDCP | Inverter | Inverter005_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 855 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 VDCN | Inverter | Inverter005_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 856 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 VDC | Inverter | Inverter005_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 P | Inverter | Inverter005_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 858 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Q | Inverter | Inverter005_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 859 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Ambient Temp | Inverter | Inverter005_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 860 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Max IGBT Temp | Inverter | Inverter005_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 861 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 IO Status | Inverter | Inverter005_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 862 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Hardware Version | Inverter | Inverter005_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV005 | Daggett 3_SUB1_INV005_M6 Software Version | Inverter | Inverter005_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_A Phase Current | Inverter | Inverter006_MODBUS.HR1004_i1_A | A Phase Current | 865 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_B Phase Current | Inverter | Inverter006_MODBUS.HR1005_i2_A | B Phase Current | 866 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_C Phase Current | Inverter | Inverter006_MODBUS.HR1006_i3_A | C Phase Current | 867 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Bus Voltage | Inverter | Inverter006_MODBUS.HR1051_vdcBus_V | Bus Voltage | 868 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV006 | Daggett 3_SUB1_INV006_Apparent Power | Inverter | Inverter006_MODBUS.HR1010_s3_VA | Apparent Power | 869 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 1 | Inverter | Inverter006_MODBUS.HR5805_du1_idc_A | Current DC Input# | 870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC Input 1 | Inverter | Inverter006_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 871 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 2 | Inverter | Inverter006_MODBUS.HR5811_du2_idc_A | Current DC Input# | 872 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 2 | Inverter | Inverter006_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 873 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 3 | Inverter | Inverter006_MODBUS.HR5817_du3_idc_A | Current DC Input# | 874 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 3 | Inverter | Inverter006_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 875 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 4 | Inverter | Inverter006_MODBUS.HR5823_du4_idc_A | Current DC Input# | 876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 4 | Inverter | Inverter006_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 877 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 5 | Inverter | Inverter006_MODBUS.HR5829_du5_idc_A | Current DC Input# | 878 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 5 | Inverter | Inverter006_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 879 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 6 | Inverter | Inverter006_MODBUS.HR5835_du6_idc_A | Current DC Input# | 880 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 6 | Inverter | Inverter006_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 881 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 7 | Inverter | Inverter006_MODBUS.HR5841_du7_idc_A | Current DC Input# | 882 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 7 | Inverter | Inverter006_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 883 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 8 | Inverter | Inverter006_MODBUS.HR5847_du8_idc_A | Current DC Input# | 884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 8 | Inverter | Inverter006_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 885 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 9 | Inverter | Inverter006_MODBUS.HR5853_du9_idc_A | Current DC Input# | 886 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 9 | Inverter | Inverter006_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 887 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 10 | Inverter | Inverter006_MODBUS.HR5859_du10_idc_A | Current DC Input# | 888 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 10 | Inverter | Inverter006_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 889 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 11 | Inverter | Inverter006_MODBUS.HR5865_du11_idc_A | Current DC Input# | 890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 11 | Inverter | Inverter006_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 891 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 12 | Inverter | Inverter006_MODBUS.HR5871_du12_idc_A | Current DC Input# | 892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 12 | Inverter | Inverter006_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 893 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 13 | Inverter | Inverter006_MODBUS.HR5877_du13_idc_A | Current DC Input# | 894 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 13 | Inverter | Inverter006_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 895 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 14 | Inverter | Inverter006_MODBUS.HR5883_du14_idc_A | Current DC Input# | 896 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 14 | Inverter | Inverter006_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 897 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 15 | Inverter | Inverter006_MODBUS.HR5889_du15_idc_A | Current DC Input# | 898 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 15 | Inverter | Inverter006_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 899 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 16 | Inverter | Inverter006_MODBUS.HR5895_du16_idc_A | Current DC Input# | 900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 16 | Inverter | Inverter006_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 901 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 17 | Inverter | Inverter006_MODBUS.HR5901_du17_idc_A | Current DC Input# | 902 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 17 | Inverter | Inverter006_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 903 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 18 | Inverter | Inverter006_MODBUS.HR5907_du18_idc_A | Current DC Input# | 904 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 18 | Inverter | Inverter006_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 905 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 19 | Inverter | Inverter006_MODBUS.HR5913_du19_idc_A | Current DC Input# | 906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 19 | Inverter | Inverter006_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 907 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current DC Input 20 | Inverter | Inverter006_MODBUS.HR5919_du20_idc_A | Current DC Input# | 908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC input 20 | Inverter | Inverter006_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 909 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current-AC | Inverter | Inverter006_MODBUS.HR1007_i3Avg_A | Current-AC | 910 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Current-DC | Inverter | Inverter006_MODBUS.HR1062_idcInput_A | Current-DC | 911 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Daily Energy Delivered | Inverter | Inverter006_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 912 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power Set Point | Inverter | Inverter006_MODBUS.HR0553_pRef | Real Power Set Point | 913 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Reactive Power Set Point | Inverter | Inverter006_MODBUS.HR0558_qRef | Reactive Power Set Point | 914 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Frequency | Inverter | Inverter006_MODBUS.HR1012_f3_Hz | Frequency | 915 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV006 | Daggett 3_SUB1_INV006_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Insulation Resistance | Inverter | Inverter006_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 916 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Number of DU Channels | Inverter | Inverter006_MODBUS.HR0653_duChannels | Number of DU Channels | 917 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Number of Running Modules | Inverter | Inverter006_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 918 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Operating State | Inverter | Inverter006_MODBUS.HR1123_currentStatus | Operating State | 919 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Power Factor | Inverter | Inverter006_MODBUS.HR1011_pf3 | Power Factor | 920 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV006 | Daggett 3_SUB1_INV006_Ramp Down | Inverter | Inverter006_MODBUS.HR0286_dropGradient_p | Ramp Down | 921 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Ramp Up | Inverter | Inverter006_MODBUS.HR0282_riseGradient_p | Ramp Up | 922 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power Delivered | Inverter | Inverter006_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 923 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Reactive Power Delivered | Inverter | Inverter006_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 924 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power | 925 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Reactive Power | Inverter | Inverter006_MODBUS.HR1009_q3_kvar | Reactive Power | 926 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Reactive Power Mode | Inverter | Inverter006_MODBUS.HR0552_qControlMode | Reactive Power Mode | 927 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Reactive Power Set Point Percent | Inverter | Inverter006_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 928 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power AC Percent | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power AC Percent | 929 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power-AC | Inverter | Inverter006_MODBUS.HR1008_p3_kW | Real Power-AC | 930 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power-DC | Inverter | Inverter006_MODBUS.HR1061_pdcInput_W | Real Power-DC | 931 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Air Intake | Inverter | Inverter006_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 932 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Cabinet | Inverter | Inverter006_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 933 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-IGBT | Inverter | Inverter006_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 934 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Temperature-Module | Inverter | Inverter006_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 935 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage A-B | Inverter | Inverter006_MODBUS.HR1006_vRS_V | Voltage A-B | 936 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage B-C | Inverter | Inverter006_MODBUS.HR1002_vST_V | Voltage B-C | 937 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage C-A | Inverter | Inverter006_MODBUS.HR1003_vTR_V | Voltage C-A | 938 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Voltage DC | Inverter | Inverter006_MODBUS.HR1051_vdcBus_V | Voltage DC | 939 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV006 | Daggett 3_SUB1_INV006_Fault Code 1 | Inverter | Inverter006_MODBUS.HRxxxx_currentFault | Fault Code 1 | 940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Warning | Inverter | Inverter006_MODBUS.HRxxxx_currentWarning | Warning | 941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Internal Input Status | Inverter | Inverter006_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Internal Output Status | Inverter | Inverter006_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 943 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Module Fault Code | Inverter | Inverter006_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 944 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Internal Humidity | Inverter | Inverter006_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 945 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Humidity | Inverter | Inverter006_MODBUS.HRxxxx_humidity | Humidity | 946 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_Comms Fault Time | Inverter | Inverter006_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 947 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Status | Inverter | Inverter006_MODBUS.HRxxxx_M1_status | Module Status | 948 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 IR | Inverter | Inverter006_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 949 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 IS | Inverter | Inverter006_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 IT | Inverter | Inverter006_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 953 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 954 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 955 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 P | Inverter | Inverter006_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 956 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Q | Inverter | Inverter006_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 957 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 958 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 959 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 960 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M1 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 962 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Status | Inverter | Inverter006_MODBUS.HRxxxx_M2_status | Module Status | 963 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 IR | Inverter | Inverter006_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 964 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 IS | Inverter | Inverter006_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 IT | Inverter | Inverter006_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 968 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 969 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 P | Inverter | Inverter006_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 971 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Q | Inverter | Inverter006_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 972 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 973 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 974 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 975 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 976 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M2 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Status | Inverter | Inverter006_MODBUS.HRxxxx_M3_status | Module Status | 978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 IR | Inverter | Inverter006_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 979 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 IS | Inverter | Inverter006_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 980 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 IT | Inverter | Inverter006_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 983 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 984 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 985 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 P | Inverter | Inverter006_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 986 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Q | Inverter | Inverter006_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 987 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 988 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 989 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 990 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 991 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M3 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 992 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Status | Inverter | Inverter006_MODBUS.HRxxxx_M4_status | Module Status | 993 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 IR | Inverter | Inverter006_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 994 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 IS | Inverter | Inverter006_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 995 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 IT | Inverter | Inverter006_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 998 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 999 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1000 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 P | Inverter | Inverter006_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1001 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Q | Inverter | Inverter006_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1002 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1003 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1004 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1005 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1006 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M4 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1007 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Status | Inverter | Inverter006_MODBUS.HRxxxx_M5_status | Module Status | 1008 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 IR | Inverter | Inverter006_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1009 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 IS | Inverter | Inverter006_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1010 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 IT | Inverter | Inverter006_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1011 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1013 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1014 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1015 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 P | Inverter | Inverter006_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1016 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Q | Inverter | Inverter006_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1017 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1018 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1019 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1020 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1021 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M5 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1022 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Status | Inverter | Inverter006_MODBUS.HRxxxx_M6_status | Module Status | 1023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 IR | Inverter | Inverter006_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1024 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 IS | Inverter | Inverter006_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1025 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 IT | Inverter | Inverter006_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 IDC | Inverter | Inverter006_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 VDCP | Inverter | Inverter006_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1028 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 VDCN | Inverter | Inverter006_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1029 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 VDC | Inverter | Inverter006_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 P | Inverter | Inverter006_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1031 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Q | Inverter | Inverter006_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1032 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Ambient Temp | Inverter | Inverter006_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1033 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Max IGBT Temp | Inverter | Inverter006_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1034 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 IO Status | Inverter | Inverter006_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1035 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Hardware Version | Inverter | Inverter006_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV006 | Daggett 3_SUB1_INV006_M6 Software Version | Inverter | Inverter006_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_A Phase Current | Inverter | Inverter007_MODBUS.HR1004_i1_A | A Phase Current | 1038 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_B Phase Current | Inverter | Inverter007_MODBUS.HR1005_i2_A | B Phase Current | 1039 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_C Phase Current | Inverter | Inverter007_MODBUS.HR1006_i3_A | C Phase Current | 1040 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Bus Voltage | Inverter | Inverter007_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1041 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV007 | Daggett 3_SUB1_INV007_Apparent Power | Inverter | Inverter007_MODBUS.HR1010_s3_VA | Apparent Power | 1042 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 1 | Inverter | Inverter007_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC Input 1 | Inverter | Inverter007_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1044 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 2 | Inverter | Inverter007_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1045 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 2 | Inverter | Inverter007_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1046 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 3 | Inverter | Inverter007_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1047 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 3 | Inverter | Inverter007_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1048 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 4 | Inverter | Inverter007_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 4 | Inverter | Inverter007_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1050 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 5 | Inverter | Inverter007_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1051 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 5 | Inverter | Inverter007_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1052 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 6 | Inverter | Inverter007_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1053 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 6 | Inverter | Inverter007_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1054 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 7 | Inverter | Inverter007_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1055 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 7 | Inverter | Inverter007_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1056 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 8 | Inverter | Inverter007_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 8 | Inverter | Inverter007_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1058 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 9 | Inverter | Inverter007_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1059 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 9 | Inverter | Inverter007_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1060 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 10 | Inverter | Inverter007_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1061 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 10 | Inverter | Inverter007_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1062 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 11 | Inverter | Inverter007_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 11 | Inverter | Inverter007_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1064 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 12 | Inverter | Inverter007_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 12 | Inverter | Inverter007_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1066 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 13 | Inverter | Inverter007_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1067 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 13 | Inverter | Inverter007_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1068 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 14 | Inverter | Inverter007_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1069 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 14 | Inverter | Inverter007_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1070 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 15 | Inverter | Inverter007_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1071 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 15 | Inverter | Inverter007_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1072 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 16 | Inverter | Inverter007_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 16 | Inverter | Inverter007_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1074 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 17 | Inverter | Inverter007_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1075 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 17 | Inverter | Inverter007_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1076 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 18 | Inverter | Inverter007_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1077 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 18 | Inverter | Inverter007_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1078 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 19 | Inverter | Inverter007_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 19 | Inverter | Inverter007_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1080 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current DC Input 20 | Inverter | Inverter007_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC input 20 | Inverter | Inverter007_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1082 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current-AC | Inverter | Inverter007_MODBUS.HR1007_i3Avg_A | Current-AC | 1083 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Current-DC | Inverter | Inverter007_MODBUS.HR1062_idcInput_A | Current-DC | 1084 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Daily Energy Delivered | Inverter | Inverter007_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1085 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power Set Point | Inverter | Inverter007_MODBUS.HR0553_pRef | Real Power Set Point | 1086 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Reactive Power Set Point | Inverter | Inverter007_MODBUS.HR0558_qRef | Reactive Power Set Point | 1087 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Frequency | Inverter | Inverter007_MODBUS.HR1012_f3_Hz | Frequency | 1088 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV007 | Daggett 3_SUB1_INV007_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Insulation Resistance | Inverter | Inverter007_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1089 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Number of DU Channels | Inverter | Inverter007_MODBUS.HR0653_duChannels | Number of DU Channels | 1090 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Number of Running Modules | Inverter | Inverter007_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1091 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Operating State | Inverter | Inverter007_MODBUS.HR1123_currentStatus | Operating State | 1092 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Power Factor | Inverter | Inverter007_MODBUS.HR1011_pf3 | Power Factor | 1093 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV007 | Daggett 3_SUB1_INV007_Ramp Down | Inverter | Inverter007_MODBUS.HR0286_dropGradient_p | Ramp Down | 1094 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Ramp Up | Inverter | Inverter007_MODBUS.HR0282_riseGradient_p | Ramp Up | 1095 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power Delivered | Inverter | Inverter007_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1096 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Reactive Power Delivered | Inverter | Inverter007_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1097 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power | 1098 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Reactive Power | Inverter | Inverter007_MODBUS.HR1009_q3_kvar | Reactive Power | 1099 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Reactive Power Mode | Inverter | Inverter007_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1100 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Reactive Power Set Point Percent | Inverter | Inverter007_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1101 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power AC Percent | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1102 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power-AC | Inverter | Inverter007_MODBUS.HR1008_p3_kW | Real Power-AC | 1103 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power-DC | Inverter | Inverter007_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1104 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Air Intake | Inverter | Inverter007_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1105 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Cabinet | Inverter | Inverter007_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1106 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-IGBT | Inverter | Inverter007_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1107 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Temperature-Module | Inverter | Inverter007_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1108 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage A-B | Inverter | Inverter007_MODBUS.HR1007_vRS_V | Voltage A-B | 1109 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage B-C | Inverter | Inverter007_MODBUS.HR1002_vST_V | Voltage B-C | 1110 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage C-A | Inverter | Inverter007_MODBUS.HR1003_vTR_V | Voltage C-A | 1111 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Voltage DC | Inverter | Inverter007_MODBUS.HR1051_vdcBus_V | Voltage DC | 1112 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV007 | Daggett 3_SUB1_INV007_Fault Code 1 | Inverter | Inverter007_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Warning | Inverter | Inverter007_MODBUS.HRxxxx_currentWarning | Warning | 1114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Internal Input Status | Inverter | Inverter007_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Internal Output Status | Inverter | Inverter007_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1116 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Module Fault Code | Inverter | Inverter007_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1117 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Internal Humidity | Inverter | Inverter007_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1118 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Humidity | Inverter | Inverter007_MODBUS.HRxxxx_humidity | Humidity | 1119 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_Comms Fault Time | Inverter | Inverter007_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1120 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Status | Inverter | Inverter007_MODBUS.HRxxxx_M1_status | Module Status | 1121 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 IR | Inverter | Inverter007_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1122 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 IS | Inverter | Inverter007_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 IT | Inverter | Inverter007_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1126 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1127 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1128 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 P | Inverter | Inverter007_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1129 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Q | Inverter | Inverter007_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1130 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1131 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1132 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1133 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M1 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1135 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Status | Inverter | Inverter007_MODBUS.HRxxxx_M2_status | Module Status | 1136 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 IR | Inverter | Inverter007_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1137 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 IS | Inverter | Inverter007_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1138 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 IT | Inverter | Inverter007_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1141 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1142 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 P | Inverter | Inverter007_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1144 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Q | Inverter | Inverter007_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1145 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1146 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1147 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1148 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1149 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M2 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Status | Inverter | Inverter007_MODBUS.HRxxxx_M3_status | Module Status | 1151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 IR | Inverter | Inverter007_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1152 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 IS | Inverter | Inverter007_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1153 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 IT | Inverter | Inverter007_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1154 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1156 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1157 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1158 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 P | Inverter | Inverter007_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1159 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Q | Inverter | Inverter007_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1160 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1161 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1162 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1163 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1164 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M3 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1165 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Status | Inverter | Inverter007_MODBUS.HRxxxx_M4_status | Module Status | 1166 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 IR | Inverter | Inverter007_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1167 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 IS | Inverter | Inverter007_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1168 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 IT | Inverter | Inverter007_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1170 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1171 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1172 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1173 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 P | Inverter | Inverter007_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1174 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Q | Inverter | Inverter007_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1175 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1176 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1177 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1178 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1179 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M4 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1180 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Status | Inverter | Inverter007_MODBUS.HRxxxx_M5_status | Module Status | 1181 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 IR | Inverter | Inverter007_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1182 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 IS | Inverter | Inverter007_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1183 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 IT | Inverter | Inverter007_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1186 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1187 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1188 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 P | Inverter | Inverter007_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1189 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Q | Inverter | Inverter007_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1190 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1191 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1192 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1193 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1194 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M5 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1195 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Status | Inverter | Inverter007_MODBUS.HRxxxx_M6_status | Module Status | 1196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 IR | Inverter | Inverter007_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1197 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 IS | Inverter | Inverter007_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 IT | Inverter | Inverter007_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 IDC | Inverter | Inverter007_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 VDCP | Inverter | Inverter007_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1201 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 VDCN | Inverter | Inverter007_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1202 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 VDC | Inverter | Inverter007_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 P | Inverter | Inverter007_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1204 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Q | Inverter | Inverter007_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1205 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Ambient Temp | Inverter | Inverter007_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1206 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Max IGBT Temp | Inverter | Inverter007_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1207 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 IO Status | Inverter | Inverter007_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1208 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Hardware Version | Inverter | Inverter007_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1209 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV007 | Daggett 3_SUB1_INV007_M6 Software Version | Inverter | Inverter007_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_A Phase Current | Inverter | Inverter008_MODBUS.HR1004_i1_A | A Phase Current | 1211 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_B Phase Current | Inverter | Inverter008_MODBUS.HR1005_i2_A | B Phase Current | 1212 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_C Phase Current | Inverter | Inverter008_MODBUS.HR1006_i3_A | C Phase Current | 1213 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Bus Voltage | Inverter | Inverter008_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1214 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV008 | Daggett 3_SUB1_INV008_Apparent Power | Inverter | Inverter008_MODBUS.HR1010_s3_VA | Apparent Power | 1215 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 1 | Inverter | Inverter008_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC Input 1 | Inverter | Inverter008_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1217 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 2 | Inverter | Inverter008_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1218 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 2 | Inverter | Inverter008_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1219 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 3 | Inverter | Inverter008_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1220 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 3 | Inverter | Inverter008_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1221 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 4 | Inverter | Inverter008_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 4 | Inverter | Inverter008_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1223 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 5 | Inverter | Inverter008_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1224 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 5 | Inverter | Inverter008_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1225 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 6 | Inverter | Inverter008_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1226 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 6 | Inverter | Inverter008_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1227 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 7 | Inverter | Inverter008_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1228 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 7 | Inverter | Inverter008_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1229 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 8 | Inverter | Inverter008_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1230 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 8 | Inverter | Inverter008_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1231 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 9 | Inverter | Inverter008_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1232 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 9 | Inverter | Inverter008_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1233 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 10 | Inverter | Inverter008_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1234 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 10 | Inverter | Inverter008_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1235 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 11 | Inverter | Inverter008_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 11 | Inverter | Inverter008_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1237 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 12 | Inverter | Inverter008_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 12 | Inverter | Inverter008_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1239 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 13 | Inverter | Inverter008_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1240 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 13 | Inverter | Inverter008_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1241 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 14 | Inverter | Inverter008_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1242 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 14 | Inverter | Inverter008_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1243 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 15 | Inverter | Inverter008_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1244 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 15 | Inverter | Inverter008_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1245 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 16 | Inverter | Inverter008_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1246 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 16 | Inverter | Inverter008_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1247 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 17 | Inverter | Inverter008_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1248 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 17 | Inverter | Inverter008_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1249 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 18 | Inverter | Inverter008_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1250 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 18 | Inverter | Inverter008_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1251 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 19 | Inverter | Inverter008_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 19 | Inverter | Inverter008_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1253 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current DC Input 20 | Inverter | Inverter008_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC input 20 | Inverter | Inverter008_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1255 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current-AC | Inverter | Inverter008_MODBUS.HR1007_i3Avg_A | Current-AC | 1256 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Current-DC | Inverter | Inverter008_MODBUS.HR1062_idcInput_A | Current-DC | 1257 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Daily Energy Delivered | Inverter | Inverter008_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1258 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power Set Point | Inverter | Inverter008_MODBUS.HR0553_pRef | Real Power Set Point | 1259 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Reactive Power Set Point | Inverter | Inverter008_MODBUS.HR0558_qRef | Reactive Power Set Point | 1260 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Frequency | Inverter | Inverter008_MODBUS.HR1012_f3_Hz | Frequency | 1261 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV008 | Daggett 3_SUB1_INV008_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Insulation Resistance | Inverter | Inverter008_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1262 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Number of DU Channels | Inverter | Inverter008_MODBUS.HR0653_duChannels | Number of DU Channels | 1263 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Number of Running Modules | Inverter | Inverter008_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1264 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Operating State | Inverter | Inverter008_MODBUS.HR1123_currentStatus | Operating State | 1265 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Power Factor | Inverter | Inverter008_MODBUS.HR1011_pf3 | Power Factor | 1266 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV008 | Daggett 3_SUB1_INV008_Ramp Down | Inverter | Inverter008_MODBUS.HR0286_dropGradient_p | Ramp Down | 1267 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Ramp Up | Inverter | Inverter008_MODBUS.HR0282_riseGradient_p | Ramp Up | 1268 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power Delivered | Inverter | Inverter008_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1269 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Reactive Power Delivered | Inverter | Inverter008_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1270 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power | 1271 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Reactive Power | Inverter | Inverter008_MODBUS.HR1009_q3_kvar | Reactive Power | 1272 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Reactive Power Mode | Inverter | Inverter008_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1273 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Reactive Power Set Point Percent | Inverter | Inverter008_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1274 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power AC Percent | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1275 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power-AC | Inverter | Inverter008_MODBUS.HR1008_p3_kW | Real Power-AC | 1276 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power-DC | Inverter | Inverter008_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1277 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Air Intake | Inverter | Inverter008_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1278 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Cabinet | Inverter | Inverter008_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1279 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-IGBT | Inverter | Inverter008_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1280 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Temperature-Module | Inverter | Inverter008_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1281 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage A-B | Inverter | Inverter008_MODBUS.HR1008_vRS_V | Voltage A-B | 1282 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage B-C | Inverter | Inverter008_MODBUS.HR1002_vST_V | Voltage B-C | 1283 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage C-A | Inverter | Inverter008_MODBUS.HR1003_vTR_V | Voltage C-A | 1284 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Voltage DC | Inverter | Inverter008_MODBUS.HR1051_vdcBus_V | Voltage DC | 1285 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV008 | Daggett 3_SUB1_INV008_Fault Code 1 | Inverter | Inverter008_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Warning | Inverter | Inverter008_MODBUS.HRxxxx_currentWarning | Warning | 1287 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Internal Input Status | Inverter | Inverter008_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1288 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Internal Output Status | Inverter | Inverter008_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1289 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Module Fault Code | Inverter | Inverter008_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1290 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Internal Humidity | Inverter | Inverter008_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1291 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Humidity | Inverter | Inverter008_MODBUS.HRxxxx_humidity | Humidity | 1292 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_Comms Fault Time | Inverter | Inverter008_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1293 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Status | Inverter | Inverter008_MODBUS.HRxxxx_M1_status | Module Status | 1294 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 IR | Inverter | Inverter008_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1295 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 IS | Inverter | Inverter008_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 IT | Inverter | Inverter008_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1299 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1300 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1301 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 P | Inverter | Inverter008_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1302 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Q | Inverter | Inverter008_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1303 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1304 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1305 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1306 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M1 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1308 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Status | Inverter | Inverter008_MODBUS.HRxxxx_M2_status | Module Status | 1309 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 IR | Inverter | Inverter008_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1310 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 IS | Inverter | Inverter008_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1311 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 IT | Inverter | Inverter008_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1314 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1315 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 P | Inverter | Inverter008_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1317 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Q | Inverter | Inverter008_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1318 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1319 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1320 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1321 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1322 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M2 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Status | Inverter | Inverter008_MODBUS.HRxxxx_M3_status | Module Status | 1324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 IR | Inverter | Inverter008_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1325 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 IS | Inverter | Inverter008_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1326 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 IT | Inverter | Inverter008_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1327 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1329 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1330 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1331 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 P | Inverter | Inverter008_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1332 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Q | Inverter | Inverter008_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1333 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1334 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1335 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1336 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1337 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M3 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1338 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Status | Inverter | Inverter008_MODBUS.HRxxxx_M4_status | Module Status | 1339 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 IR | Inverter | Inverter008_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1340 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 IS | Inverter | Inverter008_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1341 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 IT | Inverter | Inverter008_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1343 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1344 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1345 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1346 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 P | Inverter | Inverter008_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1347 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Q | Inverter | Inverter008_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1348 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1349 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1350 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1351 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1352 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M4 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1353 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Status | Inverter | Inverter008_MODBUS.HRxxxx_M5_status | Module Status | 1354 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 IR | Inverter | Inverter008_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1355 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 IS | Inverter | Inverter008_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1356 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 IT | Inverter | Inverter008_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1359 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1360 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1361 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 P | Inverter | Inverter008_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1362 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Q | Inverter | Inverter008_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1363 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1364 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1365 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1366 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1367 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M5 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1368 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Status | Inverter | Inverter008_MODBUS.HRxxxx_M6_status | Module Status | 1369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 IR | Inverter | Inverter008_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1370 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 IS | Inverter | Inverter008_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 IT | Inverter | Inverter008_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 IDC | Inverter | Inverter008_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 VDCP | Inverter | Inverter008_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1374 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 VDCN | Inverter | Inverter008_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1375 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 VDC | Inverter | Inverter008_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 P | Inverter | Inverter008_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1377 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Q | Inverter | Inverter008_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1378 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Ambient Temp | Inverter | Inverter008_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1379 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Max IGBT Temp | Inverter | Inverter008_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1380 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 IO Status | Inverter | Inverter008_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1381 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Hardware Version | Inverter | Inverter008_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1382 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV008 | Daggett 3_SUB1_INV008_M6 Software Version | Inverter | Inverter008_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_A Phase Current | Inverter | Inverter009_MODBUS.HR1004_i1_A | A Phase Current | 1384 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_B Phase Current | Inverter | Inverter009_MODBUS.HR1005_i2_A | B Phase Current | 1385 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_C Phase Current | Inverter | Inverter009_MODBUS.HR1006_i3_A | C Phase Current | 1386 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Bus Voltage | Inverter | Inverter009_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1387 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV009 | Daggett 3_SUB1_INV009_Apparent Power | Inverter | Inverter009_MODBUS.HR1010_s3_VA | Apparent Power | 1388 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 1 | Inverter | Inverter009_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC Input 1 | Inverter | Inverter009_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1390 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 2 | Inverter | Inverter009_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1391 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 2 | Inverter | Inverter009_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1392 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 3 | Inverter | Inverter009_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1393 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 3 | Inverter | Inverter009_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1394 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 4 | Inverter | Inverter009_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 4 | Inverter | Inverter009_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1396 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 5 | Inverter | Inverter009_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1397 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 5 | Inverter | Inverter009_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1398 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 6 | Inverter | Inverter009_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1399 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 6 | Inverter | Inverter009_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1400 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 7 | Inverter | Inverter009_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1401 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 7 | Inverter | Inverter009_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1402 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 8 | Inverter | Inverter009_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1403 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 8 | Inverter | Inverter009_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1404 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 9 | Inverter | Inverter009_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1405 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 9 | Inverter | Inverter009_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1406 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 10 | Inverter | Inverter009_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1407 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 10 | Inverter | Inverter009_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1408 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 11 | Inverter | Inverter009_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 11 | Inverter | Inverter009_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1410 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 12 | Inverter | Inverter009_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 12 | Inverter | Inverter009_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1412 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 13 | Inverter | Inverter009_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1413 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 13 | Inverter | Inverter009_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1414 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 14 | Inverter | Inverter009_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1415 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 14 | Inverter | Inverter009_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1416 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 15 | Inverter | Inverter009_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1417 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 15 | Inverter | Inverter009_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1418 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 16 | Inverter | Inverter009_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1419 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 16 | Inverter | Inverter009_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1420 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 17 | Inverter | Inverter009_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1421 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 17 | Inverter | Inverter009_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1422 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 18 | Inverter | Inverter009_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1423 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 18 | Inverter | Inverter009_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1424 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 19 | Inverter | Inverter009_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 19 | Inverter | Inverter009_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1426 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current DC Input 20 | Inverter | Inverter009_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC input 20 | Inverter | Inverter009_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1428 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current-AC | Inverter | Inverter009_MODBUS.HR1007_i3Avg_A | Current-AC | 1429 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Current-DC | Inverter | Inverter009_MODBUS.HR1062_idcInput_A | Current-DC | 1430 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Daily Energy Delivered | Inverter | Inverter009_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1431 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power Set Point | Inverter | Inverter009_MODBUS.HR0553_pRef | Real Power Set Point | 1432 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Reactive Power Set Point | Inverter | Inverter009_MODBUS.HR0558_qRef | Reactive Power Set Point | 1433 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Frequency | Inverter | Inverter009_MODBUS.HR1012_f3_Hz | Frequency | 1434 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV009 | Daggett 3_SUB1_INV009_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Insulation Resistance | Inverter | Inverter009_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1435 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Number of DU Channels | Inverter | Inverter009_MODBUS.HR0653_duChannels | Number of DU Channels | 1436 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Number of Running Modules | Inverter | Inverter009_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1437 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Operating State | Inverter | Inverter009_MODBUS.HR1123_currentStatus | Operating State | 1438 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Power Factor | Inverter | Inverter009_MODBUS.HR1011_pf3 | Power Factor | 1439 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV009 | Daggett 3_SUB1_INV009_Ramp Down | Inverter | Inverter009_MODBUS.HR0286_dropGradient_p | Ramp Down | 1440 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Ramp Up | Inverter | Inverter009_MODBUS.HR0282_riseGradient_p | Ramp Up | 1441 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power Delivered | Inverter | Inverter009_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1442 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Reactive Power Delivered | Inverter | Inverter009_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1443 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power | 1444 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Reactive Power | Inverter | Inverter009_MODBUS.HR1009_q3_kvar | Reactive Power | 1445 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Reactive Power Mode | Inverter | Inverter009_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1446 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Reactive Power Set Point Percent | Inverter | Inverter009_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1447 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power AC Percent | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1448 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power-AC | Inverter | Inverter009_MODBUS.HR1008_p3_kW | Real Power-AC | 1449 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power-DC | Inverter | Inverter009_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1450 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Air Intake | Inverter | Inverter009_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1451 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Cabinet | Inverter | Inverter009_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1452 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-IGBT | Inverter | Inverter009_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1453 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Temperature-Module | Inverter | Inverter009_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1454 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage A-B | Inverter | Inverter009_MODBUS.HR1009_vRS_V | Voltage A-B | 1455 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage B-C | Inverter | Inverter009_MODBUS.HR1002_vST_V | Voltage B-C | 1456 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage C-A | Inverter | Inverter009_MODBUS.HR1003_vTR_V | Voltage C-A | 1457 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Voltage DC | Inverter | Inverter009_MODBUS.HR1051_vdcBus_V | Voltage DC | 1458 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV009 | Daggett 3_SUB1_INV009_Fault Code 1 | Inverter | Inverter009_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Warning | Inverter | Inverter009_MODBUS.HRxxxx_currentWarning | Warning | 1460 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Internal Input Status | Inverter | Inverter009_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1461 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Internal Output Status | Inverter | Inverter009_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1462 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Module Fault Code | Inverter | Inverter009_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1463 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Internal Humidity | Inverter | Inverter009_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1464 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Humidity | Inverter | Inverter009_MODBUS.HRxxxx_humidity | Humidity | 1465 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_Comms Fault Time | Inverter | Inverter009_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1466 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Status | Inverter | Inverter009_MODBUS.HRxxxx_M1_status | Module Status | 1467 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 IR | Inverter | Inverter009_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1468 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 IS | Inverter | Inverter009_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 IT | Inverter | Inverter009_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1472 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1473 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1474 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 P | Inverter | Inverter009_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1475 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Q | Inverter | Inverter009_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1476 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1477 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1478 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1479 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M1 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1481 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Status | Inverter | Inverter009_MODBUS.HRxxxx_M2_status | Module Status | 1482 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 IR | Inverter | Inverter009_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1483 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 IS | Inverter | Inverter009_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1484 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 IT | Inverter | Inverter009_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1487 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1488 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 P | Inverter | Inverter009_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1490 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Q | Inverter | Inverter009_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1491 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1492 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1493 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1494 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1495 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M2 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Status | Inverter | Inverter009_MODBUS.HRxxxx_M3_status | Module Status | 1497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 IR | Inverter | Inverter009_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1498 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 IS | Inverter | Inverter009_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1499 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 IT | Inverter | Inverter009_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1500 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1502 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1503 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1504 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 P | Inverter | Inverter009_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1505 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Q | Inverter | Inverter009_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1506 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1507 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1508 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1509 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1510 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M3 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1511 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Status | Inverter | Inverter009_MODBUS.HRxxxx_M4_status | Module Status | 1512 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 IR | Inverter | Inverter009_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1513 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 IS | Inverter | Inverter009_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1514 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 IT | Inverter | Inverter009_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1516 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1517 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1518 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1519 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 P | Inverter | Inverter009_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1520 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Q | Inverter | Inverter009_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1521 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1522 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1523 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1524 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1525 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M4 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1526 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Status | Inverter | Inverter009_MODBUS.HRxxxx_M5_status | Module Status | 1527 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 IR | Inverter | Inverter009_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1528 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 IS | Inverter | Inverter009_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1529 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 IT | Inverter | Inverter009_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1532 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1533 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1534 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 P | Inverter | Inverter009_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1535 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Q | Inverter | Inverter009_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1536 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1537 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1538 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1539 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1540 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M5 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1541 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Status | Inverter | Inverter009_MODBUS.HRxxxx_M6_status | Module Status | 1542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 IR | Inverter | Inverter009_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1543 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 IS | Inverter | Inverter009_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 IT | Inverter | Inverter009_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 IDC | Inverter | Inverter009_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 VDCP | Inverter | Inverter009_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1547 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 VDCN | Inverter | Inverter009_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1548 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 VDC | Inverter | Inverter009_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 P | Inverter | Inverter009_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1550 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Q | Inverter | Inverter009_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1551 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Ambient Temp | Inverter | Inverter009_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1552 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Max IGBT Temp | Inverter | Inverter009_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1553 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 IO Status | Inverter | Inverter009_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1554 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Hardware Version | Inverter | Inverter009_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1555 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV009 | Daggett 3_SUB1_INV009_M6 Software Version | Inverter | Inverter009_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_A Phase Current | Inverter | Inverter010_MODBUS.HR1004_i1_A | A Phase Current | 1557 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_B Phase Current | Inverter | Inverter010_MODBUS.HR1005_i2_A | B Phase Current | 1558 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_C Phase Current | Inverter | Inverter010_MODBUS.HR1006_i3_A | C Phase Current | 1559 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Bus Voltage | Inverter | Inverter010_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1560 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV010 | Daggett 3_SUB1_INV010_Apparent Power | Inverter | Inverter010_MODBUS.HR1010_s3_VA | Apparent Power | 1561 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 1 | Inverter | Inverter010_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC Input 1 | Inverter | Inverter010_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1563 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 2 | Inverter | Inverter010_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1564 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 2 | Inverter | Inverter010_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1565 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 3 | Inverter | Inverter010_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1566 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 3 | Inverter | Inverter010_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1567 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 4 | Inverter | Inverter010_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 4 | Inverter | Inverter010_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1569 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 5 | Inverter | Inverter010_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1570 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 5 | Inverter | Inverter010_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1571 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 6 | Inverter | Inverter010_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1572 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 6 | Inverter | Inverter010_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1573 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 7 | Inverter | Inverter010_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1574 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 7 | Inverter | Inverter010_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1575 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 8 | Inverter | Inverter010_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1576 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 8 | Inverter | Inverter010_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1577 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 9 | Inverter | Inverter010_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1578 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 9 | Inverter | Inverter010_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1579 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 10 | Inverter | Inverter010_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1580 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 10 | Inverter | Inverter010_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1581 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 11 | Inverter | Inverter010_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 11 | Inverter | Inverter010_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1583 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 12 | Inverter | Inverter010_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 12 | Inverter | Inverter010_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1585 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 13 | Inverter | Inverter010_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1586 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 13 | Inverter | Inverter010_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1587 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 14 | Inverter | Inverter010_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1588 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 14 | Inverter | Inverter010_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1589 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 15 | Inverter | Inverter010_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1590 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 15 | Inverter | Inverter010_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1591 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 16 | Inverter | Inverter010_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1592 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 16 | Inverter | Inverter010_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1593 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 17 | Inverter | Inverter010_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1594 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 17 | Inverter | Inverter010_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1595 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 18 | Inverter | Inverter010_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1596 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 18 | Inverter | Inverter010_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1597 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 19 | Inverter | Inverter010_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 19 | Inverter | Inverter010_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1599 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current DC Input 20 | Inverter | Inverter010_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC input 20 | Inverter | Inverter010_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1601 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current-AC | Inverter | Inverter010_MODBUS.HR1007_i3Avg_A | Current-AC | 1602 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Current-DC | Inverter | Inverter010_MODBUS.HR1062_idcInput_A | Current-DC | 1603 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Daily Energy Delivered | Inverter | Inverter010_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1604 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power Set Point | Inverter | Inverter010_MODBUS.HR0553_pRef | Real Power Set Point | 1605 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Reactive Power Set Point | Inverter | Inverter010_MODBUS.HR0558_qRef | Reactive Power Set Point | 1606 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Frequency | Inverter | Inverter010_MODBUS.HR1012_f3_Hz | Frequency | 1607 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV010 | Daggett 3_SUB1_INV010_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Insulation Resistance | Inverter | Inverter010_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1608 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Number of DU Channels | Inverter | Inverter010_MODBUS.HR0653_duChannels | Number of DU Channels | 1609 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Number of Running Modules | Inverter | Inverter010_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1610 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Operating State | Inverter | Inverter010_MODBUS.HR1123_currentStatus | Operating State | 1611 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Power Factor | Inverter | Inverter010_MODBUS.HR1011_pf3 | Power Factor | 1612 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV010 | Daggett 3_SUB1_INV010_Ramp Down | Inverter | Inverter010_MODBUS.HR0286_dropGradient_p | Ramp Down | 1613 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Ramp Up | Inverter | Inverter010_MODBUS.HR0282_riseGradient_p | Ramp Up | 1614 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power Delivered | Inverter | Inverter010_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1615 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Reactive Power Delivered | Inverter | Inverter010_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1616 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power | 1617 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Reactive Power | Inverter | Inverter010_MODBUS.HR1009_q3_kvar | Reactive Power | 1618 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Reactive Power Mode | Inverter | Inverter010_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1619 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Reactive Power Set Point Percent | Inverter | Inverter010_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1620 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power AC Percent | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1621 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power-AC | Inverter | Inverter010_MODBUS.HR1008_p3_kW | Real Power-AC | 1622 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power-DC | Inverter | Inverter010_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1623 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Air Intake | Inverter | Inverter010_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1624 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Cabinet | Inverter | Inverter010_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1625 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-IGBT | Inverter | Inverter010_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1626 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Temperature-Module | Inverter | Inverter010_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1627 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage A-B | Inverter | Inverter010_MODBUS.HR1010_vRS_V | Voltage A-B | 1628 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage B-C | Inverter | Inverter010_MODBUS.HR1002_vST_V | Voltage B-C | 1629 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage C-A | Inverter | Inverter010_MODBUS.HR1003_vTR_V | Voltage C-A | 1630 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Voltage DC | Inverter | Inverter010_MODBUS.HR1051_vdcBus_V | Voltage DC | 1631 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV010 | Daggett 3_SUB1_INV010_Fault Code 1 | Inverter | Inverter010_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Warning | Inverter | Inverter010_MODBUS.HRxxxx_currentWarning | Warning | 1633 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Internal Input Status | Inverter | Inverter010_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1634 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Internal Output Status | Inverter | Inverter010_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1635 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Module Fault Code | Inverter | Inverter010_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1636 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Internal Humidity | Inverter | Inverter010_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1637 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Humidity | Inverter | Inverter010_MODBUS.HRxxxx_humidity | Humidity | 1638 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_Comms Fault Time | Inverter | Inverter010_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1639 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Status | Inverter | Inverter010_MODBUS.HRxxxx_M1_status | Module Status | 1640 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 IR | Inverter | Inverter010_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1641 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 IS | Inverter | Inverter010_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 IT | Inverter | Inverter010_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1645 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1646 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1647 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 P | Inverter | Inverter010_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1648 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Q | Inverter | Inverter010_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1649 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1650 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1651 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1652 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M1 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1654 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Status | Inverter | Inverter010_MODBUS.HRxxxx_M2_status | Module Status | 1655 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 IR | Inverter | Inverter010_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1656 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 IS | Inverter | Inverter010_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1657 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 IT | Inverter | Inverter010_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1660 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1661 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 P | Inverter | Inverter010_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1663 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Q | Inverter | Inverter010_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1664 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1665 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1666 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1667 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1668 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M2 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Status | Inverter | Inverter010_MODBUS.HRxxxx_M3_status | Module Status | 1670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 IR | Inverter | Inverter010_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1671 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 IS | Inverter | Inverter010_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1672 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 IT | Inverter | Inverter010_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1673 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1675 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1676 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1677 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 P | Inverter | Inverter010_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1678 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Q | Inverter | Inverter010_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1679 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1680 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1681 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1682 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1683 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M3 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1684 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Status | Inverter | Inverter010_MODBUS.HRxxxx_M4_status | Module Status | 1685 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 IR | Inverter | Inverter010_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1686 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 IS | Inverter | Inverter010_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1687 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 IT | Inverter | Inverter010_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1689 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1690 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1691 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1692 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 P | Inverter | Inverter010_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1693 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Q | Inverter | Inverter010_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1694 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1695 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1696 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1697 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1698 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M4 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1699 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Status | Inverter | Inverter010_MODBUS.HRxxxx_M5_status | Module Status | 1700 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 IR | Inverter | Inverter010_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1701 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 IS | Inverter | Inverter010_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1702 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 IT | Inverter | Inverter010_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1705 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1706 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1707 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 P | Inverter | Inverter010_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1708 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Q | Inverter | Inverter010_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1709 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1710 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1711 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1712 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1713 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M5 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1714 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Status | Inverter | Inverter010_MODBUS.HRxxxx_M6_status | Module Status | 1715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 IR | Inverter | Inverter010_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1716 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 IS | Inverter | Inverter010_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 IT | Inverter | Inverter010_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 IDC | Inverter | Inverter010_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 VDCP | Inverter | Inverter010_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1720 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 VDCN | Inverter | Inverter010_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1721 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 VDC | Inverter | Inverter010_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 P | Inverter | Inverter010_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1723 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Q | Inverter | Inverter010_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1724 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Ambient Temp | Inverter | Inverter010_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1725 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Max IGBT Temp | Inverter | Inverter010_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1726 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 IO Status | Inverter | Inverter010_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1727 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Hardware Version | Inverter | Inverter010_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1728 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV010 | Daggett 3_SUB1_INV010_M6 Software Version | Inverter | Inverter010_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_A Phase Current | Inverter | inverter011_MODBUS.HR1004_i1_A | A Phase Current | 1730 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_B Phase Current | Inverter | inverter011_MODBUS.HR1005_i2_A | B Phase Current | 1731 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_C Phase Current | Inverter | inverter011_MODBUS.HR1006_i3_A | C Phase Current | 1732 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Bus Voltage | Inverter | inverter011_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1733 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV011 | Daggett 3_SUB1_INV011_Apparent Power | Inverter | inverter011_MODBUS.HR1010_s3_VA | Apparent Power | 1734 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 1 | Inverter | Inverter011_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC Input 1 | Inverter | Inverter011_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1736 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 2 | Inverter | Inverter011_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1737 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 2 | Inverter | Inverter011_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1738 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 3 | Inverter | Inverter011_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1739 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 3 | Inverter | Inverter011_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1740 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 4 | Inverter | Inverter011_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 4 | Inverter | Inverter011_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1742 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 5 | Inverter | Inverter011_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1743 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 5 | Inverter | Inverter011_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1744 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 6 | Inverter | Inverter011_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1745 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 6 | Inverter | Inverter011_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1746 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 7 | Inverter | Inverter011_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1747 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 7 | Inverter | Inverter011_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1748 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 8 | Inverter | Inverter011_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1749 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 8 | Inverter | Inverter011_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1750 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 9 | Inverter | Inverter011_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1751 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 9 | Inverter | Inverter011_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1752 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 10 | Inverter | Inverter011_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1753 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 10 | Inverter | Inverter011_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1754 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 11 | Inverter | Inverter011_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 11 | Inverter | Inverter011_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1756 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 12 | Inverter | Inverter011_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 12 | Inverter | Inverter011_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1758 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 13 | Inverter | Inverter011_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1759 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 13 | Inverter | Inverter011_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1760 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 14 | Inverter | Inverter011_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1761 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 14 | Inverter | Inverter011_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1762 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 15 | Inverter | Inverter011_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1763 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 15 | Inverter | Inverter011_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1764 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 16 | Inverter | Inverter011_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1765 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 16 | Inverter | Inverter011_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1766 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 17 | Inverter | Inverter011_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1767 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 17 | Inverter | Inverter011_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1768 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 18 | Inverter | Inverter011_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1769 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 18 | Inverter | Inverter011_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1770 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 19 | Inverter | Inverter011_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 19 | Inverter | Inverter011_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1772 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current DC Input 20 | Inverter | Inverter011_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC input 20 | Inverter | Inverter011_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1774 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current-AC | Inverter | inverter011_MODBUS.HR1007_i3Avg_A | Current-AC | 1775 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Current-DC | Inverter | inverter011_MODBUS.HR1062_idcInput_A | Current-DC | 1776 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Daily Energy Delivered | Inverter | inverter011_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1777 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power Set Point | Inverter | inverter011_MODBUS.HR0553_pRef | Real Power Set Point | 1778 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Reactive Power Set Point | Inverter | inverter011_MODBUS.HR0558_qRef | Reactive Power Set Point | 1779 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Frequency | Inverter | inverter011_MODBUS.HR1012_f3_Hz | Frequency | 1780 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV011 | Daggett 3_SUB1_INV011_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Insulation Resistance | Inverter | inverter011_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1781 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Number of DU Channels | Inverter | inverter011_MODBUS.HR0653_duChannels | Number of DU Channels | 1782 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Number of Running Modules | Inverter | inverter011_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1783 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Operating State | Inverter | inverter011_MODBUS.HR1123_currentStatus | Operating State | 1784 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Power Factor | Inverter | inverter011_MODBUS.HR1011_pf3 | Power Factor | 1785 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV011 | Daggett 3_SUB1_INV011_Ramp Down | Inverter | inverter011_MODBUS.HR0286_dropGradient_p | Ramp Down | 1786 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Ramp Up | Inverter | inverter011_MODBUS.HR0282_riseGradient_p | Ramp Up | 1787 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power Delivered | Inverter | inverter011_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1788 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Reactive Power Delivered | Inverter | inverter011_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1789 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power | 1790 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Reactive Power | Inverter | inverter011_MODBUS.HR1009_q3_kvar | Reactive Power | 1791 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Reactive Power Mode | Inverter | inverter011_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1792 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Reactive Power Set Point Percent | Inverter | inverter011_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1793 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power AC Percent | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1794 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power-AC | Inverter | inverter011_MODBUS.HR1008_p3_kW | Real Power-AC | 1795 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power-DC | Inverter | inverter011_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1796 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Air Intake | Inverter | inverter011_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1797 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Cabinet | Inverter | inverter011_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1798 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-IGBT | Inverter | inverter011_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1799 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Temperature-Module | Inverter | inverter011_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1800 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage A-B | Inverter | inverter011_MODBUS.HR1001_vRS_V | Voltage A-B | 1801 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage B-C | Inverter | inverter011_MODBUS.HR1002_vST_V | Voltage B-C | 1802 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage C-A | Inverter | inverter011_MODBUS.HR1003_vTR_V | Voltage C-A | 1803 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Voltage DC | Inverter | inverter011_MODBUS.HR1051_vdcBus_V | Voltage DC | 1804 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV011 | Daggett 3_SUB1_INV011_Fault Code 1 | Inverter | Inverter011_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Warning | Inverter | Inverter011_MODBUS.HRxxxx_currentWarning | Warning | 1806 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Internal Input Status | Inverter | Inverter011_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1807 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Internal Output Status | Inverter | Inverter011_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1808 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Module Fault Code | Inverter | Inverter011_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1809 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Internal Humidity | Inverter | Inverter011_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1810 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Humidity | Inverter | Inverter011_MODBUS.HRxxxx_humidity | Humidity | 1811 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_Comms Fault Time | Inverter | Inverter011_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1812 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Status | Inverter | Inverter011_MODBUS.HRxxxx_M1_status | Module Status | 1813 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 IR | Inverter | Inverter011_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1814 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 IS | Inverter | Inverter011_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 IT | Inverter | Inverter011_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1818 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1819 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1820 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 P | Inverter | Inverter011_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1821 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Q | Inverter | Inverter011_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1822 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1823 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1824 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1825 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M1 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1827 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Status | Inverter | Inverter011_MODBUS.HRxxxx_M2_status | Module Status | 1828 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 IR | Inverter | Inverter011_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1829 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 IS | Inverter | Inverter011_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1830 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 IT | Inverter | Inverter011_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1833 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1834 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 P | Inverter | Inverter011_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1836 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Q | Inverter | Inverter011_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1837 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1838 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1839 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1840 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1841 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M2 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Status | Inverter | Inverter011_MODBUS.HRxxxx_M3_status | Module Status | 1843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 IR | Inverter | Inverter011_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1844 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 IS | Inverter | Inverter011_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1845 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 IT | Inverter | Inverter011_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1846 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1848 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1849 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1850 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 P | Inverter | Inverter011_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1851 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Q | Inverter | Inverter011_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1852 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1853 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1854 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1855 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1856 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M3 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1857 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Status | Inverter | Inverter011_MODBUS.HRxxxx_M4_status | Module Status | 1858 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 IR | Inverter | Inverter011_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1859 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 IS | Inverter | Inverter011_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1860 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 IT | Inverter | Inverter011_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1862 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1863 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1864 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1865 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 P | Inverter | Inverter011_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1866 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Q | Inverter | Inverter011_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1867 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1868 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1869 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1870 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1871 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M4 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1872 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Status | Inverter | Inverter011_MODBUS.HRxxxx_M5_status | Module Status | 1873 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 IR | Inverter | Inverter011_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1874 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 IS | Inverter | Inverter011_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1875 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 IT | Inverter | Inverter011_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1878 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1879 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1880 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 P | Inverter | Inverter011_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1881 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Q | Inverter | Inverter011_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1882 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1883 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1884 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1885 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1886 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M5 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1887 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Status | Inverter | Inverter011_MODBUS.HRxxxx_M6_status | Module Status | 1888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 IR | Inverter | Inverter011_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1889 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 IS | Inverter | Inverter011_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 IT | Inverter | Inverter011_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 IDC | Inverter | Inverter011_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 VDCP | Inverter | Inverter011_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1893 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 VDCN | Inverter | Inverter011_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1894 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 VDC | Inverter | Inverter011_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 P | Inverter | Inverter011_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1896 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Q | Inverter | Inverter011_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1897 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Ambient Temp | Inverter | Inverter011_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1898 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Max IGBT Temp | Inverter | Inverter011_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1899 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 IO Status | Inverter | Inverter011_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1900 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Hardware Version | Inverter | Inverter011_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1901 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV011 | Daggett 3_SUB1_INV011_M6 Software Version | Inverter | Inverter011_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_A Phase Current | Inverter | inverter012_MODBUS.HR1004_i1_A | A Phase Current | 1903 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_B Phase Current | Inverter | inverter012_MODBUS.HR1005_i2_A | B Phase Current | 1904 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_C Phase Current | Inverter | inverter012_MODBUS.HR1006_i3_A | C Phase Current | 1905 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Bus Voltage | Inverter | inverter012_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1906 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV012 | Daggett 3_SUB1_INV012_Apparent Power | Inverter | inverter012_MODBUS.HR1010_s3_VA | Apparent Power | 1907 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 1 | Inverter | Inverter012_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC Input 1 | Inverter | Inverter012_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1909 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 2 | Inverter | Inverter012_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1910 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 2 | Inverter | Inverter012_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1911 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 3 | Inverter | Inverter012_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1912 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 3 | Inverter | Inverter012_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1913 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 4 | Inverter | Inverter012_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 4 | Inverter | Inverter012_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1915 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 5 | Inverter | Inverter012_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1916 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 5 | Inverter | Inverter012_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1917 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 6 | Inverter | Inverter012_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1918 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 6 | Inverter | Inverter012_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1919 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 7 | Inverter | Inverter012_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1920 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 7 | Inverter | Inverter012_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1921 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 8 | Inverter | Inverter012_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1922 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 8 | Inverter | Inverter012_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1923 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 9 | Inverter | Inverter012_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1924 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 9 | Inverter | Inverter012_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1925 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 10 | Inverter | Inverter012_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1926 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 10 | Inverter | Inverter012_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1927 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 11 | Inverter | Inverter012_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 11 | Inverter | Inverter012_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1929 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 12 | Inverter | Inverter012_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 12 | Inverter | Inverter012_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1931 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 13 | Inverter | Inverter012_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1932 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 13 | Inverter | Inverter012_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1933 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 14 | Inverter | Inverter012_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1934 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 14 | Inverter | Inverter012_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1935 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 15 | Inverter | Inverter012_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1936 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 15 | Inverter | Inverter012_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1937 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 16 | Inverter | Inverter012_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1938 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 16 | Inverter | Inverter012_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1939 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 17 | Inverter | Inverter012_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1940 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 17 | Inverter | Inverter012_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1941 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 18 | Inverter | Inverter012_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1942 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 18 | Inverter | Inverter012_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1943 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 19 | Inverter | Inverter012_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 19 | Inverter | Inverter012_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1945 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current DC Input 20 | Inverter | Inverter012_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC input 20 | Inverter | Inverter012_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1947 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current-AC | Inverter | inverter012_MODBUS.HR1007_i3Avg_A | Current-AC | 1948 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Current-DC | Inverter | inverter012_MODBUS.HR1062_idcInput_A | Current-DC | 1949 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Daily Energy Delivered | Inverter | inverter012_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1950 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power Set Point | Inverter | inverter012_MODBUS.HR0553_pRef | Real Power Set Point | 1951 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Reactive Power Set Point | Inverter | inverter012_MODBUS.HR0558_qRef | Reactive Power Set Point | 1952 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Frequency | Inverter | inverter012_MODBUS.HR1012_f3_Hz | Frequency | 1953 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV012 | Daggett 3_SUB1_INV012_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Insulation Resistance | Inverter | inverter012_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1954 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Number of DU Channels | Inverter | inverter012_MODBUS.HR0653_duChannels | Number of DU Channels | 1955 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Number of Running Modules | Inverter | inverter012_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1956 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Operating State | Inverter | inverter012_MODBUS.HR1123_currentStatus | Operating State | 1957 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Power Factor | Inverter | inverter012_MODBUS.HR1011_pf3 | Power Factor | 1958 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV012 | Daggett 3_SUB1_INV012_Ramp Down | Inverter | inverter012_MODBUS.HR0286_dropGradient_p | Ramp Down | 1959 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Ramp Up | Inverter | inverter012_MODBUS.HR0282_riseGradient_p | Ramp Up | 1960 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power Delivered | Inverter | inverter012_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1961 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Reactive Power Delivered | Inverter | inverter012_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1962 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power | 1963 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Reactive Power | Inverter | inverter012_MODBUS.HR1009_q3_kvar | Reactive Power | 1964 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Reactive Power Mode | Inverter | inverter012_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1965 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Reactive Power Set Point Percent | Inverter | inverter012_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1966 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power AC Percent | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1967 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power-AC | Inverter | inverter012_MODBUS.HR1008_p3_kW | Real Power-AC | 1968 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power-DC | Inverter | inverter012_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1969 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Air Intake | Inverter | inverter012_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1970 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Cabinet | Inverter | inverter012_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1971 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-IGBT | Inverter | inverter012_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1972 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Temperature-Module | Inverter | inverter012_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1973 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage A-B | Inverter | inverter012_MODBUS.HR1002_vRS_V | Voltage A-B | 1974 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage B-C | Inverter | inverter012_MODBUS.HR1002_vST_V | Voltage B-C | 1975 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage C-A | Inverter | inverter012_MODBUS.HR1003_vTR_V | Voltage C-A | 1976 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Voltage DC | Inverter | inverter012_MODBUS.HR1051_vdcBus_V | Voltage DC | 1977 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV012 | Daggett 3_SUB1_INV012_Fault Code 1 | Inverter | Inverter012_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Warning | Inverter | Inverter012_MODBUS.HRxxxx_currentWarning | Warning | 1979 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Internal Input Status | Inverter | Inverter012_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1980 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Internal Output Status | Inverter | Inverter012_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1981 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Module Fault Code | Inverter | Inverter012_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1982 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Internal Humidity | Inverter | Inverter012_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1983 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Humidity | Inverter | Inverter012_MODBUS.HRxxxx_humidity | Humidity | 1984 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_Comms Fault Time | Inverter | Inverter012_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1985 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Status | Inverter | Inverter012_MODBUS.HRxxxx_M1_status | Module Status | 1986 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 IR | Inverter | Inverter012_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1987 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 IS | Inverter | Inverter012_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 IT | Inverter | Inverter012_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1991 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1992 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1993 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 P | Inverter | Inverter012_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1994 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Q | Inverter | Inverter012_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1995 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1996 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1997 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1998 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M1 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2000 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Status | Inverter | Inverter012_MODBUS.HRxxxx_M2_status | Module Status | 2001 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 IR | Inverter | Inverter012_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2002 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 IS | Inverter | Inverter012_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2003 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 IT | Inverter | Inverter012_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2006 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2007 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 P | Inverter | Inverter012_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2009 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Q | Inverter | Inverter012_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2010 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2011 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2012 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2013 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2014 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M2 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Status | Inverter | Inverter012_MODBUS.HRxxxx_M3_status | Module Status | 2016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 IR | Inverter | Inverter012_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2017 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 IS | Inverter | Inverter012_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2018 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 IT | Inverter | Inverter012_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2019 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2021 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2022 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2023 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 P | Inverter | Inverter012_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2024 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Q | Inverter | Inverter012_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2025 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2026 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2027 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2028 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2029 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M3 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2030 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Status | Inverter | Inverter012_MODBUS.HRxxxx_M4_status | Module Status | 2031 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 IR | Inverter | Inverter012_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2032 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 IS | Inverter | Inverter012_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2033 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 IT | Inverter | Inverter012_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2035 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2036 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2037 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2038 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 P | Inverter | Inverter012_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2039 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Q | Inverter | Inverter012_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2040 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2041 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2042 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2043 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2044 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M4 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2045 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Status | Inverter | Inverter012_MODBUS.HRxxxx_M5_status | Module Status | 2046 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 IR | Inverter | Inverter012_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2047 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 IS | Inverter | Inverter012_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2048 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 IT | Inverter | Inverter012_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2051 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2052 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2053 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 P | Inverter | Inverter012_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2054 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Q | Inverter | Inverter012_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2055 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2056 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2057 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2058 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2059 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M5 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2060 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Status | Inverter | Inverter012_MODBUS.HRxxxx_M6_status | Module Status | 2061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 IR | Inverter | Inverter012_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2062 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 IS | Inverter | Inverter012_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 IT | Inverter | Inverter012_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 IDC | Inverter | Inverter012_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 VDCP | Inverter | Inverter012_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2066 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 VDCN | Inverter | Inverter012_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2067 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 VDC | Inverter | Inverter012_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 P | Inverter | Inverter012_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2069 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Q | Inverter | Inverter012_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2070 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Ambient Temp | Inverter | Inverter012_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2071 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Max IGBT Temp | Inverter | Inverter012_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2072 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 IO Status | Inverter | Inverter012_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2073 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Hardware Version | Inverter | Inverter012_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2074 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV012 | Daggett 3_SUB1_INV012_M6 Software Version | Inverter | Inverter012_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_A Phase Current | Inverter | inverter013_MODBUS.HR1004_i1_A | A Phase Current | 2076 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_B Phase Current | Inverter | inverter013_MODBUS.HR1005_i2_A | B Phase Current | 2077 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_C Phase Current | Inverter | inverter013_MODBUS.HR1006_i3_A | C Phase Current | 2078 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Bus Voltage | Inverter | inverter013_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2079 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV013 | Daggett 3_SUB1_INV013_Apparent Power | Inverter | inverter013_MODBUS.HR1010_s3_VA | Apparent Power | 2080 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 1 | Inverter | Inverter013_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC Input 1 | Inverter | Inverter013_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2082 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 2 | Inverter | Inverter013_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2083 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 2 | Inverter | Inverter013_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2084 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 3 | Inverter | Inverter013_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2085 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 3 | Inverter | Inverter013_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2086 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 4 | Inverter | Inverter013_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 4 | Inverter | Inverter013_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2088 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 5 | Inverter | Inverter013_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2089 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 5 | Inverter | Inverter013_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2090 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 6 | Inverter | Inverter013_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2091 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 6 | Inverter | Inverter013_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2092 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 7 | Inverter | Inverter013_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2093 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 7 | Inverter | Inverter013_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2094 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 8 | Inverter | Inverter013_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2095 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 8 | Inverter | Inverter013_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2096 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 9 | Inverter | Inverter013_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2097 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 9 | Inverter | Inverter013_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2098 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 10 | Inverter | Inverter013_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2099 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 10 | Inverter | Inverter013_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2100 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 11 | Inverter | Inverter013_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 11 | Inverter | Inverter013_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2102 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 12 | Inverter | Inverter013_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 12 | Inverter | Inverter013_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2104 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 13 | Inverter | Inverter013_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2105 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 13 | Inverter | Inverter013_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2106 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 14 | Inverter | Inverter013_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2107 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 14 | Inverter | Inverter013_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2108 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 15 | Inverter | Inverter013_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2109 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 15 | Inverter | Inverter013_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2110 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 16 | Inverter | Inverter013_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2111 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 16 | Inverter | Inverter013_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2112 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 17 | Inverter | Inverter013_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2113 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 17 | Inverter | Inverter013_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2114 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 18 | Inverter | Inverter013_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2115 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 18 | Inverter | Inverter013_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2116 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 19 | Inverter | Inverter013_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 19 | Inverter | Inverter013_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2118 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current DC Input 20 | Inverter | Inverter013_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC input 20 | Inverter | Inverter013_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2120 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current-AC | Inverter | inverter013_MODBUS.HR1007_i3Avg_A | Current-AC | 2121 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Current-DC | Inverter | inverter013_MODBUS.HR1062_idcInput_A | Current-DC | 2122 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Daily Energy Delivered | Inverter | inverter013_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2123 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power Set Point | Inverter | inverter013_MODBUS.HR0553_pRef | Real Power Set Point | 2124 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Reactive Power Set Point | Inverter | inverter013_MODBUS.HR0558_qRef | Reactive Power Set Point | 2125 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Frequency | Inverter | inverter013_MODBUS.HR1012_f3_Hz | Frequency | 2126 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV013 | Daggett 3_SUB1_INV013_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Insulation Resistance | Inverter | inverter013_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2127 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Number of DU Channels | Inverter | inverter013_MODBUS.HR0653_duChannels | Number of DU Channels | 2128 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Number of Running Modules | Inverter | inverter013_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2129 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Operating State | Inverter | inverter013_MODBUS.HR1123_currentStatus | Operating State | 2130 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Power Factor | Inverter | inverter013_MODBUS.HR1011_pf3 | Power Factor | 2131 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV013 | Daggett 3_SUB1_INV013_Ramp Down | Inverter | inverter013_MODBUS.HR0286_dropGradient_p | Ramp Down | 2132 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Ramp Up | Inverter | inverter013_MODBUS.HR0282_riseGradient_p | Ramp Up | 2133 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power Delivered | Inverter | inverter013_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2134 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Reactive Power Delivered | Inverter | inverter013_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2135 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power | 2136 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Reactive Power | Inverter | inverter013_MODBUS.HR1009_q3_kvar | Reactive Power | 2137 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Reactive Power Mode | Inverter | inverter013_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2138 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Reactive Power Set Point Percent | Inverter | inverter013_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2139 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power AC Percent | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2140 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power-AC | Inverter | inverter013_MODBUS.HR1008_p3_kW | Real Power-AC | 2141 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power-DC | Inverter | inverter013_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2142 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Air Intake | Inverter | inverter013_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2143 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Cabinet | Inverter | inverter013_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2144 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-IGBT | Inverter | inverter013_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2145 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Temperature-Module | Inverter | inverter013_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2146 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage A-B | Inverter | inverter013_MODBUS.HR1003_vRS_V | Voltage A-B | 2147 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage B-C | Inverter | inverter013_MODBUS.HR1002_vST_V | Voltage B-C | 2148 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage C-A | Inverter | inverter013_MODBUS.HR1003_vTR_V | Voltage C-A | 2149 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Voltage DC | Inverter | inverter013_MODBUS.HR1051_vdcBus_V | Voltage DC | 2150 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV013 | Daggett 3_SUB1_INV013_Fault Code 1 | Inverter | Inverter013_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Warning | Inverter | Inverter013_MODBUS.HRxxxx_currentWarning | Warning | 2152 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Internal Input Status | Inverter | Inverter013_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2153 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Internal Output Status | Inverter | Inverter013_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2154 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Module Fault Code | Inverter | Inverter013_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2155 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Internal Humidity | Inverter | Inverter013_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2156 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Humidity | Inverter | Inverter013_MODBUS.HRxxxx_humidity | Humidity | 2157 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_Comms Fault Time | Inverter | Inverter013_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Status | Inverter | Inverter013_MODBUS.HRxxxx_M1_status | Module Status | 2159 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 IR | Inverter | Inverter013_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2160 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 IS | Inverter | Inverter013_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 IT | Inverter | Inverter013_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2164 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2166 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 P | Inverter | Inverter013_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2167 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Q | Inverter | Inverter013_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2168 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2169 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2170 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M1 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2173 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Status | Inverter | Inverter013_MODBUS.HRxxxx_M2_status | Module Status | 2174 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 IR | Inverter | Inverter013_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2175 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 IS | Inverter | Inverter013_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2176 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 IT | Inverter | Inverter013_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2179 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2180 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 P | Inverter | Inverter013_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2182 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Q | Inverter | Inverter013_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2183 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2184 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2185 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2186 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2187 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M2 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Status | Inverter | Inverter013_MODBUS.HRxxxx_M3_status | Module Status | 2189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 IR | Inverter | Inverter013_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2190 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 IS | Inverter | Inverter013_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2191 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 IT | Inverter | Inverter013_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2194 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2195 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2196 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 P | Inverter | Inverter013_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2197 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Q | Inverter | Inverter013_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2198 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2199 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2200 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2201 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2202 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M3 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2203 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Status | Inverter | Inverter013_MODBUS.HRxxxx_M4_status | Module Status | 2204 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 IR | Inverter | Inverter013_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2205 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 IS | Inverter | Inverter013_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2206 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 IT | Inverter | Inverter013_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2209 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2210 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2211 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 P | Inverter | Inverter013_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2212 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Q | Inverter | Inverter013_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2213 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2214 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2215 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2216 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2217 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M4 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2218 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Status | Inverter | Inverter013_MODBUS.HRxxxx_M5_status | Module Status | 2219 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 IR | Inverter | Inverter013_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2220 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 IS | Inverter | Inverter013_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2221 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 IT | Inverter | Inverter013_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2224 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2225 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2226 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 P | Inverter | Inverter013_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2227 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Q | Inverter | Inverter013_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2228 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2229 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2230 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2231 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2232 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M5 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2233 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Status | Inverter | Inverter013_MODBUS.HRxxxx_M6_status | Module Status | 2234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 IR | Inverter | Inverter013_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2235 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 IS | Inverter | Inverter013_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 IT | Inverter | Inverter013_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 IDC | Inverter | Inverter013_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 VDCP | Inverter | Inverter013_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2239 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 VDCN | Inverter | Inverter013_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2240 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 VDC | Inverter | Inverter013_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 P | Inverter | Inverter013_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2242 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Q | Inverter | Inverter013_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2243 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Ambient Temp | Inverter | Inverter013_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2244 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Max IGBT Temp | Inverter | Inverter013_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2245 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 IO Status | Inverter | Inverter013_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2246 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Hardware Version | Inverter | Inverter013_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2247 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV013 | Daggett 3_SUB1_INV013_M6 Software Version | Inverter | Inverter013_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_A Phase Current | Inverter | inverter014_MODBUS.HR1004_i1_A | A Phase Current | 2249 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_B Phase Current | Inverter | inverter014_MODBUS.HR1005_i2_A | B Phase Current | 2250 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_C Phase Current | Inverter | inverter014_MODBUS.HR1006_i3_A | C Phase Current | 2251 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Bus Voltage | Inverter | inverter014_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2252 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV014 | Daggett 3_SUB1_INV014_Apparent Power | Inverter | inverter014_MODBUS.HR1010_s3_VA | Apparent Power | 2253 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 1 | Inverter | Inverter014_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC Input 1 | Inverter | Inverter014_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2255 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 2 | Inverter | Inverter014_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2256 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 2 | Inverter | Inverter014_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2257 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 3 | Inverter | Inverter014_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 3 | Inverter | Inverter014_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2259 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 4 | Inverter | Inverter014_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 4 | Inverter | Inverter014_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2261 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 5 | Inverter | Inverter014_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2262 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 5 | Inverter | Inverter014_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2263 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 6 | Inverter | Inverter014_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2264 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 6 | Inverter | Inverter014_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2265 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 7 | Inverter | Inverter014_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2266 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 7 | Inverter | Inverter014_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2267 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 8 | Inverter | Inverter014_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2268 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 8 | Inverter | Inverter014_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2269 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 9 | Inverter | Inverter014_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2270 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 9 | Inverter | Inverter014_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2271 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 10 | Inverter | Inverter014_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2272 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 10 | Inverter | Inverter014_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2273 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 11 | Inverter | Inverter014_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 11 | Inverter | Inverter014_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2275 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 12 | Inverter | Inverter014_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 12 | Inverter | Inverter014_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2277 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 13 | Inverter | Inverter014_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2278 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 13 | Inverter | Inverter014_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2279 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 14 | Inverter | Inverter014_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2280 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 14 | Inverter | Inverter014_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2281 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 15 | Inverter | Inverter014_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2282 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 15 | Inverter | Inverter014_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2283 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 16 | Inverter | Inverter014_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2284 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 16 | Inverter | Inverter014_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2285 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 17 | Inverter | Inverter014_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2286 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 17 | Inverter | Inverter014_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2287 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 18 | Inverter | Inverter014_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2288 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 18 | Inverter | Inverter014_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2289 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 19 | Inverter | Inverter014_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 19 | Inverter | Inverter014_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2291 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current DC Input 20 | Inverter | Inverter014_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC input 20 | Inverter | Inverter014_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2293 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current-AC | Inverter | inverter014_MODBUS.HR1007_i3Avg_A | Current-AC | 2294 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Current-DC | Inverter | inverter014_MODBUS.HR1062_idcInput_A | Current-DC | 2295 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Daily Energy Delivered | Inverter | inverter014_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2296 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power Set Point | Inverter | inverter014_MODBUS.HR0553_pRef | Real Power Set Point | 2297 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Reactive Power Set Point | Inverter | inverter014_MODBUS.HR0558_qRef | Reactive Power Set Point | 2298 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Frequency | Inverter | inverter014_MODBUS.HR1012_f3_Hz | Frequency | 2299 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV014 | Daggett 3_SUB1_INV014_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Insulation Resistance | Inverter | inverter014_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2300 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Number of DU Channels | Inverter | inverter014_MODBUS.HR0653_duChannels | Number of DU Channels | 2301 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Number of Running Modules | Inverter | inverter014_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2302 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Operating State | Inverter | inverter014_MODBUS.HR1123_currentStatus | Operating State | 2303 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Power Factor | Inverter | inverter014_MODBUS.HR1011_pf3 | Power Factor | 2304 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV014 | Daggett 3_SUB1_INV014_Ramp Down | Inverter | inverter014_MODBUS.HR0286_dropGradient_p | Ramp Down | 2305 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Ramp Up | Inverter | inverter014_MODBUS.HR0282_riseGradient_p | Ramp Up | 2306 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power Delivered | Inverter | inverter014_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2307 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Reactive Power Delivered | Inverter | inverter014_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2308 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power | 2309 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Reactive Power | Inverter | inverter014_MODBUS.HR1009_q3_kvar | Reactive Power | 2310 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Reactive Power Mode | Inverter | inverter014_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2311 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Reactive Power Set Point Percent | Inverter | inverter014_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2312 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power AC Percent | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2313 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power-AC | Inverter | inverter014_MODBUS.HR1008_p3_kW | Real Power-AC | 2314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power-DC | Inverter | inverter014_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2315 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Air Intake | Inverter | inverter014_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2316 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Cabinet | Inverter | inverter014_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2317 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-IGBT | Inverter | inverter014_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2318 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Temperature-Module | Inverter | inverter014_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2319 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage A-B | Inverter | inverter014_MODBUS.HR1004_vRS_V | Voltage A-B | 2320 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage B-C | Inverter | inverter014_MODBUS.HR1002_vST_V | Voltage B-C | 2321 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage C-A | Inverter | inverter014_MODBUS.HR1003_vTR_V | Voltage C-A | 2322 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Voltage DC | Inverter | inverter014_MODBUS.HR1051_vdcBus_V | Voltage DC | 2323 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV014 | Daggett 3_SUB1_INV014_Fault Code 1 | Inverter | Inverter014_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Warning | Inverter | Inverter014_MODBUS.HRxxxx_currentWarning | Warning | 2325 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Internal Input Status | Inverter | Inverter014_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2326 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Internal Output Status | Inverter | Inverter014_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2327 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Module Fault Code | Inverter | Inverter014_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2328 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Internal Humidity | Inverter | Inverter014_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2329 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Humidity | Inverter | Inverter014_MODBUS.HRxxxx_humidity | Humidity | 2330 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_Comms Fault Time | Inverter | Inverter014_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Status | Inverter | Inverter014_MODBUS.HRxxxx_M1_status | Module Status | 2332 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 IR | Inverter | Inverter014_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2333 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 IS | Inverter | Inverter014_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 IT | Inverter | Inverter014_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2337 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2339 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 P | Inverter | Inverter014_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2340 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Q | Inverter | Inverter014_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2341 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2342 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2343 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M1 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2346 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Status | Inverter | Inverter014_MODBUS.HRxxxx_M2_status | Module Status | 2347 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 IR | Inverter | Inverter014_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2348 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 IS | Inverter | Inverter014_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2349 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 IT | Inverter | Inverter014_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2352 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2353 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 P | Inverter | Inverter014_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2355 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Q | Inverter | Inverter014_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2356 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2357 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2358 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2359 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2360 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M2 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Status | Inverter | Inverter014_MODBUS.HRxxxx_M3_status | Module Status | 2362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 IR | Inverter | Inverter014_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2363 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 IS | Inverter | Inverter014_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2364 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 IT | Inverter | Inverter014_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2367 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2368 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2369 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 P | Inverter | Inverter014_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2370 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Q | Inverter | Inverter014_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2371 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2372 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2373 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2374 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2375 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M3 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2376 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Status | Inverter | Inverter014_MODBUS.HRxxxx_M4_status | Module Status | 2377 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 IR | Inverter | Inverter014_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2378 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 IS | Inverter | Inverter014_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2379 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 IT | Inverter | Inverter014_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2382 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2383 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2384 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 P | Inverter | Inverter014_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2385 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Q | Inverter | Inverter014_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2386 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2387 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2388 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2389 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2390 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M4 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2391 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Status | Inverter | Inverter014_MODBUS.HRxxxx_M5_status | Module Status | 2392 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 IR | Inverter | Inverter014_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2393 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 IS | Inverter | Inverter014_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2394 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 IT | Inverter | Inverter014_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2397 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2398 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2399 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 P | Inverter | Inverter014_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2400 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Q | Inverter | Inverter014_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2401 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2402 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2403 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2404 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2405 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M5 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2406 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Status | Inverter | Inverter014_MODBUS.HRxxxx_M6_status | Module Status | 2407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 IR | Inverter | Inverter014_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2408 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 IS | Inverter | Inverter014_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 IT | Inverter | Inverter014_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 IDC | Inverter | Inverter014_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 VDCP | Inverter | Inverter014_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2412 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 VDCN | Inverter | Inverter014_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2413 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 VDC | Inverter | Inverter014_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 P | Inverter | Inverter014_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2415 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Q | Inverter | Inverter014_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2416 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Ambient Temp | Inverter | Inverter014_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2417 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Max IGBT Temp | Inverter | Inverter014_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2418 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 IO Status | Inverter | Inverter014_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2419 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Hardware Version | Inverter | Inverter014_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2420 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV014 | Daggett 3_SUB1_INV014_M6 Software Version | Inverter | Inverter014_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_A Phase Current | Inverter | inverter015_MODBUS.HR1004_i1_A | A Phase Current | 2422 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_B Phase Current | Inverter | inverter015_MODBUS.HR1005_i2_A | B Phase Current | 2423 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_C Phase Current | Inverter | inverter015_MODBUS.HR1006_i3_A | C Phase Current | 2424 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Bus Voltage | Inverter | inverter015_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2425 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV015 | Daggett 3_SUB1_INV015_Apparent Power | Inverter | inverter015_MODBUS.HR1010_s3_VA | Apparent Power | 2426 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 1 | Inverter | Inverter015_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC Input 1 | Inverter | Inverter015_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2428 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 2 | Inverter | Inverter015_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2429 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 2 | Inverter | Inverter015_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2430 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 3 | Inverter | Inverter015_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 3 | Inverter | Inverter015_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2432 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 4 | Inverter | Inverter015_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 4 | Inverter | Inverter015_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2434 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 5 | Inverter | Inverter015_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2435 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 5 | Inverter | Inverter015_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2436 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 6 | Inverter | Inverter015_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2437 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 6 | Inverter | Inverter015_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2438 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 7 | Inverter | Inverter015_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2439 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 7 | Inverter | Inverter015_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2440 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 8 | Inverter | Inverter015_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2441 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 8 | Inverter | Inverter015_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2442 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 9 | Inverter | Inverter015_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2443 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 9 | Inverter | Inverter015_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2444 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 10 | Inverter | Inverter015_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2445 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 10 | Inverter | Inverter015_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2446 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 11 | Inverter | Inverter015_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 11 | Inverter | Inverter015_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2448 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 12 | Inverter | Inverter015_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 12 | Inverter | Inverter015_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2450 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 13 | Inverter | Inverter015_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2451 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 13 | Inverter | Inverter015_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2452 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 14 | Inverter | Inverter015_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2453 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 14 | Inverter | Inverter015_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2454 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 15 | Inverter | Inverter015_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2455 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 15 | Inverter | Inverter015_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2456 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 16 | Inverter | Inverter015_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2457 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 16 | Inverter | Inverter015_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2458 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 17 | Inverter | Inverter015_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2459 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 17 | Inverter | Inverter015_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2460 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 18 | Inverter | Inverter015_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2461 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 18 | Inverter | Inverter015_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2462 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 19 | Inverter | Inverter015_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 19 | Inverter | Inverter015_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2464 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current DC Input 20 | Inverter | Inverter015_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC input 20 | Inverter | Inverter015_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2466 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current-AC | Inverter | inverter015_MODBUS.HR1007_i3Avg_A | Current-AC | 2467 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Current-DC | Inverter | inverter015_MODBUS.HR1062_idcInput_A | Current-DC | 2468 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Daily Energy Delivered | Inverter | inverter015_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2469 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power Set Point | Inverter | inverter015_MODBUS.HR0553_pRef | Real Power Set Point | 2470 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Reactive Power Set Point | Inverter | inverter015_MODBUS.HR0558_qRef | Reactive Power Set Point | 2471 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Frequency | Inverter | inverter015_MODBUS.HR1012_f3_Hz | Frequency | 2472 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV015 | Daggett 3_SUB1_INV015_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Insulation Resistance | Inverter | inverter015_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2473 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Number of DU Channels | Inverter | inverter015_MODBUS.HR0653_duChannels | Number of DU Channels | 2474 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Number of Running Modules | Inverter | inverter015_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2475 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Operating State | Inverter | inverter015_MODBUS.HR1123_currentStatus | Operating State | 2476 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Power Factor | Inverter | inverter015_MODBUS.HR1011_pf3 | Power Factor | 2477 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV015 | Daggett 3_SUB1_INV015_Ramp Down | Inverter | inverter015_MODBUS.HR0286_dropGradient_p | Ramp Down | 2478 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Ramp Up | Inverter | inverter015_MODBUS.HR0282_riseGradient_p | Ramp Up | 2479 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power Delivered | Inverter | inverter015_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2480 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Reactive Power Delivered | Inverter | inverter015_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2481 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power | 2482 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Reactive Power | Inverter | inverter015_MODBUS.HR1009_q3_kvar | Reactive Power | 2483 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Reactive Power Mode | Inverter | inverter015_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2484 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Reactive Power Set Point Percent | Inverter | inverter015_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2485 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power AC Percent | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2486 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power-AC | Inverter | inverter015_MODBUS.HR1008_p3_kW | Real Power-AC | 2487 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power-DC | Inverter | inverter015_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2488 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Air Intake | Inverter | inverter015_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2489 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Cabinet | Inverter | inverter015_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2490 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-IGBT | Inverter | inverter015_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2491 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Temperature-Module | Inverter | inverter015_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2492 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage A-B | Inverter | inverter015_MODBUS.HR1005_vRS_V | Voltage A-B | 2493 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage B-C | Inverter | inverter015_MODBUS.HR1002_vST_V | Voltage B-C | 2494 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage C-A | Inverter | inverter015_MODBUS.HR1003_vTR_V | Voltage C-A | 2495 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Voltage DC | Inverter | inverter015_MODBUS.HR1051_vdcBus_V | Voltage DC | 2496 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV015 | Daggett 3_SUB1_INV015_Fault Code 1 | Inverter | Inverter015_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Warning | Inverter | Inverter015_MODBUS.HRxxxx_currentWarning | Warning | 2498 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Internal Input Status | Inverter | Inverter015_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2499 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Internal Output Status | Inverter | Inverter015_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2500 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Module Fault Code | Inverter | Inverter015_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2501 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Internal Humidity | Inverter | Inverter015_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2502 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Humidity | Inverter | Inverter015_MODBUS.HRxxxx_humidity | Humidity | 2503 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_Comms Fault Time | Inverter | Inverter015_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Status | Inverter | Inverter015_MODBUS.HRxxxx_M1_status | Module Status | 2505 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 IR | Inverter | Inverter015_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2506 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 IS | Inverter | Inverter015_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 IT | Inverter | Inverter015_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2510 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2512 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 P | Inverter | Inverter015_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2513 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Q | Inverter | Inverter015_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2514 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2515 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2516 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M1 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2519 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Status | Inverter | Inverter015_MODBUS.HRxxxx_M2_status | Module Status | 2520 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 IR | Inverter | Inverter015_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2521 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 IS | Inverter | Inverter015_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2522 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 IT | Inverter | Inverter015_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2525 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2526 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 P | Inverter | Inverter015_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2528 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Q | Inverter | Inverter015_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2529 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2530 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2531 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2532 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2533 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M2 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Status | Inverter | Inverter015_MODBUS.HRxxxx_M3_status | Module Status | 2535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 IR | Inverter | Inverter015_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2536 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 IS | Inverter | Inverter015_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2537 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 IT | Inverter | Inverter015_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2540 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2541 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2542 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 P | Inverter | Inverter015_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2543 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Q | Inverter | Inverter015_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2544 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2545 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2546 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2547 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2548 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M3 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2549 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Status | Inverter | Inverter015_MODBUS.HRxxxx_M4_status | Module Status | 2550 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 IR | Inverter | Inverter015_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2551 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 IS | Inverter | Inverter015_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2552 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 IT | Inverter | Inverter015_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2555 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2556 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2557 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 P | Inverter | Inverter015_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2558 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Q | Inverter | Inverter015_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2559 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2560 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2561 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2562 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2563 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M4 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2564 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Status | Inverter | Inverter015_MODBUS.HRxxxx_M5_status | Module Status | 2565 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 IR | Inverter | Inverter015_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2566 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 IS | Inverter | Inverter015_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2567 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 IT | Inverter | Inverter015_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2570 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2571 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2572 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 P | Inverter | Inverter015_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2573 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Q | Inverter | Inverter015_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2574 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2575 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2576 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2577 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2578 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M5 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2579 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Status | Inverter | Inverter015_MODBUS.HRxxxx_M6_status | Module Status | 2580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 IR | Inverter | Inverter015_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2581 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 IS | Inverter | Inverter015_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 IT | Inverter | Inverter015_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 IDC | Inverter | Inverter015_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 VDCP | Inverter | Inverter015_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2585 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 VDCN | Inverter | Inverter015_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2586 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 VDC | Inverter | Inverter015_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 P | Inverter | Inverter015_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2588 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Q | Inverter | Inverter015_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2589 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Ambient Temp | Inverter | Inverter015_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2590 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Max IGBT Temp | Inverter | Inverter015_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2591 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 IO Status | Inverter | Inverter015_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2592 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Hardware Version | Inverter | Inverter015_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2593 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV015 | Daggett 3_SUB1_INV015_M6 Software Version | Inverter | Inverter015_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_A Phase Current | Inverter | inverter016_MODBUS.HR1004_i1_A | A Phase Current | 2595 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_B Phase Current | Inverter | inverter016_MODBUS.HR1005_i2_A | B Phase Current | 2596 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_C Phase Current | Inverter | inverter016_MODBUS.HR1006_i3_A | C Phase Current | 2597 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Bus Voltage | Inverter | inverter016_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2598 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV016 | Daggett 3_SUB1_INV016_Apparent Power | Inverter | inverter016_MODBUS.HR1010_s3_VA | Apparent Power | 2599 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 1 | Inverter | Inverter016_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC Input 1 | Inverter | Inverter016_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2601 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 2 | Inverter | Inverter016_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2602 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 2 | Inverter | Inverter016_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2603 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 3 | Inverter | Inverter016_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 3 | Inverter | Inverter016_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2605 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 4 | Inverter | Inverter016_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 4 | Inverter | Inverter016_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2607 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 5 | Inverter | Inverter016_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2608 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 5 | Inverter | Inverter016_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2609 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 6 | Inverter | Inverter016_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2610 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 6 | Inverter | Inverter016_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2611 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 7 | Inverter | Inverter016_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2612 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 7 | Inverter | Inverter016_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2613 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 8 | Inverter | Inverter016_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2614 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 8 | Inverter | Inverter016_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2615 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 9 | Inverter | Inverter016_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2616 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 9 | Inverter | Inverter016_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2617 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 10 | Inverter | Inverter016_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2618 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 10 | Inverter | Inverter016_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2619 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 11 | Inverter | Inverter016_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 11 | Inverter | Inverter016_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2621 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 12 | Inverter | Inverter016_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 12 | Inverter | Inverter016_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2623 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 13 | Inverter | Inverter016_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2624 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 13 | Inverter | Inverter016_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2625 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 14 | Inverter | Inverter016_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2626 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 14 | Inverter | Inverter016_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2627 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 15 | Inverter | Inverter016_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2628 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 15 | Inverter | Inverter016_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2629 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 16 | Inverter | Inverter016_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2630 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 16 | Inverter | Inverter016_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2631 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 17 | Inverter | Inverter016_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2632 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 17 | Inverter | Inverter016_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2633 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 18 | Inverter | Inverter016_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2634 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 18 | Inverter | Inverter016_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2635 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 19 | Inverter | Inverter016_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 19 | Inverter | Inverter016_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2637 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current DC Input 20 | Inverter | Inverter016_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC input 20 | Inverter | Inverter016_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2639 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current-AC | Inverter | inverter016_MODBUS.HR1007_i3Avg_A | Current-AC | 2640 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Current-DC | Inverter | inverter016_MODBUS.HR1062_idcInput_A | Current-DC | 2641 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Daily Energy Delivered | Inverter | inverter016_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2642 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power Set Point | Inverter | inverter016_MODBUS.HR0553_pRef | Real Power Set Point | 2643 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Reactive Power Set Point | Inverter | inverter016_MODBUS.HR0558_qRef | Reactive Power Set Point | 2644 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Frequency | Inverter | inverter016_MODBUS.HR1012_f3_Hz | Frequency | 2645 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV016 | Daggett 3_SUB1_INV016_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Insulation Resistance | Inverter | inverter016_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2646 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Number of DU Channels | Inverter | inverter016_MODBUS.HR0653_duChannels | Number of DU Channels | 2647 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Number of Running Modules | Inverter | inverter016_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2648 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Operating State | Inverter | inverter016_MODBUS.HR1123_currentStatus | Operating State | 2649 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Power Factor | Inverter | inverter016_MODBUS.HR1011_pf3 | Power Factor | 2650 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV016 | Daggett 3_SUB1_INV016_Ramp Down | Inverter | inverter016_MODBUS.HR0286_dropGradient_p | Ramp Down | 2651 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Ramp Up | Inverter | inverter016_MODBUS.HR0282_riseGradient_p | Ramp Up | 2652 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power Delivered | Inverter | inverter016_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2653 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Reactive Power Delivered | Inverter | inverter016_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2654 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power | 2655 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Reactive Power | Inverter | inverter016_MODBUS.HR1009_q3_kvar | Reactive Power | 2656 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Reactive Power Mode | Inverter | inverter016_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2657 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Reactive Power Set Point Percent | Inverter | inverter016_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2658 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power AC Percent | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2659 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power-AC | Inverter | inverter016_MODBUS.HR1008_p3_kW | Real Power-AC | 2660 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power-DC | Inverter | inverter016_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2661 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Air Intake | Inverter | inverter016_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2662 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Cabinet | Inverter | inverter016_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2663 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-IGBT | Inverter | inverter016_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2664 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Temperature-Module | Inverter | inverter016_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2665 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage A-B | Inverter | inverter016_MODBUS.HR1006_vRS_V | Voltage A-B | 2666 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage B-C | Inverter | inverter016_MODBUS.HR1002_vST_V | Voltage B-C | 2667 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage C-A | Inverter | inverter016_MODBUS.HR1003_vTR_V | Voltage C-A | 2668 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Voltage DC | Inverter | inverter016_MODBUS.HR1051_vdcBus_V | Voltage DC | 2669 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV016 | Daggett 3_SUB1_INV016_Fault Code 1 | Inverter | Inverter016_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Warning | Inverter | Inverter016_MODBUS.HRxxxx_currentWarning | Warning | 2671 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Internal Input Status | Inverter | Inverter016_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2672 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Internal Output Status | Inverter | Inverter016_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2673 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Module Fault Code | Inverter | Inverter016_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2674 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Internal Humidity | Inverter | Inverter016_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2675 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Humidity | Inverter | Inverter016_MODBUS.HRxxxx_humidity | Humidity | 2676 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_Comms Fault Time | Inverter | Inverter016_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Status | Inverter | Inverter016_MODBUS.HRxxxx_M1_status | Module Status | 2678 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 IR | Inverter | Inverter016_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2679 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 IS | Inverter | Inverter016_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 IT | Inverter | Inverter016_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2683 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2685 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 P | Inverter | Inverter016_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2686 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Q | Inverter | Inverter016_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2687 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2688 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2689 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M1 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2692 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Status | Inverter | Inverter016_MODBUS.HRxxxx_M2_status | Module Status | 2693 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 IR | Inverter | Inverter016_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2694 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 IS | Inverter | Inverter016_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2695 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 IT | Inverter | Inverter016_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2698 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2699 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 P | Inverter | Inverter016_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2701 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Q | Inverter | Inverter016_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2702 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2703 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2704 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2705 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2706 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M2 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Status | Inverter | Inverter016_MODBUS.HRxxxx_M3_status | Module Status | 2708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 IR | Inverter | Inverter016_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2709 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 IS | Inverter | Inverter016_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2710 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 IT | Inverter | Inverter016_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2713 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2714 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2715 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 P | Inverter | Inverter016_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2716 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Q | Inverter | Inverter016_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2717 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2718 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2719 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2720 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2721 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M3 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2722 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Status | Inverter | Inverter016_MODBUS.HRxxxx_M4_status | Module Status | 2723 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 IR | Inverter | Inverter016_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2724 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 IS | Inverter | Inverter016_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2725 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 IT | Inverter | Inverter016_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2728 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2729 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2730 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 P | Inverter | Inverter016_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2731 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Q | Inverter | Inverter016_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2732 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2733 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2734 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2735 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2736 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M4 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2737 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Status | Inverter | Inverter016_MODBUS.HRxxxx_M5_status | Module Status | 2738 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 IR | Inverter | Inverter016_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2739 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 IS | Inverter | Inverter016_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2740 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 IT | Inverter | Inverter016_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2743 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2744 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2745 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 P | Inverter | Inverter016_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2746 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Q | Inverter | Inverter016_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2747 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2748 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2749 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2750 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2751 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M5 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2752 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Status | Inverter | Inverter016_MODBUS.HRxxxx_M6_status | Module Status | 2753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 IR | Inverter | Inverter016_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2754 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 IS | Inverter | Inverter016_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 IT | Inverter | Inverter016_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 IDC | Inverter | Inverter016_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 VDCP | Inverter | Inverter016_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2758 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 VDCN | Inverter | Inverter016_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2759 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 VDC | Inverter | Inverter016_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 P | Inverter | Inverter016_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2761 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Q | Inverter | Inverter016_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2762 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Ambient Temp | Inverter | Inverter016_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2763 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Max IGBT Temp | Inverter | Inverter016_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2764 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 IO Status | Inverter | Inverter016_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2765 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Hardware Version | Inverter | Inverter016_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2766 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV016 | Daggett 3_SUB1_INV016_M6 Software Version | Inverter | Inverter016_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_A Phase Current | Inverter | inverter017_MODBUS.HR1004_i1_A | A Phase Current | 2768 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_B Phase Current | Inverter | inverter017_MODBUS.HR1005_i2_A | B Phase Current | 2769 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_C Phase Current | Inverter | inverter017_MODBUS.HR1006_i3_A | C Phase Current | 2770 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Bus Voltage | Inverter | inverter017_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2771 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV017 | Daggett 3_SUB1_INV017_Apparent Power | Inverter | inverter017_MODBUS.HR1010_s3_VA | Apparent Power | 2772 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 1 | Inverter | Inverter017_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC Input 1 | Inverter | Inverter017_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2774 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 2 | Inverter | Inverter017_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2775 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 2 | Inverter | Inverter017_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2776 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 3 | Inverter | Inverter017_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 3 | Inverter | Inverter017_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2778 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 4 | Inverter | Inverter017_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 4 | Inverter | Inverter017_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2780 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 5 | Inverter | Inverter017_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2781 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 5 | Inverter | Inverter017_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2782 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 6 | Inverter | Inverter017_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2783 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 6 | Inverter | Inverter017_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2784 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 7 | Inverter | Inverter017_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2785 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 7 | Inverter | Inverter017_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2786 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 8 | Inverter | Inverter017_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2787 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 8 | Inverter | Inverter017_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2788 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 9 | Inverter | Inverter017_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2789 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 9 | Inverter | Inverter017_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2790 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 10 | Inverter | Inverter017_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2791 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 10 | Inverter | Inverter017_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2792 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 11 | Inverter | Inverter017_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 11 | Inverter | Inverter017_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2794 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 12 | Inverter | Inverter017_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 12 | Inverter | Inverter017_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2796 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 13 | Inverter | Inverter017_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2797 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 13 | Inverter | Inverter017_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2798 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 14 | Inverter | Inverter017_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2799 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 14 | Inverter | Inverter017_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2800 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 15 | Inverter | Inverter017_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2801 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 15 | Inverter | Inverter017_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2802 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 16 | Inverter | Inverter017_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2803 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 16 | Inverter | Inverter017_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2804 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 17 | Inverter | Inverter017_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2805 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 17 | Inverter | Inverter017_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2806 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 18 | Inverter | Inverter017_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2807 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 18 | Inverter | Inverter017_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2808 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 19 | Inverter | Inverter017_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 19 | Inverter | Inverter017_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2810 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current DC Input 20 | Inverter | Inverter017_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC input 20 | Inverter | Inverter017_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2812 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current-AC | Inverter | inverter017_MODBUS.HR1007_i3Avg_A | Current-AC | 2813 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Current-DC | Inverter | inverter017_MODBUS.HR1062_idcInput_A | Current-DC | 2814 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Daily Energy Delivered | Inverter | inverter017_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2815 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power Set Point | Inverter | inverter017_MODBUS.HR0553_pRef | Real Power Set Point | 2816 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Reactive Power Set Point | Inverter | inverter017_MODBUS.HR0558_qRef | Reactive Power Set Point | 2817 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Frequency | Inverter | inverter017_MODBUS.HR1012_f3_Hz | Frequency | 2818 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV017 | Daggett 3_SUB1_INV017_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Insulation Resistance | Inverter | inverter017_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2819 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Number of DU Channels | Inverter | inverter017_MODBUS.HR0653_duChannels | Number of DU Channels | 2820 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Number of Running Modules | Inverter | inverter017_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2821 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Operating State | Inverter | inverter017_MODBUS.HR1123_currentStatus | Operating State | 2822 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Power Factor | Inverter | inverter017_MODBUS.HR1011_pf3 | Power Factor | 2823 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV017 | Daggett 3_SUB1_INV017_Ramp Down | Inverter | inverter017_MODBUS.HR0286_dropGradient_p | Ramp Down | 2824 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Ramp Up | Inverter | inverter017_MODBUS.HR0282_riseGradient_p | Ramp Up | 2825 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power Delivered | Inverter | inverter017_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2826 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Reactive Power Delivered | Inverter | inverter017_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2827 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power | 2828 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Reactive Power | Inverter | inverter017_MODBUS.HR1009_q3_kvar | Reactive Power | 2829 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Reactive Power Mode | Inverter | inverter017_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2830 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Reactive Power Set Point Percent | Inverter | inverter017_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2831 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power AC Percent | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2832 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power-AC | Inverter | inverter017_MODBUS.HR1008_p3_kW | Real Power-AC | 2833 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power-DC | Inverter | inverter017_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2834 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Air Intake | Inverter | inverter017_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2835 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Cabinet | Inverter | inverter017_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2836 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-IGBT | Inverter | inverter017_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2837 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Temperature-Module | Inverter | inverter017_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2838 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage A-B | Inverter | inverter017_MODBUS.HR1007_vRS_V | Voltage A-B | 2839 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage B-C | Inverter | inverter017_MODBUS.HR1002_vST_V | Voltage B-C | 2840 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage C-A | Inverter | inverter017_MODBUS.HR1003_vTR_V | Voltage C-A | 2841 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Voltage DC | Inverter | inverter017_MODBUS.HR1051_vdcBus_V | Voltage DC | 2842 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV017 | Daggett 3_SUB1_INV017_Fault Code 1 | Inverter | Inverter017_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Warning | Inverter | Inverter017_MODBUS.HRxxxx_currentWarning | Warning | 2844 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Internal Input Status | Inverter | Inverter017_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2845 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Internal Output Status | Inverter | Inverter017_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2846 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Module Fault Code | Inverter | Inverter017_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2847 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Internal Humidity | Inverter | Inverter017_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2848 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Humidity | Inverter | Inverter017_MODBUS.HRxxxx_humidity | Humidity | 2849 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_Comms Fault Time | Inverter | Inverter017_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Status | Inverter | Inverter017_MODBUS.HRxxxx_M1_status | Module Status | 2851 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 IR | Inverter | Inverter017_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2852 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 IS | Inverter | Inverter017_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 IT | Inverter | Inverter017_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2856 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2858 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 P | Inverter | Inverter017_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2859 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Q | Inverter | Inverter017_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2860 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2861 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2862 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M1 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2865 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Status | Inverter | Inverter017_MODBUS.HRxxxx_M2_status | Module Status | 2866 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 IR | Inverter | Inverter017_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2867 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 IS | Inverter | Inverter017_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2868 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 IT | Inverter | Inverter017_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2871 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2872 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 P | Inverter | Inverter017_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2874 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Q | Inverter | Inverter017_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2875 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2876 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2877 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2878 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2879 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M2 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Status | Inverter | Inverter017_MODBUS.HRxxxx_M3_status | Module Status | 2881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 IR | Inverter | Inverter017_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2882 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 IS | Inverter | Inverter017_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2883 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 IT | Inverter | Inverter017_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2886 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2887 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2888 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 P | Inverter | Inverter017_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2889 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Q | Inverter | Inverter017_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2890 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2891 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2892 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2893 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2894 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M3 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2895 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Status | Inverter | Inverter017_MODBUS.HRxxxx_M4_status | Module Status | 2896 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 IR | Inverter | Inverter017_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2897 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 IS | Inverter | Inverter017_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2898 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 IT | Inverter | Inverter017_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2901 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2902 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2903 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 P | Inverter | Inverter017_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2904 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Q | Inverter | Inverter017_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2905 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2906 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2907 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2908 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2909 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M4 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2910 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Status | Inverter | Inverter017_MODBUS.HRxxxx_M5_status | Module Status | 2911 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 IR | Inverter | Inverter017_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2912 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 IS | Inverter | Inverter017_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2913 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 IT | Inverter | Inverter017_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2916 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2917 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2918 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 P | Inverter | Inverter017_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2919 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Q | Inverter | Inverter017_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2920 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2921 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2922 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2923 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2924 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M5 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2925 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Status | Inverter | Inverter017_MODBUS.HRxxxx_M6_status | Module Status | 2926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 IR | Inverter | Inverter017_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2927 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 IS | Inverter | Inverter017_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 IT | Inverter | Inverter017_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 IDC | Inverter | Inverter017_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 VDCP | Inverter | Inverter017_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2931 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 VDCN | Inverter | Inverter017_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2932 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 VDC | Inverter | Inverter017_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 P | Inverter | Inverter017_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2934 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Q | Inverter | Inverter017_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2935 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Ambient Temp | Inverter | Inverter017_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2936 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Max IGBT Temp | Inverter | Inverter017_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2937 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 IO Status | Inverter | Inverter017_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2938 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Hardware Version | Inverter | Inverter017_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2939 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV017 | Daggett 3_SUB1_INV017_M6 Software Version | Inverter | Inverter017_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_A Phase Current | Inverter | inverter018_MODBUS.HR1004_i1_A | A Phase Current | 2941 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_B Phase Current | Inverter | inverter018_MODBUS.HR1005_i2_A | B Phase Current | 2942 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_C Phase Current | Inverter | inverter018_MODBUS.HR1006_i3_A | C Phase Current | 2943 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Bus Voltage | Inverter | inverter018_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2944 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV018 | Daggett 3_SUB1_INV018_Apparent Power | Inverter | inverter018_MODBUS.HR1010_s3_VA | Apparent Power | 2945 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 1 | Inverter | Inverter018_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC Input 1 | Inverter | Inverter018_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2947 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 2 | Inverter | Inverter018_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2948 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 2 | Inverter | Inverter018_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2949 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 3 | Inverter | Inverter018_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 3 | Inverter | Inverter018_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2951 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 4 | Inverter | Inverter018_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 4 | Inverter | Inverter018_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2953 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 5 | Inverter | Inverter018_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2954 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 5 | Inverter | Inverter018_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2955 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 6 | Inverter | Inverter018_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2956 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 6 | Inverter | Inverter018_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2957 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 7 | Inverter | Inverter018_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2958 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 7 | Inverter | Inverter018_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2959 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 8 | Inverter | Inverter018_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2960 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 8 | Inverter | Inverter018_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2961 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 9 | Inverter | Inverter018_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2962 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 9 | Inverter | Inverter018_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2963 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 10 | Inverter | Inverter018_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2964 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 10 | Inverter | Inverter018_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2965 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 11 | Inverter | Inverter018_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 11 | Inverter | Inverter018_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2967 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 12 | Inverter | Inverter018_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 12 | Inverter | Inverter018_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2969 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 13 | Inverter | Inverter018_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2970 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 13 | Inverter | Inverter018_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2971 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 14 | Inverter | Inverter018_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2972 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 14 | Inverter | Inverter018_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2973 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 15 | Inverter | Inverter018_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2974 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 15 | Inverter | Inverter018_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2975 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 16 | Inverter | Inverter018_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2976 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 16 | Inverter | Inverter018_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2977 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 17 | Inverter | Inverter018_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2978 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 17 | Inverter | Inverter018_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2979 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 18 | Inverter | Inverter018_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2980 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 18 | Inverter | Inverter018_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2981 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 19 | Inverter | Inverter018_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 19 | Inverter | Inverter018_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2983 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current DC Input 20 | Inverter | Inverter018_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC input 20 | Inverter | Inverter018_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2985 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current-AC | Inverter | inverter018_MODBUS.HR1007_i3Avg_A | Current-AC | 2986 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Current-DC | Inverter | inverter018_MODBUS.HR1062_idcInput_A | Current-DC | 2987 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Daily Energy Delivered | Inverter | inverter018_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2988 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power Set Point | Inverter | inverter018_MODBUS.HR0553_pRef | Real Power Set Point | 2989 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Reactive Power Set Point | Inverter | inverter018_MODBUS.HR0558_qRef | Reactive Power Set Point | 2990 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Frequency | Inverter | inverter018_MODBUS.HR1012_f3_Hz | Frequency | 2991 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV018 | Daggett 3_SUB1_INV018_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Insulation Resistance | Inverter | inverter018_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2992 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Number of DU Channels | Inverter | inverter018_MODBUS.HR0653_duChannels | Number of DU Channels | 2993 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Number of Running Modules | Inverter | inverter018_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2994 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Operating State | Inverter | inverter018_MODBUS.HR1123_currentStatus | Operating State | 2995 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Power Factor | Inverter | inverter018_MODBUS.HR1011_pf3 | Power Factor | 2996 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV018 | Daggett 3_SUB1_INV018_Ramp Down | Inverter | inverter018_MODBUS.HR0286_dropGradient_p | Ramp Down | 2997 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Ramp Up | Inverter | inverter018_MODBUS.HR0282_riseGradient_p | Ramp Up | 2998 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power Delivered | Inverter | inverter018_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2999 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Reactive Power Delivered | Inverter | inverter018_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3000 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power | 3001 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Reactive Power | Inverter | inverter018_MODBUS.HR1009_q3_kvar | Reactive Power | 3002 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Reactive Power Mode | Inverter | inverter018_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3003 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Reactive Power Set Point Percent | Inverter | inverter018_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3004 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power AC Percent | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3005 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power-AC | Inverter | inverter018_MODBUS.HR1008_p3_kW | Real Power-AC | 3006 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power-DC | Inverter | inverter018_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3007 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Air Intake | Inverter | inverter018_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3008 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Cabinet | Inverter | inverter018_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3009 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-IGBT | Inverter | inverter018_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3010 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Temperature-Module | Inverter | inverter018_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3011 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage A-B | Inverter | inverter018_MODBUS.HR1008_vRS_V | Voltage A-B | 3012 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage B-C | Inverter | inverter018_MODBUS.HR1002_vST_V | Voltage B-C | 3013 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage C-A | Inverter | inverter018_MODBUS.HR1003_vTR_V | Voltage C-A | 3014 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Voltage DC | Inverter | inverter018_MODBUS.HR1051_vdcBus_V | Voltage DC | 3015 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV018 | Daggett 3_SUB1_INV018_Fault Code 1 | Inverter | Inverter018_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Warning | Inverter | Inverter018_MODBUS.HRxxxx_currentWarning | Warning | 3017 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Internal Input Status | Inverter | Inverter018_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3018 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Internal Output Status | Inverter | Inverter018_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3019 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Module Fault Code | Inverter | Inverter018_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3020 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Internal Humidity | Inverter | Inverter018_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3021 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Humidity | Inverter | Inverter018_MODBUS.HRxxxx_humidity | Humidity | 3022 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_Comms Fault Time | Inverter | Inverter018_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Status | Inverter | Inverter018_MODBUS.HRxxxx_M1_status | Module Status | 3024 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 IR | Inverter | Inverter018_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3025 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 IS | Inverter | Inverter018_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 IT | Inverter | Inverter018_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3029 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3031 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 P | Inverter | Inverter018_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3032 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Q | Inverter | Inverter018_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3033 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3034 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3035 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M1 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3038 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Status | Inverter | Inverter018_MODBUS.HRxxxx_M2_status | Module Status | 3039 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 IR | Inverter | Inverter018_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3040 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 IS | Inverter | Inverter018_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3041 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 IT | Inverter | Inverter018_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3044 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3045 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 P | Inverter | Inverter018_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3047 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Q | Inverter | Inverter018_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3048 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3049 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3050 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3051 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3052 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M2 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Status | Inverter | Inverter018_MODBUS.HRxxxx_M3_status | Module Status | 3054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 IR | Inverter | Inverter018_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3055 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 IS | Inverter | Inverter018_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3056 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 IT | Inverter | Inverter018_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3059 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3060 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3061 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 P | Inverter | Inverter018_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3062 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Q | Inverter | Inverter018_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3063 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3064 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3065 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3066 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3067 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M3 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3068 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Status | Inverter | Inverter018_MODBUS.HRxxxx_M4_status | Module Status | 3069 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 IR | Inverter | Inverter018_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3070 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 IS | Inverter | Inverter018_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3071 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 IT | Inverter | Inverter018_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3074 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3075 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3076 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 P | Inverter | Inverter018_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3077 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Q | Inverter | Inverter018_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3078 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3079 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3080 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3081 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3082 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M4 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3083 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Status | Inverter | Inverter018_MODBUS.HRxxxx_M5_status | Module Status | 3084 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 IR | Inverter | Inverter018_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3085 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 IS | Inverter | Inverter018_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3086 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 IT | Inverter | Inverter018_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3089 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3090 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3091 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 P | Inverter | Inverter018_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3092 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Q | Inverter | Inverter018_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3093 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3094 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3095 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3096 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3097 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M5 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3098 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Status | Inverter | Inverter018_MODBUS.HRxxxx_M6_status | Module Status | 3099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 IR | Inverter | Inverter018_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 IS | Inverter | Inverter018_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 IT | Inverter | Inverter018_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 IDC | Inverter | Inverter018_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 VDCP | Inverter | Inverter018_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3104 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 VDCN | Inverter | Inverter018_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 VDC | Inverter | Inverter018_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 P | Inverter | Inverter018_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3107 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Q | Inverter | Inverter018_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3108 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Ambient Temp | Inverter | Inverter018_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3109 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Max IGBT Temp | Inverter | Inverter018_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3110 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 IO Status | Inverter | Inverter018_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3111 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Hardware Version | Inverter | Inverter018_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV018 | Daggett 3_SUB1_INV018_M6 Software Version | Inverter | Inverter018_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_A Phase Current | Inverter | inverter019_MODBUS.HR1004_i1_A | A Phase Current | 3114 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_B Phase Current | Inverter | inverter019_MODBUS.HR1005_i2_A | B Phase Current | 3115 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_C Phase Current | Inverter | inverter019_MODBUS.HR1006_i3_A | C Phase Current | 3116 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Bus Voltage | Inverter | inverter019_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3117 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV019 | Daggett 3_SUB1_INV019_Apparent Power | Inverter | inverter019_MODBUS.HR1010_s3_VA | Apparent Power | 3118 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 1 | Inverter | Inverter019_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC Input 1 | Inverter | Inverter019_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3120 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 2 | Inverter | Inverter019_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3121 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 2 | Inverter | Inverter019_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3122 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 3 | Inverter | Inverter019_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 3 | Inverter | Inverter019_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3124 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 4 | Inverter | Inverter019_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 4 | Inverter | Inverter019_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3126 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 5 | Inverter | Inverter019_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3127 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 5 | Inverter | Inverter019_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3128 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 6 | Inverter | Inverter019_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3129 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 6 | Inverter | Inverter019_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3130 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 7 | Inverter | Inverter019_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 7 | Inverter | Inverter019_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3132 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 8 | Inverter | Inverter019_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3133 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 8 | Inverter | Inverter019_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3134 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 9 | Inverter | Inverter019_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3135 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 9 | Inverter | Inverter019_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3136 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 10 | Inverter | Inverter019_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3137 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 10 | Inverter | Inverter019_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3138 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 11 | Inverter | Inverter019_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 11 | Inverter | Inverter019_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3140 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 12 | Inverter | Inverter019_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 12 | Inverter | Inverter019_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3142 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 13 | Inverter | Inverter019_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3143 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 13 | Inverter | Inverter019_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3144 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 14 | Inverter | Inverter019_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3145 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 14 | Inverter | Inverter019_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3146 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 15 | Inverter | Inverter019_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 15 | Inverter | Inverter019_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3148 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 16 | Inverter | Inverter019_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3149 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 16 | Inverter | Inverter019_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3150 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 17 | Inverter | Inverter019_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3151 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 17 | Inverter | Inverter019_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3152 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 18 | Inverter | Inverter019_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3153 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 18 | Inverter | Inverter019_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3154 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 19 | Inverter | Inverter019_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 19 | Inverter | Inverter019_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3156 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current DC Input 20 | Inverter | Inverter019_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC input 20 | Inverter | Inverter019_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3158 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current-AC | Inverter | inverter019_MODBUS.HR1007_i3Avg_A | Current-AC | 3159 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Current-DC | Inverter | inverter019_MODBUS.HR1062_idcInput_A | Current-DC | 3160 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Daily Energy Delivered | Inverter | inverter019_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3161 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power Set Point | Inverter | inverter019_MODBUS.HR0553_pRef | Real Power Set Point | 3162 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Reactive Power Set Point | Inverter | inverter019_MODBUS.HR0558_qRef | Reactive Power Set Point | 3163 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Frequency | Inverter | inverter019_MODBUS.HR1012_f3_Hz | Frequency | 3164 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV019 | Daggett 3_SUB1_INV019_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Insulation Resistance | Inverter | inverter019_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3165 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Number of DU Channels | Inverter | inverter019_MODBUS.HR0653_duChannels | Number of DU Channels | 3166 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Number of Running Modules | Inverter | inverter019_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3167 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Operating State | Inverter | inverter019_MODBUS.HR1123_currentStatus | Operating State | 3168 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Power Factor | Inverter | inverter019_MODBUS.HR1011_pf3 | Power Factor | 3169 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV019 | Daggett 3_SUB1_INV019_Ramp Down | Inverter | inverter019_MODBUS.HR0286_dropGradient_p | Ramp Down | 3170 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Ramp Up | Inverter | inverter019_MODBUS.HR0282_riseGradient_p | Ramp Up | 3171 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power Delivered | Inverter | inverter019_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3172 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Reactive Power Delivered | Inverter | inverter019_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3173 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power | 3174 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Reactive Power | Inverter | inverter019_MODBUS.HR1009_q3_kvar | Reactive Power | 3175 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Reactive Power Mode | Inverter | inverter019_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3176 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Reactive Power Set Point Percent | Inverter | inverter019_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3177 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power AC Percent | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3178 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power-AC | Inverter | inverter019_MODBUS.HR1008_p3_kW | Real Power-AC | 3179 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power-DC | Inverter | inverter019_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3180 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Air Intake | Inverter | inverter019_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3181 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Cabinet | Inverter | inverter019_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3182 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-IGBT | Inverter | inverter019_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3183 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Temperature-Module | Inverter | inverter019_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3184 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage A-B | Inverter | inverter019_MODBUS.HR1009_vRS_V | Voltage A-B | 3185 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage B-C | Inverter | inverter019_MODBUS.HR1002_vST_V | Voltage B-C | 3186 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage C-A | Inverter | inverter019_MODBUS.HR1003_vTR_V | Voltage C-A | 3187 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Voltage DC | Inverter | inverter019_MODBUS.HR1051_vdcBus_V | Voltage DC | 3188 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV019 | Daggett 3_SUB1_INV019_Fault Code 1 | Inverter | Inverter019_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Warning | Inverter | Inverter019_MODBUS.HRxxxx_currentWarning | Warning | 3190 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Internal Input Status | Inverter | Inverter019_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3191 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Internal Output Status | Inverter | Inverter019_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3192 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Module Fault Code | Inverter | Inverter019_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3193 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Internal Humidity | Inverter | Inverter019_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3194 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Humidity | Inverter | Inverter019_MODBUS.HRxxxx_humidity | Humidity | 3195 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_Comms Fault Time | Inverter | Inverter019_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Status | Inverter | Inverter019_MODBUS.HRxxxx_M1_status | Module Status | 3197 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 IR | Inverter | Inverter019_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 IS | Inverter | Inverter019_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 IT | Inverter | Inverter019_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3202 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3204 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 P | Inverter | Inverter019_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3205 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Q | Inverter | Inverter019_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3206 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3207 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3208 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3209 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M1 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3211 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Status | Inverter | Inverter019_MODBUS.HRxxxx_M2_status | Module Status | 3212 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 IR | Inverter | Inverter019_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3213 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 IS | Inverter | Inverter019_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 IT | Inverter | Inverter019_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3217 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3218 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3219 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 P | Inverter | Inverter019_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3220 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Q | Inverter | Inverter019_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3221 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3222 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3223 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3224 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3225 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M2 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3226 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Status | Inverter | Inverter019_MODBUS.HRxxxx_M3_status | Module Status | 3227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 IR | Inverter | Inverter019_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3228 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 IS | Inverter | Inverter019_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3229 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 IT | Inverter | Inverter019_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3230 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3231 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3232 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3233 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3234 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 P | Inverter | Inverter019_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3235 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Q | Inverter | Inverter019_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3236 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3237 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3238 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3239 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3240 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M3 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3241 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Status | Inverter | Inverter019_MODBUS.HRxxxx_M4_status | Module Status | 3242 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 IR | Inverter | Inverter019_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3243 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 IS | Inverter | Inverter019_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3244 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 IT | Inverter | Inverter019_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3245 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3246 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3247 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3248 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3249 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 P | Inverter | Inverter019_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3250 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Q | Inverter | Inverter019_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3251 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3252 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3253 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3254 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3255 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M4 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3256 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Status | Inverter | Inverter019_MODBUS.HRxxxx_M5_status | Module Status | 3257 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 IR | Inverter | Inverter019_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 IS | Inverter | Inverter019_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 IT | Inverter | Inverter019_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3261 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3262 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3263 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3264 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 P | Inverter | Inverter019_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3265 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Q | Inverter | Inverter019_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3266 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3267 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3268 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3270 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M5 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3271 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Status | Inverter | Inverter019_MODBUS.HRxxxx_M6_status | Module Status | 3272 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 IR | Inverter | Inverter019_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 IS | Inverter | Inverter019_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 IT | Inverter | Inverter019_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 IDC | Inverter | Inverter019_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 VDCP | Inverter | Inverter019_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3277 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 VDCN | Inverter | Inverter019_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 VDC | Inverter | Inverter019_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3279 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 P | Inverter | Inverter019_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3280 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Q | Inverter | Inverter019_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3281 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Ambient Temp | Inverter | Inverter019_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3282 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Max IGBT Temp | Inverter | Inverter019_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3283 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 IO Status | Inverter | Inverter019_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3284 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Hardware Version | Inverter | Inverter019_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV019 | Daggett 3_SUB1_INV019_M6 Software Version | Inverter | Inverter019_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_A Phase Current | Inverter | inverter020_MODBUS.HR1004_i1_A | A Phase Current | 3287 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_B Phase Current | Inverter | inverter020_MODBUS.HR1005_i2_A | B Phase Current | 3288 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_C Phase Current | Inverter | inverter020_MODBUS.HR1006_i3_A | C Phase Current | 3289 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Bus Voltage | Inverter | inverter020_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3290 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV020 | Daggett 3_SUB1_INV020_Apparent Power | Inverter | inverter020_MODBUS.HR1010_s3_VA | Apparent Power | 3291 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 1 | Inverter | Inverter020_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC Input 1 | Inverter | Inverter020_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3293 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 2 | Inverter | Inverter020_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3294 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 2 | Inverter | Inverter020_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3295 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 3 | Inverter | Inverter020_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 3 | Inverter | Inverter020_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3297 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 4 | Inverter | Inverter020_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 4 | Inverter | Inverter020_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3299 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 5 | Inverter | Inverter020_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3300 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 5 | Inverter | Inverter020_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3301 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 6 | Inverter | Inverter020_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3302 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 6 | Inverter | Inverter020_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3303 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 7 | Inverter | Inverter020_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 7 | Inverter | Inverter020_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3305 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 8 | Inverter | Inverter020_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3306 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 8 | Inverter | Inverter020_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3307 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 9 | Inverter | Inverter020_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3308 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 9 | Inverter | Inverter020_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3309 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 10 | Inverter | Inverter020_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3310 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 10 | Inverter | Inverter020_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3311 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 11 | Inverter | Inverter020_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 11 | Inverter | Inverter020_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3313 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 12 | Inverter | Inverter020_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 12 | Inverter | Inverter020_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3315 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 13 | Inverter | Inverter020_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3316 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 13 | Inverter | Inverter020_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3317 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 14 | Inverter | Inverter020_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3318 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 14 | Inverter | Inverter020_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3319 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 15 | Inverter | Inverter020_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 15 | Inverter | Inverter020_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3321 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 16 | Inverter | Inverter020_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3322 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 16 | Inverter | Inverter020_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3323 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 17 | Inverter | Inverter020_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3324 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 17 | Inverter | Inverter020_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3325 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 18 | Inverter | Inverter020_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3326 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 18 | Inverter | Inverter020_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3327 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 19 | Inverter | Inverter020_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 19 | Inverter | Inverter020_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3329 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current DC Input 20 | Inverter | Inverter020_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC input 20 | Inverter | Inverter020_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3331 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current-AC | Inverter | inverter020_MODBUS.HR1007_i3Avg_A | Current-AC | 3332 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Current-DC | Inverter | inverter020_MODBUS.HR1062_idcInput_A | Current-DC | 3333 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Daily Energy Delivered | Inverter | inverter020_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3334 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power Set Point | Inverter | inverter020_MODBUS.HR0553_pRef | Real Power Set Point | 3335 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Reactive Power Set Point | Inverter | inverter020_MODBUS.HR0558_qRef | Reactive Power Set Point | 3336 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Frequency | Inverter | inverter020_MODBUS.HR1012_f3_Hz | Frequency | 3337 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV020 | Daggett 3_SUB1_INV020_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Insulation Resistance | Inverter | inverter020_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3338 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Number of DU Channels | Inverter | inverter020_MODBUS.HR0653_duChannels | Number of DU Channels | 3339 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Number of Running Modules | Inverter | inverter020_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3340 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Operating State | Inverter | inverter020_MODBUS.HR1123_currentStatus | Operating State | 3341 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Power Factor | Inverter | inverter020_MODBUS.HR1011_pf3 | Power Factor | 3342 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV020 | Daggett 3_SUB1_INV020_Ramp Down | Inverter | inverter020_MODBUS.HR0286_dropGradient_p | Ramp Down | 3343 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Ramp Up | Inverter | inverter020_MODBUS.HR0282_riseGradient_p | Ramp Up | 3344 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power Delivered | Inverter | inverter020_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3345 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Reactive Power Delivered | Inverter | inverter020_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3346 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power | 3347 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Reactive Power | Inverter | inverter020_MODBUS.HR1009_q3_kvar | Reactive Power | 3348 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Reactive Power Mode | Inverter | inverter020_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3349 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Reactive Power Set Point Percent | Inverter | inverter020_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3350 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power AC Percent | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3351 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power-AC | Inverter | inverter020_MODBUS.HR1008_p3_kW | Real Power-AC | 3352 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power-DC | Inverter | inverter020_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3353 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Air Intake | Inverter | inverter020_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3354 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Cabinet | Inverter | inverter020_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3355 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-IGBT | Inverter | inverter020_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3356 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Temperature-Module | Inverter | inverter020_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3357 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage A-B | Inverter | inverter020_MODBUS.HR1010_vRS_V | Voltage A-B | 3358 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage B-C | Inverter | inverter020_MODBUS.HR1002_vST_V | Voltage B-C | 3359 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage C-A | Inverter | inverter020_MODBUS.HR1003_vTR_V | Voltage C-A | 3360 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Voltage DC | Inverter | inverter020_MODBUS.HR1051_vdcBus_V | Voltage DC | 3361 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV020 | Daggett 3_SUB1_INV020_Fault Code 1 | Inverter | Inverter020_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Warning | Inverter | Inverter020_MODBUS.HRxxxx_currentWarning | Warning | 3363 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Internal Input Status | Inverter | Inverter020_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3364 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Internal Output Status | Inverter | Inverter020_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3365 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Module Fault Code | Inverter | Inverter020_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3366 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Internal Humidity | Inverter | Inverter020_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3367 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Humidity | Inverter | Inverter020_MODBUS.HRxxxx_humidity | Humidity | 3368 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_Comms Fault Time | Inverter | Inverter020_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Status | Inverter | Inverter020_MODBUS.HRxxxx_M1_status | Module Status | 3370 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 IR | Inverter | Inverter020_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 IS | Inverter | Inverter020_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 IT | Inverter | Inverter020_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3375 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3377 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 P | Inverter | Inverter020_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3378 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Q | Inverter | Inverter020_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3379 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3380 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3381 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3382 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M1 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3384 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Status | Inverter | Inverter020_MODBUS.HRxxxx_M2_status | Module Status | 3385 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 IR | Inverter | Inverter020_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3386 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 IS | Inverter | Inverter020_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 IT | Inverter | Inverter020_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3390 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3391 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3392 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 P | Inverter | Inverter020_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3393 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Q | Inverter | Inverter020_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3394 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3395 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3396 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3397 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3398 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M2 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3399 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Status | Inverter | Inverter020_MODBUS.HRxxxx_M3_status | Module Status | 3400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 IR | Inverter | Inverter020_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3401 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 IS | Inverter | Inverter020_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3402 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 IT | Inverter | Inverter020_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3403 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3404 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3405 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3406 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3407 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 P | Inverter | Inverter020_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3408 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Q | Inverter | Inverter020_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3409 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3410 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3411 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3412 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3413 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M3 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3414 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Status | Inverter | Inverter020_MODBUS.HRxxxx_M4_status | Module Status | 3415 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 IR | Inverter | Inverter020_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3416 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 IS | Inverter | Inverter020_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3417 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 IT | Inverter | Inverter020_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3418 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3419 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3420 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3421 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3422 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 P | Inverter | Inverter020_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3423 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Q | Inverter | Inverter020_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3424 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3425 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3426 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3427 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3428 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M4 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3429 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Status | Inverter | Inverter020_MODBUS.HRxxxx_M5_status | Module Status | 3430 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 IR | Inverter | Inverter020_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 IS | Inverter | Inverter020_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 IT | Inverter | Inverter020_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3434 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3435 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3436 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3437 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 P | Inverter | Inverter020_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3438 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Q | Inverter | Inverter020_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3439 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3440 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3441 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3443 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M5 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3444 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Status | Inverter | Inverter020_MODBUS.HRxxxx_M6_status | Module Status | 3445 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 IR | Inverter | Inverter020_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 IS | Inverter | Inverter020_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 IT | Inverter | Inverter020_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 IDC | Inverter | Inverter020_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 VDCP | Inverter | Inverter020_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3450 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 VDCN | Inverter | Inverter020_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 VDC | Inverter | Inverter020_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3452 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 P | Inverter | Inverter020_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3453 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Q | Inverter | Inverter020_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3454 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Ambient Temp | Inverter | Inverter020_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3455 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Max IGBT Temp | Inverter | Inverter020_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3456 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 IO Status | Inverter | Inverter020_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3457 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Hardware Version | Inverter | Inverter020_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV020 | Daggett 3_SUB1_INV020_M6 Software Version | Inverter | Inverter020_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_A Phase Current | Inverter | inverter021_MODBUS.HR1004_i1_A | A Phase Current | 3460 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_B Phase Current | Inverter | inverter021_MODBUS.HR1005_i2_A | B Phase Current | 3461 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_C Phase Current | Inverter | inverter021_MODBUS.HR1006_i3_A | C Phase Current | 3462 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Bus Voltage | Inverter | inverter021_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3463 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV021 | Daggett 3_SUB1_INV021_Apparent Power | Inverter | inverter021_MODBUS.HR1010_s3_VA | Apparent Power | 3464 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 1 | Inverter | Inverter021_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC Input 1 | Inverter | Inverter021_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3466 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 2 | Inverter | Inverter021_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3467 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 2 | Inverter | Inverter021_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3468 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 3 | Inverter | Inverter021_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 3 | Inverter | Inverter021_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3470 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 4 | Inverter | Inverter021_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 4 | Inverter | Inverter021_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3472 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 5 | Inverter | Inverter021_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3473 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 5 | Inverter | Inverter021_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3474 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 6 | Inverter | Inverter021_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3475 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 6 | Inverter | Inverter021_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3476 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 7 | Inverter | Inverter021_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 7 | Inverter | Inverter021_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3478 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 8 | Inverter | Inverter021_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3479 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 8 | Inverter | Inverter021_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3480 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 9 | Inverter | Inverter021_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3481 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 9 | Inverter | Inverter021_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3482 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 10 | Inverter | Inverter021_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3483 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 10 | Inverter | Inverter021_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3484 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 11 | Inverter | Inverter021_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 11 | Inverter | Inverter021_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3486 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 12 | Inverter | Inverter021_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 12 | Inverter | Inverter021_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3488 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 13 | Inverter | Inverter021_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3489 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 13 | Inverter | Inverter021_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3490 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 14 | Inverter | Inverter021_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3491 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 14 | Inverter | Inverter021_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3492 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 15 | Inverter | Inverter021_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 15 | Inverter | Inverter021_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3494 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 16 | Inverter | Inverter021_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3495 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 16 | Inverter | Inverter021_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3496 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 17 | Inverter | Inverter021_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3497 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 17 | Inverter | Inverter021_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3498 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 18 | Inverter | Inverter021_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3499 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 18 | Inverter | Inverter021_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3500 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 19 | Inverter | Inverter021_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 19 | Inverter | Inverter021_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3502 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current DC Input 20 | Inverter | Inverter021_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC input 20 | Inverter | Inverter021_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3504 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current-AC | Inverter | inverter021_MODBUS.HR1007_i3Avg_A | Current-AC | 3505 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Current-DC | Inverter | inverter021_MODBUS.HR1062_idcInput_A | Current-DC | 3506 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Daily Energy Delivered | Inverter | inverter021_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3507 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power Set Point | Inverter | inverter021_MODBUS.HR0553_pRef | Real Power Set Point | 3508 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Reactive Power Set Point | Inverter | inverter021_MODBUS.HR0558_qRef | Reactive Power Set Point | 3509 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Frequency | Inverter | inverter021_MODBUS.HR1012_f3_Hz | Frequency | 3510 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV021 | Daggett 3_SUB1_INV021_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Insulation Resistance | Inverter | inverter021_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3511 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Number of DU Channels | Inverter | inverter021_MODBUS.HR0653_duChannels | Number of DU Channels | 3512 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Number of Running Modules | Inverter | inverter021_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3513 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Operating State | Inverter | inverter021_MODBUS.HR1123_currentStatus | Operating State | 3514 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Power Factor | Inverter | inverter021_MODBUS.HR1011_pf3 | Power Factor | 3515 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV021 | Daggett 3_SUB1_INV021_Ramp Down | Inverter | inverter021_MODBUS.HR0286_dropGradient_p | Ramp Down | 3516 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Ramp Up | Inverter | inverter021_MODBUS.HR0282_riseGradient_p | Ramp Up | 3517 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power Delivered | Inverter | inverter021_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3518 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Reactive Power Delivered | Inverter | inverter021_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3519 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power | 3520 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Reactive Power | Inverter | inverter021_MODBUS.HR1009_q3_kvar | Reactive Power | 3521 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Reactive Power Mode | Inverter | inverter021_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3522 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Reactive Power Set Point Percent | Inverter | inverter021_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3523 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power AC Percent | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3524 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power-AC | Inverter | inverter021_MODBUS.HR1008_p3_kW | Real Power-AC | 3525 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power-DC | Inverter | inverter021_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3526 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Air Intake | Inverter | inverter021_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3527 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Cabinet | Inverter | inverter021_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3528 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-IGBT | Inverter | inverter021_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3529 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Temperature-Module | Inverter | inverter021_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3530 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage A-B | Inverter | inverter021_MODBUS.HR1001_vRS_V | Voltage A-B | 3531 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage B-C | Inverter | inverter021_MODBUS.HR1002_vST_V | Voltage B-C | 3532 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage C-A | Inverter | inverter021_MODBUS.HR1003_vTR_V | Voltage C-A | 3533 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Voltage DC | Inverter | inverter021_MODBUS.HR1051_vdcBus_V | Voltage DC | 3534 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV021 | Daggett 3_SUB1_INV021_Fault Code 1 | Inverter | Inverter021_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Warning | Inverter | Inverter021_MODBUS.HRxxxx_currentWarning | Warning | 3536 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Internal Input Status | Inverter | Inverter021_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3537 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Internal Output Status | Inverter | Inverter021_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3538 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Module Fault Code | Inverter | Inverter021_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3539 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Internal Humidity | Inverter | Inverter021_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3540 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Humidity | Inverter | Inverter021_MODBUS.HRxxxx_humidity | Humidity | 3541 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_Comms Fault Time | Inverter | Inverter021_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Status | Inverter | Inverter021_MODBUS.HRxxxx_M1_status | Module Status | 3543 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 IR | Inverter | Inverter021_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 IS | Inverter | Inverter021_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 IT | Inverter | Inverter021_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3548 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3550 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 P | Inverter | Inverter021_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3551 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Q | Inverter | Inverter021_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3552 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3553 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3554 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3555 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M1 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3557 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Status | Inverter | Inverter021_MODBUS.HRxxxx_M2_status | Module Status | 3558 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 IR | Inverter | Inverter021_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3559 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 IS | Inverter | Inverter021_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 IT | Inverter | Inverter021_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3563 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3564 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3565 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 P | Inverter | Inverter021_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3566 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Q | Inverter | Inverter021_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3567 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3568 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3569 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3570 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3571 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M2 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3572 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Status | Inverter | Inverter021_MODBUS.HRxxxx_M3_status | Module Status | 3573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 IR | Inverter | Inverter021_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3574 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 IS | Inverter | Inverter021_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3575 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 IT | Inverter | Inverter021_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3576 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3577 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3578 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3579 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3580 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 P | Inverter | Inverter021_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3581 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Q | Inverter | Inverter021_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3582 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3583 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3584 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3585 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3586 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M3 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3587 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Status | Inverter | Inverter021_MODBUS.HRxxxx_M4_status | Module Status | 3588 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 IR | Inverter | Inverter021_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3589 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 IS | Inverter | Inverter021_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3590 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 IT | Inverter | Inverter021_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3591 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3592 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3593 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3594 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3595 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 P | Inverter | Inverter021_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3596 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Q | Inverter | Inverter021_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3597 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3598 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3599 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3600 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3601 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M4 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3602 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Status | Inverter | Inverter021_MODBUS.HRxxxx_M5_status | Module Status | 3603 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 IR | Inverter | Inverter021_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 IS | Inverter | Inverter021_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 IT | Inverter | Inverter021_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3607 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3608 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3609 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3610 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 P | Inverter | Inverter021_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3611 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Q | Inverter | Inverter021_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3612 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3613 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3614 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3616 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M5 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3617 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Status | Inverter | Inverter021_MODBUS.HRxxxx_M6_status | Module Status | 3618 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 IR | Inverter | Inverter021_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 IS | Inverter | Inverter021_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 IT | Inverter | Inverter021_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 IDC | Inverter | Inverter021_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 VDCP | Inverter | Inverter021_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3623 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 VDCN | Inverter | Inverter021_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 VDC | Inverter | Inverter021_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3625 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 P | Inverter | Inverter021_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3626 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Q | Inverter | Inverter021_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3627 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Ambient Temp | Inverter | Inverter021_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3628 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Max IGBT Temp | Inverter | Inverter021_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3629 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 IO Status | Inverter | Inverter021_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3630 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Hardware Version | Inverter | Inverter021_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV021 | Daggett 3_SUB1_INV021_M6 Software Version | Inverter | Inverter021_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_A Phase Current | Inverter | inverter022_MODBUS.HR1004_i1_A | A Phase Current | 3633 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_B Phase Current | Inverter | inverter022_MODBUS.HR1005_i2_A | B Phase Current | 3634 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_C Phase Current | Inverter | inverter022_MODBUS.HR1006_i3_A | C Phase Current | 3635 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Bus Voltage | Inverter | inverter022_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3636 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV022 | Daggett 3_SUB1_INV022_Apparent Power | Inverter | inverter022_MODBUS.HR1010_s3_VA | Apparent Power | 3637 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 1 | Inverter | Inverter022_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC Input 1 | Inverter | Inverter022_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3639 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 2 | Inverter | Inverter022_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3640 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 2 | Inverter | Inverter022_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3641 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 3 | Inverter | Inverter022_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 3 | Inverter | Inverter022_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3643 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 4 | Inverter | Inverter022_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 4 | Inverter | Inverter022_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3645 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 5 | Inverter | Inverter022_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3646 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 5 | Inverter | Inverter022_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3647 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 6 | Inverter | Inverter022_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3648 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 6 | Inverter | Inverter022_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3649 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 7 | Inverter | Inverter022_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 7 | Inverter | Inverter022_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3651 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 8 | Inverter | Inverter022_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3652 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 8 | Inverter | Inverter022_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3653 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 9 | Inverter | Inverter022_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3654 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 9 | Inverter | Inverter022_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3655 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 10 | Inverter | Inverter022_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3656 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 10 | Inverter | Inverter022_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3657 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 11 | Inverter | Inverter022_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 11 | Inverter | Inverter022_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3659 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 12 | Inverter | Inverter022_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 12 | Inverter | Inverter022_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3661 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 13 | Inverter | Inverter022_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3662 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 13 | Inverter | Inverter022_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3663 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 14 | Inverter | Inverter022_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3664 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 14 | Inverter | Inverter022_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3665 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 15 | Inverter | Inverter022_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 15 | Inverter | Inverter022_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3667 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 16 | Inverter | Inverter022_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3668 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 16 | Inverter | Inverter022_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3669 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 17 | Inverter | Inverter022_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3670 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 17 | Inverter | Inverter022_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3671 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 18 | Inverter | Inverter022_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3672 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 18 | Inverter | Inverter022_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3673 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 19 | Inverter | Inverter022_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 19 | Inverter | Inverter022_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3675 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current DC Input 20 | Inverter | Inverter022_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC input 20 | Inverter | Inverter022_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3677 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current-AC | Inverter | inverter022_MODBUS.HR1007_i3Avg_A | Current-AC | 3678 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Current-DC | Inverter | inverter022_MODBUS.HR1062_idcInput_A | Current-DC | 3679 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Daily Energy Delivered | Inverter | inverter022_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3680 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power Set Point | Inverter | inverter022_MODBUS.HR0553_pRef | Real Power Set Point | 3681 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Reactive Power Set Point | Inverter | inverter022_MODBUS.HR0558_qRef | Reactive Power Set Point | 3682 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Frequency | Inverter | inverter022_MODBUS.HR1012_f3_Hz | Frequency | 3683 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV022 | Daggett 3_SUB1_INV022_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Insulation Resistance | Inverter | inverter022_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3684 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Number of DU Channels | Inverter | inverter022_MODBUS.HR0653_duChannels | Number of DU Channels | 3685 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Number of Running Modules | Inverter | inverter022_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3686 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Operating State | Inverter | inverter022_MODBUS.HR1123_currentStatus | Operating State | 3687 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Power Factor | Inverter | inverter022_MODBUS.HR1011_pf3 | Power Factor | 3688 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV022 | Daggett 3_SUB1_INV022_Ramp Down | Inverter | inverter022_MODBUS.HR0286_dropGradient_p | Ramp Down | 3689 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Ramp Up | Inverter | inverter022_MODBUS.HR0282_riseGradient_p | Ramp Up | 3690 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power Delivered | Inverter | inverter022_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3691 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Reactive Power Delivered | Inverter | inverter022_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3692 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power | 3693 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Reactive Power | Inverter | inverter022_MODBUS.HR1009_q3_kvar | Reactive Power | 3694 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Reactive Power Mode | Inverter | inverter022_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3695 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Reactive Power Set Point Percent | Inverter | inverter022_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3696 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power AC Percent | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3697 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power-AC | Inverter | inverter022_MODBUS.HR1008_p3_kW | Real Power-AC | 3698 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power-DC | Inverter | inverter022_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3699 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Air Intake | Inverter | inverter022_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3700 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Cabinet | Inverter | inverter022_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3701 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-IGBT | Inverter | inverter022_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3702 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Temperature-Module | Inverter | inverter022_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3703 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage A-B | Inverter | inverter022_MODBUS.HR1002_vRS_V | Voltage A-B | 3704 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage B-C | Inverter | inverter022_MODBUS.HR1002_vST_V | Voltage B-C | 3705 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage C-A | Inverter | inverter022_MODBUS.HR1003_vTR_V | Voltage C-A | 3706 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Voltage DC | Inverter | inverter022_MODBUS.HR1051_vdcBus_V | Voltage DC | 3707 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV022 | Daggett 3_SUB1_INV022_Fault Code 1 | Inverter | Inverter022_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Warning | Inverter | Inverter022_MODBUS.HRxxxx_currentWarning | Warning | 3709 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Internal Input Status | Inverter | Inverter022_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3710 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Internal Output Status | Inverter | Inverter022_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3711 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Module Fault Code | Inverter | Inverter022_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3712 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Internal Humidity | Inverter | Inverter022_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3713 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Humidity | Inverter | Inverter022_MODBUS.HRxxxx_humidity | Humidity | 3714 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_Comms Fault Time | Inverter | Inverter022_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Status | Inverter | Inverter022_MODBUS.HRxxxx_M1_status | Module Status | 3716 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 IR | Inverter | Inverter022_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 IS | Inverter | Inverter022_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 IT | Inverter | Inverter022_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3721 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3723 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 P | Inverter | Inverter022_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3724 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Q | Inverter | Inverter022_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3725 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3726 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3727 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3728 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M1 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3730 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Status | Inverter | Inverter022_MODBUS.HRxxxx_M2_status | Module Status | 3731 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 IR | Inverter | Inverter022_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3732 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 IS | Inverter | Inverter022_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 IT | Inverter | Inverter022_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3736 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3737 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3738 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 P | Inverter | Inverter022_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3739 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Q | Inverter | Inverter022_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3740 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3741 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3742 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3743 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3744 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M2 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3745 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Status | Inverter | Inverter022_MODBUS.HRxxxx_M3_status | Module Status | 3746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 IR | Inverter | Inverter022_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3747 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 IS | Inverter | Inverter022_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3748 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 IT | Inverter | Inverter022_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3749 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3750 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3751 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3752 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3753 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 P | Inverter | Inverter022_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3754 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Q | Inverter | Inverter022_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3755 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3756 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3757 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3758 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3759 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M3 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3760 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Status | Inverter | Inverter022_MODBUS.HRxxxx_M4_status | Module Status | 3761 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 IR | Inverter | Inverter022_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3762 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 IS | Inverter | Inverter022_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3763 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 IT | Inverter | Inverter022_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3764 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3765 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3766 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3767 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3768 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 P | Inverter | Inverter022_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3769 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Q | Inverter | Inverter022_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3770 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3771 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3772 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3773 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3774 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M4 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3775 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Status | Inverter | Inverter022_MODBUS.HRxxxx_M5_status | Module Status | 3776 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 IR | Inverter | Inverter022_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 IS | Inverter | Inverter022_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 IT | Inverter | Inverter022_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3780 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3781 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3782 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3783 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 P | Inverter | Inverter022_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3784 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Q | Inverter | Inverter022_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3785 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3786 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3787 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3789 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M5 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3790 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Status | Inverter | Inverter022_MODBUS.HRxxxx_M6_status | Module Status | 3791 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 IR | Inverter | Inverter022_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 IS | Inverter | Inverter022_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 IT | Inverter | Inverter022_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 IDC | Inverter | Inverter022_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 VDCP | Inverter | Inverter022_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3796 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 VDCN | Inverter | Inverter022_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 VDC | Inverter | Inverter022_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3798 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 P | Inverter | Inverter022_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3799 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Q | Inverter | Inverter022_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3800 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Ambient Temp | Inverter | Inverter022_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3801 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Max IGBT Temp | Inverter | Inverter022_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3802 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 IO Status | Inverter | Inverter022_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3803 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Hardware Version | Inverter | Inverter022_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV022 | Daggett 3_SUB1_INV022_M6 Software Version | Inverter | Inverter022_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_A Phase Current | Inverter | inverter023_MODBUS.HR1004_i1_A | A Phase Current | 3806 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_B Phase Current | Inverter | inverter023_MODBUS.HR1005_i2_A | B Phase Current | 3807 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_C Phase Current | Inverter | inverter023_MODBUS.HR1006_i3_A | C Phase Current | 3808 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Bus Voltage | Inverter | inverter023_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3809 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV023 | Daggett 3_SUB1_INV023_Apparent Power | Inverter | inverter023_MODBUS.HR1010_s3_VA | Apparent Power | 3810 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 1 | Inverter | Inverter023_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC Input 1 | Inverter | Inverter023_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3812 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 2 | Inverter | Inverter023_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3813 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 2 | Inverter | Inverter023_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3814 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 3 | Inverter | Inverter023_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 3 | Inverter | Inverter023_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3816 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 4 | Inverter | Inverter023_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 4 | Inverter | Inverter023_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3818 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 5 | Inverter | Inverter023_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3819 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 5 | Inverter | Inverter023_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3820 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 6 | Inverter | Inverter023_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3821 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 6 | Inverter | Inverter023_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3822 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 7 | Inverter | Inverter023_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 7 | Inverter | Inverter023_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3824 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 8 | Inverter | Inverter023_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3825 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 8 | Inverter | Inverter023_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3826 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 9 | Inverter | Inverter023_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3827 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 9 | Inverter | Inverter023_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3828 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 10 | Inverter | Inverter023_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3829 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 10 | Inverter | Inverter023_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3830 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 11 | Inverter | Inverter023_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 11 | Inverter | Inverter023_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3832 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 12 | Inverter | Inverter023_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 12 | Inverter | Inverter023_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3834 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 13 | Inverter | Inverter023_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3835 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 13 | Inverter | Inverter023_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3836 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 14 | Inverter | Inverter023_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3837 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 14 | Inverter | Inverter023_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3838 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 15 | Inverter | Inverter023_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 15 | Inverter | Inverter023_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3840 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 16 | Inverter | Inverter023_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3841 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 16 | Inverter | Inverter023_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3842 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 17 | Inverter | Inverter023_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3843 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 17 | Inverter | Inverter023_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3844 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 18 | Inverter | Inverter023_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3845 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 18 | Inverter | Inverter023_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3846 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 19 | Inverter | Inverter023_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 19 | Inverter | Inverter023_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3848 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current DC Input 20 | Inverter | Inverter023_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC input 20 | Inverter | Inverter023_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3850 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current-AC | Inverter | inverter023_MODBUS.HR1007_i3Avg_A | Current-AC | 3851 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Current-DC | Inverter | inverter023_MODBUS.HR1062_idcInput_A | Current-DC | 3852 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Daily Energy Delivered | Inverter | inverter023_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3853 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power Set Point | Inverter | inverter023_MODBUS.HR0553_pRef | Real Power Set Point | 3854 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Reactive Power Set Point | Inverter | inverter023_MODBUS.HR0558_qRef | Reactive Power Set Point | 3855 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Frequency | Inverter | inverter023_MODBUS.HR1012_f3_Hz | Frequency | 3856 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV023 | Daggett 3_SUB1_INV023_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Insulation Resistance | Inverter | inverter023_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3857 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Number of DU Channels | Inverter | inverter023_MODBUS.HR0653_duChannels | Number of DU Channels | 3858 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Number of Running Modules | Inverter | inverter023_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3859 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Operating State | Inverter | inverter023_MODBUS.HR1123_currentStatus | Operating State | 3860 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Power Factor | Inverter | inverter023_MODBUS.HR1011_pf3 | Power Factor | 3861 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV023 | Daggett 3_SUB1_INV023_Ramp Down | Inverter | inverter023_MODBUS.HR0286_dropGradient_p | Ramp Down | 3862 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Ramp Up | Inverter | inverter023_MODBUS.HR0282_riseGradient_p | Ramp Up | 3863 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power Delivered | Inverter | inverter023_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3864 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Reactive Power Delivered | Inverter | inverter023_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3865 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power | 3866 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Reactive Power | Inverter | inverter023_MODBUS.HR1009_q3_kvar | Reactive Power | 3867 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Reactive Power Mode | Inverter | inverter023_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3868 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Reactive Power Set Point Percent | Inverter | inverter023_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3869 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power AC Percent | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3870 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power-AC | Inverter | inverter023_MODBUS.HR1008_p3_kW | Real Power-AC | 3871 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power-DC | Inverter | inverter023_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3872 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Air Intake | Inverter | inverter023_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3873 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Cabinet | Inverter | inverter023_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3874 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-IGBT | Inverter | inverter023_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3875 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Temperature-Module | Inverter | inverter023_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3876 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage A-B | Inverter | inverter023_MODBUS.HR1003_vRS_V | Voltage A-B | 3877 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage B-C | Inverter | inverter023_MODBUS.HR1002_vST_V | Voltage B-C | 3878 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage C-A | Inverter | inverter023_MODBUS.HR1003_vTR_V | Voltage C-A | 3879 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Voltage DC | Inverter | inverter023_MODBUS.HR1051_vdcBus_V | Voltage DC | 3880 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV023 | Daggett 3_SUB1_INV023_Fault Code 1 | Inverter | Inverter023_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Warning | Inverter | Inverter023_MODBUS.HRxxxx_currentWarning | Warning | 3882 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Internal Input Status | Inverter | Inverter023_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3883 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Internal Output Status | Inverter | Inverter023_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3884 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Module Fault Code | Inverter | Inverter023_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3885 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Internal Humidity | Inverter | Inverter023_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3886 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Humidity | Inverter | Inverter023_MODBUS.HRxxxx_humidity | Humidity | 3887 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_Comms Fault Time | Inverter | Inverter023_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Status | Inverter | Inverter023_MODBUS.HRxxxx_M1_status | Module Status | 3889 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 IR | Inverter | Inverter023_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 IS | Inverter | Inverter023_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 IT | Inverter | Inverter023_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3894 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3896 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 P | Inverter | Inverter023_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3897 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Q | Inverter | Inverter023_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3898 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3899 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3900 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3901 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M1 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3903 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Status | Inverter | Inverter023_MODBUS.HRxxxx_M2_status | Module Status | 3904 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 IR | Inverter | Inverter023_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3905 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 IS | Inverter | Inverter023_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 IT | Inverter | Inverter023_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3909 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3910 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3911 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 P | Inverter | Inverter023_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3912 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Q | Inverter | Inverter023_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3913 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3914 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3915 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3916 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3917 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M2 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3918 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Status | Inverter | Inverter023_MODBUS.HRxxxx_M3_status | Module Status | 3919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 IR | Inverter | Inverter023_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3920 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 IS | Inverter | Inverter023_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3921 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 IT | Inverter | Inverter023_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3922 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3923 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3924 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3925 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3926 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 P | Inverter | Inverter023_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3927 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Q | Inverter | Inverter023_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3928 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3929 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3930 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3931 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3932 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M3 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3933 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Status | Inverter | Inverter023_MODBUS.HRxxxx_M4_status | Module Status | 3934 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 IR | Inverter | Inverter023_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3935 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 IS | Inverter | Inverter023_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3936 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 IT | Inverter | Inverter023_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3937 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3938 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3939 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3940 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3941 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 P | Inverter | Inverter023_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3942 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Q | Inverter | Inverter023_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3943 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3944 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3945 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3946 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3947 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M4 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3948 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Status | Inverter | Inverter023_MODBUS.HRxxxx_M5_status | Module Status | 3949 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 IR | Inverter | Inverter023_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 IS | Inverter | Inverter023_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 IT | Inverter | Inverter023_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3953 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3954 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3955 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3956 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 P | Inverter | Inverter023_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3957 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Q | Inverter | Inverter023_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3958 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3959 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3960 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3962 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M5 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3963 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Status | Inverter | Inverter023_MODBUS.HRxxxx_M6_status | Module Status | 3964 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 IR | Inverter | Inverter023_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 IS | Inverter | Inverter023_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 IT | Inverter | Inverter023_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 IDC | Inverter | Inverter023_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 VDCP | Inverter | Inverter023_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3969 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 VDCN | Inverter | Inverter023_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 VDC | Inverter | Inverter023_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3971 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 P | Inverter | Inverter023_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3972 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Q | Inverter | Inverter023_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3973 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Ambient Temp | Inverter | Inverter023_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3974 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Max IGBT Temp | Inverter | Inverter023_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3975 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 IO Status | Inverter | Inverter023_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3976 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Hardware Version | Inverter | Inverter023_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV023 | Daggett 3_SUB1_INV023_M6 Software Version | Inverter | Inverter023_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_A Phase Current | Inverter | inverter024_MODBUS.HR1004_i1_A | A Phase Current | 3979 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_B Phase Current | Inverter | inverter024_MODBUS.HR1005_i2_A | B Phase Current | 3980 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_C Phase Current | Inverter | inverter024_MODBUS.HR1006_i3_A | C Phase Current | 3981 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Bus Voltage | Inverter | inverter024_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3982 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV024 | Daggett 3_SUB1_INV024_Apparent Power | Inverter | inverter024_MODBUS.HR1010_s3_VA | Apparent Power | 3983 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 1 | Inverter | Inverter024_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC Input 1 | Inverter | Inverter024_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3985 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 2 | Inverter | Inverter024_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3986 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 2 | Inverter | Inverter024_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3987 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 3 | Inverter | Inverter024_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 3 | Inverter | Inverter024_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3989 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 4 | Inverter | Inverter024_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 4 | Inverter | Inverter024_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3991 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 5 | Inverter | Inverter024_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3992 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 5 | Inverter | Inverter024_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3993 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 6 | Inverter | Inverter024_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3994 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 6 | Inverter | Inverter024_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3995 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 7 | Inverter | Inverter024_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 7 | Inverter | Inverter024_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3997 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 8 | Inverter | Inverter024_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3998 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 8 | Inverter | Inverter024_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3999 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 9 | Inverter | Inverter024_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4000 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 9 | Inverter | Inverter024_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4001 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 10 | Inverter | Inverter024_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4002 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 10 | Inverter | Inverter024_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4003 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 11 | Inverter | Inverter024_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 11 | Inverter | Inverter024_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4005 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 12 | Inverter | Inverter024_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 12 | Inverter | Inverter024_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4007 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 13 | Inverter | Inverter024_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4008 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 13 | Inverter | Inverter024_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4009 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 14 | Inverter | Inverter024_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4010 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 14 | Inverter | Inverter024_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4011 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 15 | Inverter | Inverter024_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 15 | Inverter | Inverter024_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4013 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 16 | Inverter | Inverter024_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4014 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 16 | Inverter | Inverter024_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4015 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 17 | Inverter | Inverter024_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4016 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 17 | Inverter | Inverter024_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4017 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 18 | Inverter | Inverter024_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4018 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 18 | Inverter | Inverter024_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4019 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 19 | Inverter | Inverter024_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 19 | Inverter | Inverter024_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4021 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current DC Input 20 | Inverter | Inverter024_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC input 20 | Inverter | Inverter024_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4023 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current-AC | Inverter | inverter024_MODBUS.HR1007_i3Avg_A | Current-AC | 4024 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Current-DC | Inverter | inverter024_MODBUS.HR1062_idcInput_A | Current-DC | 4025 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Daily Energy Delivered | Inverter | inverter024_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4026 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power Set Point | Inverter | inverter024_MODBUS.HR0553_pRef | Real Power Set Point | 4027 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Reactive Power Set Point | Inverter | inverter024_MODBUS.HR0558_qRef | Reactive Power Set Point | 4028 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Frequency | Inverter | inverter024_MODBUS.HR1012_f3_Hz | Frequency | 4029 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV024 | Daggett 3_SUB1_INV024_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Insulation Resistance | Inverter | inverter024_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4030 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Number of DU Channels | Inverter | inverter024_MODBUS.HR0653_duChannels | Number of DU Channels | 4031 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Number of Running Modules | Inverter | inverter024_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4032 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Operating State | Inverter | inverter024_MODBUS.HR1123_currentStatus | Operating State | 4033 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Power Factor | Inverter | inverter024_MODBUS.HR1011_pf3 | Power Factor | 4034 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV024 | Daggett 3_SUB1_INV024_Ramp Down | Inverter | inverter024_MODBUS.HR0286_dropGradient_p | Ramp Down | 4035 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Ramp Up | Inverter | inverter024_MODBUS.HR0282_riseGradient_p | Ramp Up | 4036 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power Delivered | Inverter | inverter024_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4037 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Reactive Power Delivered | Inverter | inverter024_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4038 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power | 4039 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Reactive Power | Inverter | inverter024_MODBUS.HR1009_q3_kvar | Reactive Power | 4040 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Reactive Power Mode | Inverter | inverter024_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4041 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Reactive Power Set Point Percent | Inverter | inverter024_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4042 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power AC Percent | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4043 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power-AC | Inverter | inverter024_MODBUS.HR1008_p3_kW | Real Power-AC | 4044 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power-DC | Inverter | inverter024_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4045 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Air Intake | Inverter | inverter024_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4046 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Cabinet | Inverter | inverter024_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4047 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-IGBT | Inverter | inverter024_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4048 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Temperature-Module | Inverter | inverter024_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4049 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage A-B | Inverter | inverter024_MODBUS.HR1004_vRS_V | Voltage A-B | 4050 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage B-C | Inverter | inverter024_MODBUS.HR1002_vST_V | Voltage B-C | 4051 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage C-A | Inverter | inverter024_MODBUS.HR1003_vTR_V | Voltage C-A | 4052 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Voltage DC | Inverter | inverter024_MODBUS.HR1051_vdcBus_V | Voltage DC | 4053 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV024 | Daggett 3_SUB1_INV024_Fault Code 1 | Inverter | Inverter024_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Warning | Inverter | Inverter024_MODBUS.HRxxxx_currentWarning | Warning | 4055 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Internal Input Status | Inverter | Inverter024_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4056 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Internal Output Status | Inverter | Inverter024_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4057 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Module Fault Code | Inverter | Inverter024_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4058 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Internal Humidity | Inverter | Inverter024_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4059 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Humidity | Inverter | Inverter024_MODBUS.HRxxxx_humidity | Humidity | 4060 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_Comms Fault Time | Inverter | Inverter024_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Status | Inverter | Inverter024_MODBUS.HRxxxx_M1_status | Module Status | 4062 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 IR | Inverter | Inverter024_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 IS | Inverter | Inverter024_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 IT | Inverter | Inverter024_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4067 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4069 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 P | Inverter | Inverter024_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4070 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Q | Inverter | Inverter024_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4071 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4072 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4073 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4074 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M1 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4076 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Status | Inverter | Inverter024_MODBUS.HRxxxx_M2_status | Module Status | 4077 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 IR | Inverter | Inverter024_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4078 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 IS | Inverter | Inverter024_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 IT | Inverter | Inverter024_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4082 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4083 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4084 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 P | Inverter | Inverter024_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4085 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Q | Inverter | Inverter024_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4086 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4087 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4088 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4089 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4090 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M2 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4091 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Status | Inverter | Inverter024_MODBUS.HRxxxx_M3_status | Module Status | 4092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 IR | Inverter | Inverter024_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4093 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 IS | Inverter | Inverter024_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4094 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 IT | Inverter | Inverter024_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4095 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4096 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4097 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4098 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4099 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 P | Inverter | Inverter024_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4100 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Q | Inverter | Inverter024_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4101 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4102 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4103 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4104 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4105 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M3 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4106 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Status | Inverter | Inverter024_MODBUS.HRxxxx_M4_status | Module Status | 4107 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 IR | Inverter | Inverter024_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4108 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 IS | Inverter | Inverter024_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4109 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 IT | Inverter | Inverter024_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4110 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4111 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4112 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4113 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4114 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 P | Inverter | Inverter024_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4115 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Q | Inverter | Inverter024_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4116 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4117 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4118 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4119 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4120 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M4 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4121 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Status | Inverter | Inverter024_MODBUS.HRxxxx_M5_status | Module Status | 4122 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 IR | Inverter | Inverter024_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 IS | Inverter | Inverter024_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 IT | Inverter | Inverter024_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4126 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4127 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4128 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4129 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 P | Inverter | Inverter024_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4130 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Q | Inverter | Inverter024_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4131 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4132 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4133 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4135 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M5 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4136 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Status | Inverter | Inverter024_MODBUS.HRxxxx_M6_status | Module Status | 4137 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 IR | Inverter | Inverter024_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4138 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 IS | Inverter | Inverter024_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 IT | Inverter | Inverter024_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 IDC | Inverter | Inverter024_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 VDCP | Inverter | Inverter024_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4142 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 VDCN | Inverter | Inverter024_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 VDC | Inverter | Inverter024_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4144 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 P | Inverter | Inverter024_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4145 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Q | Inverter | Inverter024_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4146 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Ambient Temp | Inverter | Inverter024_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4147 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Max IGBT Temp | Inverter | Inverter024_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4148 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 IO Status | Inverter | Inverter024_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4149 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Hardware Version | Inverter | Inverter024_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV024 | Daggett 3_SUB1_INV024_M6 Software Version | Inverter | Inverter024_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_A Phase Current | Inverter | inverter025_MODBUS.HR1004_i1_A | A Phase Current | 4152 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_B Phase Current | Inverter | inverter025_MODBUS.HR1005_i2_A | B Phase Current | 4153 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_C Phase Current | Inverter | inverter025_MODBUS.HR1006_i3_A | C Phase Current | 4154 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Bus Voltage | Inverter | inverter025_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4155 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV025 | Daggett 3_SUB1_INV025_Apparent Power | Inverter | inverter025_MODBUS.HR1010_s3_VA | Apparent Power | 4156 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 1 | Inverter | Inverter025_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC Input 1 | Inverter | Inverter025_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4158 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 2 | Inverter | Inverter025_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4159 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 2 | Inverter | Inverter025_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4160 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 3 | Inverter | Inverter025_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 3 | Inverter | Inverter025_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4162 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 4 | Inverter | Inverter025_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 4 | Inverter | Inverter025_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4164 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 5 | Inverter | Inverter025_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4165 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 5 | Inverter | Inverter025_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4166 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 6 | Inverter | Inverter025_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4167 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 6 | Inverter | Inverter025_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4168 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 7 | Inverter | Inverter025_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 7 | Inverter | Inverter025_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4170 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 8 | Inverter | Inverter025_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4171 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 8 | Inverter | Inverter025_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4172 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 9 | Inverter | Inverter025_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4173 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 9 | Inverter | Inverter025_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4174 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 10 | Inverter | Inverter025_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4175 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 10 | Inverter | Inverter025_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4176 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 11 | Inverter | Inverter025_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 11 | Inverter | Inverter025_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4178 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 12 | Inverter | Inverter025_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 12 | Inverter | Inverter025_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4180 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 13 | Inverter | Inverter025_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4181 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 13 | Inverter | Inverter025_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4182 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 14 | Inverter | Inverter025_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4183 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 14 | Inverter | Inverter025_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4184 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 15 | Inverter | Inverter025_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 15 | Inverter | Inverter025_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4186 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 16 | Inverter | Inverter025_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4187 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 16 | Inverter | Inverter025_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4188 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 17 | Inverter | Inverter025_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4189 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 17 | Inverter | Inverter025_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4190 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 18 | Inverter | Inverter025_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4191 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 18 | Inverter | Inverter025_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4192 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 19 | Inverter | Inverter025_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 19 | Inverter | Inverter025_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4194 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current DC Input 20 | Inverter | Inverter025_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC input 20 | Inverter | Inverter025_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4196 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current-AC | Inverter | inverter025_MODBUS.HR1007_i3Avg_A | Current-AC | 4197 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Current-DC | Inverter | inverter025_MODBUS.HR1062_idcInput_A | Current-DC | 4198 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Daily Energy Delivered | Inverter | inverter025_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4199 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power Set Point | Inverter | inverter025_MODBUS.HR0553_pRef | Real Power Set Point | 4200 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Reactive Power Set Point | Inverter | inverter025_MODBUS.HR0558_qRef | Reactive Power Set Point | 4201 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Frequency | Inverter | inverter025_MODBUS.HR1012_f3_Hz | Frequency | 4202 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV025 | Daggett 3_SUB1_INV025_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Insulation Resistance | Inverter | inverter025_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4203 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Number of DU Channels | Inverter | inverter025_MODBUS.HR0653_duChannels | Number of DU Channels | 4204 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Number of Running Modules | Inverter | inverter025_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4205 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Operating State | Inverter | inverter025_MODBUS.HR1123_currentStatus | Operating State | 4206 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Power Factor | Inverter | inverter025_MODBUS.HR1011_pf3 | Power Factor | 4207 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV025 | Daggett 3_SUB1_INV025_Ramp Down | Inverter | inverter025_MODBUS.HR0286_dropGradient_p | Ramp Down | 4208 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Ramp Up | Inverter | inverter025_MODBUS.HR0282_riseGradient_p | Ramp Up | 4209 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power Delivered | Inverter | inverter025_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4210 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Reactive Power Delivered | Inverter | inverter025_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4211 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power | 4212 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Reactive Power | Inverter | inverter025_MODBUS.HR1009_q3_kvar | Reactive Power | 4213 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Reactive Power Mode | Inverter | inverter025_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4214 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Reactive Power Set Point Percent | Inverter | inverter025_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4215 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power AC Percent | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4216 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power-AC | Inverter | inverter025_MODBUS.HR1008_p3_kW | Real Power-AC | 4217 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power-DC | Inverter | inverter025_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4218 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Air Intake | Inverter | inverter025_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4219 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Cabinet | Inverter | inverter025_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4220 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-IGBT | Inverter | inverter025_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4221 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Temperature-Module | Inverter | inverter025_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4222 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage A-B | Inverter | inverter025_MODBUS.HR1005_vRS_V | Voltage A-B | 4223 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage B-C | Inverter | inverter025_MODBUS.HR1002_vST_V | Voltage B-C | 4224 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage C-A | Inverter | inverter025_MODBUS.HR1003_vTR_V | Voltage C-A | 4225 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Voltage DC | Inverter | inverter025_MODBUS.HR1051_vdcBus_V | Voltage DC | 4226 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV025 | Daggett 3_SUB1_INV025_Fault Code 1 | Inverter | Inverter025_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Warning | Inverter | Inverter025_MODBUS.HRxxxx_currentWarning | Warning | 4228 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Internal Input Status | Inverter | Inverter025_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4229 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Internal Output Status | Inverter | Inverter025_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4230 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Module Fault Code | Inverter | Inverter025_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4231 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Internal Humidity | Inverter | Inverter025_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4232 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Humidity | Inverter | Inverter025_MODBUS.HRxxxx_humidity | Humidity | 4233 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_Comms Fault Time | Inverter | Inverter025_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Status | Inverter | Inverter025_MODBUS.HRxxxx_M1_status | Module Status | 4235 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 IR | Inverter | Inverter025_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 IS | Inverter | Inverter025_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 IT | Inverter | Inverter025_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4240 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4242 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 P | Inverter | Inverter025_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4243 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Q | Inverter | Inverter025_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4244 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4245 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4246 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4247 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M1 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Status | Inverter | Inverter025_MODBUS.HRxxxx_M2_status | Module Status | 4250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 IR | Inverter | Inverter025_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4251 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 IS | Inverter | Inverter025_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 IT | Inverter | Inverter025_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4255 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4256 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4257 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 P | Inverter | Inverter025_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4258 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Q | Inverter | Inverter025_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4259 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4260 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4261 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4262 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4263 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M2 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4264 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Status | Inverter | Inverter025_MODBUS.HRxxxx_M3_status | Module Status | 4265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 IR | Inverter | Inverter025_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4266 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 IS | Inverter | Inverter025_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4267 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 IT | Inverter | Inverter025_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4268 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4269 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4270 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4271 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4272 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 P | Inverter | Inverter025_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4273 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Q | Inverter | Inverter025_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4274 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4275 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4276 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4277 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4278 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M3 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4279 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Status | Inverter | Inverter025_MODBUS.HRxxxx_M4_status | Module Status | 4280 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 IR | Inverter | Inverter025_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4281 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 IS | Inverter | Inverter025_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4282 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 IT | Inverter | Inverter025_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4283 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4284 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4285 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4286 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4287 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 P | Inverter | Inverter025_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4288 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Q | Inverter | Inverter025_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4289 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4290 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4291 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4292 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4293 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M4 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4294 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Status | Inverter | Inverter025_MODBUS.HRxxxx_M5_status | Module Status | 4295 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 IR | Inverter | Inverter025_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 IS | Inverter | Inverter025_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 IT | Inverter | Inverter025_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4299 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4300 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4301 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4302 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 P | Inverter | Inverter025_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4303 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Q | Inverter | Inverter025_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4304 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4305 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4306 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4308 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M5 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4309 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Status | Inverter | Inverter025_MODBUS.HRxxxx_M6_status | Module Status | 4310 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 IR | Inverter | Inverter025_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4311 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 IS | Inverter | Inverter025_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 IT | Inverter | Inverter025_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 IDC | Inverter | Inverter025_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 VDCP | Inverter | Inverter025_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4315 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 VDCN | Inverter | Inverter025_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 VDC | Inverter | Inverter025_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4317 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 P | Inverter | Inverter025_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4318 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Q | Inverter | Inverter025_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4319 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Ambient Temp | Inverter | Inverter025_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4320 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Max IGBT Temp | Inverter | Inverter025_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4321 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 IO Status | Inverter | Inverter025_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4322 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Hardware Version | Inverter | Inverter025_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV025 | Daggett 3_SUB1_INV025_M6 Software Version | Inverter | Inverter025_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_A Phase Current | Inverter | inverter026_MODBUS.HR1004_i1_A | A Phase Current | 4325 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_B Phase Current | Inverter | inverter026_MODBUS.HR1005_i2_A | B Phase Current | 4326 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_C Phase Current | Inverter | inverter026_MODBUS.HR1006_i3_A | C Phase Current | 4327 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Bus Voltage | Inverter | inverter026_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4328 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV026 | Daggett 3_SUB1_INV026_Apparent Power | Inverter | inverter026_MODBUS.HR1010_s3_VA | Apparent Power | 4329 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 1 | Inverter | Inverter026_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC Input 1 | Inverter | Inverter026_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4331 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 2 | Inverter | Inverter026_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4332 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 2 | Inverter | Inverter026_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4333 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 3 | Inverter | Inverter026_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 3 | Inverter | Inverter026_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4335 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 4 | Inverter | Inverter026_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 4 | Inverter | Inverter026_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4337 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 5 | Inverter | Inverter026_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4338 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 5 | Inverter | Inverter026_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4339 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 6 | Inverter | Inverter026_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4340 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 6 | Inverter | Inverter026_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4341 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 7 | Inverter | Inverter026_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 7 | Inverter | Inverter026_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4343 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 8 | Inverter | Inverter026_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4344 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 8 | Inverter | Inverter026_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4345 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 9 | Inverter | Inverter026_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4346 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 9 | Inverter | Inverter026_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4347 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 10 | Inverter | Inverter026_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4348 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 10 | Inverter | Inverter026_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4349 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 11 | Inverter | Inverter026_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 11 | Inverter | Inverter026_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4351 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 12 | Inverter | Inverter026_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 12 | Inverter | Inverter026_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4353 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 13 | Inverter | Inverter026_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4354 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 13 | Inverter | Inverter026_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4355 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 14 | Inverter | Inverter026_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4356 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 14 | Inverter | Inverter026_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4357 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 15 | Inverter | Inverter026_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 15 | Inverter | Inverter026_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4359 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 16 | Inverter | Inverter026_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4360 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 16 | Inverter | Inverter026_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4361 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 17 | Inverter | Inverter026_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4362 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 17 | Inverter | Inverter026_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4363 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 18 | Inverter | Inverter026_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4364 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 18 | Inverter | Inverter026_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4365 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 19 | Inverter | Inverter026_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 19 | Inverter | Inverter026_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4367 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current DC Input 20 | Inverter | Inverter026_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC input 20 | Inverter | Inverter026_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4369 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current-AC | Inverter | inverter026_MODBUS.HR1007_i3Avg_A | Current-AC | 4370 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Current-DC | Inverter | inverter026_MODBUS.HR1062_idcInput_A | Current-DC | 4371 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Daily Energy Delivered | Inverter | inverter026_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4372 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power Set Point | Inverter | inverter026_MODBUS.HR0553_pRef | Real Power Set Point | 4373 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Reactive Power Set Point | Inverter | inverter026_MODBUS.HR0558_qRef | Reactive Power Set Point | 4374 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Frequency | Inverter | inverter026_MODBUS.HR1012_f3_Hz | Frequency | 4375 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV026 | Daggett 3_SUB1_INV026_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Insulation Resistance | Inverter | inverter026_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4376 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Number of DU Channels | Inverter | inverter026_MODBUS.HR0653_duChannels | Number of DU Channels | 4377 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Number of Running Modules | Inverter | inverter026_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4378 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Operating State | Inverter | inverter026_MODBUS.HR1123_currentStatus | Operating State | 4379 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Power Factor | Inverter | inverter026_MODBUS.HR1011_pf3 | Power Factor | 4380 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV026 | Daggett 3_SUB1_INV026_Ramp Down | Inverter | inverter026_MODBUS.HR0286_dropGradient_p | Ramp Down | 4381 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Ramp Up | Inverter | inverter026_MODBUS.HR0282_riseGradient_p | Ramp Up | 4382 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power Delivered | Inverter | inverter026_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4383 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Reactive Power Delivered | Inverter | inverter026_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4384 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power | 4385 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Reactive Power | Inverter | inverter026_MODBUS.HR1009_q3_kvar | Reactive Power | 4386 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Reactive Power Mode | Inverter | inverter026_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4387 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Reactive Power Set Point Percent | Inverter | inverter026_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4388 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power AC Percent | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4389 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power-AC | Inverter | inverter026_MODBUS.HR1008_p3_kW | Real Power-AC | 4390 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power-DC | Inverter | inverter026_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4391 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Air Intake | Inverter | inverter026_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4392 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Cabinet | Inverter | inverter026_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4393 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-IGBT | Inverter | inverter026_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4394 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Temperature-Module | Inverter | inverter026_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4395 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage A-B | Inverter | inverter026_MODBUS.HR1006_vRS_V | Voltage A-B | 4396 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage B-C | Inverter | inverter026_MODBUS.HR1002_vST_V | Voltage B-C | 4397 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage C-A | Inverter | inverter026_MODBUS.HR1003_vTR_V | Voltage C-A | 4398 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Voltage DC | Inverter | inverter026_MODBUS.HR1051_vdcBus_V | Voltage DC | 4399 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV026 | Daggett 3_SUB1_INV026_Fault Code 1 | Inverter | Inverter026_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Warning | Inverter | Inverter026_MODBUS.HRxxxx_currentWarning | Warning | 4401 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Internal Input Status | Inverter | Inverter026_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4402 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Internal Output Status | Inverter | Inverter026_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4403 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Module Fault Code | Inverter | Inverter026_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4404 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Internal Humidity | Inverter | Inverter026_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4405 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Humidity | Inverter | Inverter026_MODBUS.HRxxxx_humidity | Humidity | 4406 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_Comms Fault Time | Inverter | Inverter026_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Status | Inverter | Inverter026_MODBUS.HRxxxx_M1_status | Module Status | 4408 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 IR | Inverter | Inverter026_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 IS | Inverter | Inverter026_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 IT | Inverter | Inverter026_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4413 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4415 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 P | Inverter | Inverter026_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4416 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Q | Inverter | Inverter026_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4417 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4418 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4419 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4420 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M1 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Status | Inverter | Inverter026_MODBUS.HRxxxx_M2_status | Module Status | 4423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 IR | Inverter | Inverter026_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4424 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 IS | Inverter | Inverter026_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 IT | Inverter | Inverter026_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4428 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4429 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4430 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 P | Inverter | Inverter026_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4431 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Q | Inverter | Inverter026_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4432 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4433 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4434 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4435 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4436 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M2 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4437 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Status | Inverter | Inverter026_MODBUS.HRxxxx_M3_status | Module Status | 4438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 IR | Inverter | Inverter026_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4439 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 IS | Inverter | Inverter026_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4440 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 IT | Inverter | Inverter026_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4441 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4442 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4443 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4444 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4445 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 P | Inverter | Inverter026_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4446 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Q | Inverter | Inverter026_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4447 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4448 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4449 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4450 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4451 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M3 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4452 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Status | Inverter | Inverter026_MODBUS.HRxxxx_M4_status | Module Status | 4453 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 IR | Inverter | Inverter026_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4454 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 IS | Inverter | Inverter026_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4455 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 IT | Inverter | Inverter026_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4456 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4457 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4458 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4459 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4460 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 P | Inverter | Inverter026_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4461 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Q | Inverter | Inverter026_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4462 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4463 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4464 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4465 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4466 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M4 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4467 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Status | Inverter | Inverter026_MODBUS.HRxxxx_M5_status | Module Status | 4468 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 IR | Inverter | Inverter026_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 IS | Inverter | Inverter026_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 IT | Inverter | Inverter026_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4472 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4473 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4474 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4475 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 P | Inverter | Inverter026_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4476 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Q | Inverter | Inverter026_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4477 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4478 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4479 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4481 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M5 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4482 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Status | Inverter | Inverter026_MODBUS.HRxxxx_M6_status | Module Status | 4483 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 IR | Inverter | Inverter026_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4484 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 IS | Inverter | Inverter026_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 IT | Inverter | Inverter026_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 IDC | Inverter | Inverter026_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 VDCP | Inverter | Inverter026_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4488 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 VDCN | Inverter | Inverter026_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 VDC | Inverter | Inverter026_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4490 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 P | Inverter | Inverter026_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4491 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Q | Inverter | Inverter026_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4492 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Ambient Temp | Inverter | Inverter026_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4493 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Max IGBT Temp | Inverter | Inverter026_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4494 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 IO Status | Inverter | Inverter026_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4495 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Hardware Version | Inverter | Inverter026_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV026 | Daggett 3_SUB1_INV026_M6 Software Version | Inverter | Inverter026_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_A Phase Current | Inverter | inverter027_MODBUS.HR1004_i1_A | A Phase Current | 4498 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_B Phase Current | Inverter | inverter027_MODBUS.HR1005_i2_A | B Phase Current | 4499 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_C Phase Current | Inverter | inverter027_MODBUS.HR1006_i3_A | C Phase Current | 4500 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Bus Voltage | Inverter | inverter027_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4501 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV027 | Daggett 3_SUB1_INV027_Apparent Power | Inverter | inverter027_MODBUS.HR1010_s3_VA | Apparent Power | 4502 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 1 | Inverter | Inverter027_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC Input 1 | Inverter | Inverter027_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4504 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 2 | Inverter | Inverter027_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4505 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 2 | Inverter | Inverter027_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4506 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 3 | Inverter | Inverter027_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 3 | Inverter | Inverter027_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4508 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 4 | Inverter | Inverter027_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 4 | Inverter | Inverter027_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4510 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 5 | Inverter | Inverter027_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4511 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 5 | Inverter | Inverter027_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4512 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 6 | Inverter | Inverter027_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4513 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 6 | Inverter | Inverter027_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4514 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 7 | Inverter | Inverter027_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 7 | Inverter | Inverter027_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4516 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 8 | Inverter | Inverter027_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4517 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 8 | Inverter | Inverter027_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4518 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 9 | Inverter | Inverter027_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4519 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 9 | Inverter | Inverter027_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4520 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 10 | Inverter | Inverter027_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4521 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 10 | Inverter | Inverter027_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4522 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 11 | Inverter | Inverter027_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 11 | Inverter | Inverter027_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4524 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 12 | Inverter | Inverter027_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 12 | Inverter | Inverter027_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4526 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 13 | Inverter | Inverter027_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4527 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 13 | Inverter | Inverter027_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4528 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 14 | Inverter | Inverter027_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4529 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 14 | Inverter | Inverter027_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4530 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 15 | Inverter | Inverter027_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 15 | Inverter | Inverter027_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4532 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 16 | Inverter | Inverter027_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4533 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 16 | Inverter | Inverter027_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4534 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 17 | Inverter | Inverter027_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4535 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 17 | Inverter | Inverter027_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4536 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 18 | Inverter | Inverter027_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4537 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 18 | Inverter | Inverter027_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4538 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 19 | Inverter | Inverter027_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 19 | Inverter | Inverter027_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4540 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current DC Input 20 | Inverter | Inverter027_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC input 20 | Inverter | Inverter027_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4542 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current-AC | Inverter | inverter027_MODBUS.HR1007_i3Avg_A | Current-AC | 4543 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Current-DC | Inverter | inverter027_MODBUS.HR1062_idcInput_A | Current-DC | 4544 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Daily Energy Delivered | Inverter | inverter027_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4545 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power Set Point | Inverter | inverter027_MODBUS.HR0553_pRef | Real Power Set Point | 4546 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Reactive Power Set Point | Inverter | inverter027_MODBUS.HR0558_qRef | Reactive Power Set Point | 4547 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Frequency | Inverter | inverter027_MODBUS.HR1012_f3_Hz | Frequency | 4548 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV027 | Daggett 3_SUB1_INV027_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Insulation Resistance | Inverter | inverter027_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4549 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Number of DU Channels | Inverter | inverter027_MODBUS.HR0653_duChannels | Number of DU Channels | 4550 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Number of Running Modules | Inverter | inverter027_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4551 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Operating State | Inverter | inverter027_MODBUS.HR1123_currentStatus | Operating State | 4552 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Power Factor | Inverter | inverter027_MODBUS.HR1011_pf3 | Power Factor | 4553 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV027 | Daggett 3_SUB1_INV027_Ramp Down | Inverter | inverter027_MODBUS.HR0286_dropGradient_p | Ramp Down | 4554 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Ramp Up | Inverter | inverter027_MODBUS.HR0282_riseGradient_p | Ramp Up | 4555 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power Delivered | Inverter | inverter027_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4556 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Reactive Power Delivered | Inverter | inverter027_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4557 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power | 4558 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Reactive Power | Inverter | inverter027_MODBUS.HR1009_q3_kvar | Reactive Power | 4559 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Reactive Power Mode | Inverter | inverter027_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4560 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Reactive Power Set Point Percent | Inverter | inverter027_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4561 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power AC Percent | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4562 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power-AC | Inverter | inverter027_MODBUS.HR1008_p3_kW | Real Power-AC | 4563 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power-DC | Inverter | inverter027_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4564 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Air Intake | Inverter | inverter027_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4565 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Cabinet | Inverter | inverter027_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4566 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-IGBT | Inverter | inverter027_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4567 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Temperature-Module | Inverter | inverter027_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4568 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage A-B | Inverter | inverter027_MODBUS.HR1007_vRS_V | Voltage A-B | 4569 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage B-C | Inverter | inverter027_MODBUS.HR1002_vST_V | Voltage B-C | 4570 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage C-A | Inverter | inverter027_MODBUS.HR1003_vTR_V | Voltage C-A | 4571 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Voltage DC | Inverter | inverter027_MODBUS.HR1051_vdcBus_V | Voltage DC | 4572 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV027 | Daggett 3_SUB1_INV027_Fault Code 1 | Inverter | Inverter027_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Warning | Inverter | Inverter027_MODBUS.HRxxxx_currentWarning | Warning | 4574 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Internal Input Status | Inverter | Inverter027_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4575 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Internal Output Status | Inverter | Inverter027_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4576 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Module Fault Code | Inverter | Inverter027_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4577 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Internal Humidity | Inverter | Inverter027_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4578 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Humidity | Inverter | Inverter027_MODBUS.HRxxxx_humidity | Humidity | 4579 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_Comms Fault Time | Inverter | Inverter027_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Status | Inverter | Inverter027_MODBUS.HRxxxx_M1_status | Module Status | 4581 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 IR | Inverter | Inverter027_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 IS | Inverter | Inverter027_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 IT | Inverter | Inverter027_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4586 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4588 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 P | Inverter | Inverter027_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4589 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Q | Inverter | Inverter027_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4590 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4591 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4592 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4593 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M1 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Status | Inverter | Inverter027_MODBUS.HRxxxx_M2_status | Module Status | 4596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 IR | Inverter | Inverter027_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4597 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 IS | Inverter | Inverter027_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 IT | Inverter | Inverter027_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4601 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4602 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4603 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 P | Inverter | Inverter027_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4604 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Q | Inverter | Inverter027_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4605 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4606 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4607 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4608 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4609 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M2 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4610 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Status | Inverter | Inverter027_MODBUS.HRxxxx_M3_status | Module Status | 4611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 IR | Inverter | Inverter027_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4612 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 IS | Inverter | Inverter027_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4613 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 IT | Inverter | Inverter027_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4614 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4615 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4616 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4617 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4618 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 P | Inverter | Inverter027_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4619 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Q | Inverter | Inverter027_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4620 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4621 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4622 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4623 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4624 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M3 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4625 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Status | Inverter | Inverter027_MODBUS.HRxxxx_M4_status | Module Status | 4626 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 IR | Inverter | Inverter027_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4627 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 IS | Inverter | Inverter027_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4628 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 IT | Inverter | Inverter027_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4629 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4630 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4631 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4632 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4633 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 P | Inverter | Inverter027_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4634 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Q | Inverter | Inverter027_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4635 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4636 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4637 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4638 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4639 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M4 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4640 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Status | Inverter | Inverter027_MODBUS.HRxxxx_M5_status | Module Status | 4641 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 IR | Inverter | Inverter027_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 IS | Inverter | Inverter027_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 IT | Inverter | Inverter027_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4645 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4646 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4647 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4648 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 P | Inverter | Inverter027_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4649 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Q | Inverter | Inverter027_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4650 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4651 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4652 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4654 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M5 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4655 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Status | Inverter | Inverter027_MODBUS.HRxxxx_M6_status | Module Status | 4656 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 IR | Inverter | Inverter027_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4657 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 IS | Inverter | Inverter027_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 IT | Inverter | Inverter027_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 IDC | Inverter | Inverter027_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 VDCP | Inverter | Inverter027_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4661 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 VDCN | Inverter | Inverter027_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 VDC | Inverter | Inverter027_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4663 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 P | Inverter | Inverter027_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4664 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Q | Inverter | Inverter027_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4665 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Ambient Temp | Inverter | Inverter027_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4666 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Max IGBT Temp | Inverter | Inverter027_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4667 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 IO Status | Inverter | Inverter027_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4668 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Hardware Version | Inverter | Inverter027_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV027 | Daggett 3_SUB1_INV027_M6 Software Version | Inverter | Inverter027_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_A Phase Current | Inverter | inverter028_MODBUS.HR1004_i1_A | A Phase Current | 4671 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_B Phase Current | Inverter | inverter028_MODBUS.HR1005_i2_A | B Phase Current | 4672 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_C Phase Current | Inverter | inverter028_MODBUS.HR1006_i3_A | C Phase Current | 4673 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Bus Voltage | Inverter | inverter028_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4674 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV028 | Daggett 3_SUB1_INV028_Apparent Power | Inverter | inverter028_MODBUS.HR1010_s3_VA | Apparent Power | 4675 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 1 | Inverter | Inverter028_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC Input 1 | Inverter | Inverter028_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4677 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 2 | Inverter | Inverter028_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4678 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 2 | Inverter | Inverter028_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4679 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 3 | Inverter | Inverter028_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 3 | Inverter | Inverter028_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4681 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 4 | Inverter | Inverter028_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 4 | Inverter | Inverter028_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4683 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 5 | Inverter | Inverter028_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4684 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 5 | Inverter | Inverter028_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4685 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 6 | Inverter | Inverter028_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4686 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 6 | Inverter | Inverter028_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4687 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 7 | Inverter | Inverter028_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 7 | Inverter | Inverter028_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4689 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 8 | Inverter | Inverter028_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4690 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 8 | Inverter | Inverter028_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4691 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 9 | Inverter | Inverter028_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4692 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 9 | Inverter | Inverter028_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4693 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 10 | Inverter | Inverter028_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4694 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 10 | Inverter | Inverter028_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4695 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 11 | Inverter | Inverter028_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 11 | Inverter | Inverter028_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4697 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 12 | Inverter | Inverter028_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 12 | Inverter | Inverter028_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4699 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 13 | Inverter | Inverter028_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4700 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 13 | Inverter | Inverter028_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4701 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 14 | Inverter | Inverter028_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4702 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 14 | Inverter | Inverter028_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4703 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 15 | Inverter | Inverter028_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 15 | Inverter | Inverter028_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4705 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 16 | Inverter | Inverter028_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4706 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 16 | Inverter | Inverter028_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4707 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 17 | Inverter | Inverter028_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4708 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 17 | Inverter | Inverter028_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4709 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 18 | Inverter | Inverter028_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4710 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 18 | Inverter | Inverter028_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4711 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 19 | Inverter | Inverter028_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 19 | Inverter | Inverter028_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4713 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current DC Input 20 | Inverter | Inverter028_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC input 20 | Inverter | Inverter028_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4715 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current-AC | Inverter | inverter028_MODBUS.HR1007_i3Avg_A | Current-AC | 4716 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Current-DC | Inverter | inverter028_MODBUS.HR1062_idcInput_A | Current-DC | 4717 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Daily Energy Delivered | Inverter | inverter028_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4718 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power Set Point | Inverter | inverter028_MODBUS.HR0553_pRef | Real Power Set Point | 4719 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Reactive Power Set Point | Inverter | inverter028_MODBUS.HR0558_qRef | Reactive Power Set Point | 4720 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Frequency | Inverter | inverter028_MODBUS.HR1012_f3_Hz | Frequency | 4721 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV028 | Daggett 3_SUB1_INV028_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Insulation Resistance | Inverter | inverter028_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4722 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Number of DU Channels | Inverter | inverter028_MODBUS.HR0653_duChannels | Number of DU Channels | 4723 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Number of Running Modules | Inverter | inverter028_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4724 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Operating State | Inverter | inverter028_MODBUS.HR1123_currentStatus | Operating State | 4725 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Power Factor | Inverter | inverter028_MODBUS.HR1011_pf3 | Power Factor | 4726 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV028 | Daggett 3_SUB1_INV028_Ramp Down | Inverter | inverter028_MODBUS.HR0286_dropGradient_p | Ramp Down | 4727 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Ramp Up | Inverter | inverter028_MODBUS.HR0282_riseGradient_p | Ramp Up | 4728 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power Delivered | Inverter | inverter028_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4729 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Reactive Power Delivered | Inverter | inverter028_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4730 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power | 4731 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Reactive Power | Inverter | inverter028_MODBUS.HR1009_q3_kvar | Reactive Power | 4732 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Reactive Power Mode | Inverter | inverter028_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4733 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Reactive Power Set Point Percent | Inverter | inverter028_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4734 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power AC Percent | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4735 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power-AC | Inverter | inverter028_MODBUS.HR1008_p3_kW | Real Power-AC | 4736 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power-DC | Inverter | inverter028_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4737 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Air Intake | Inverter | inverter028_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4738 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Cabinet | Inverter | inverter028_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4739 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-IGBT | Inverter | inverter028_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4740 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Temperature-Module | Inverter | inverter028_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4741 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage A-B | Inverter | inverter028_MODBUS.HR1008_vRS_V | Voltage A-B | 4742 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage B-C | Inverter | inverter028_MODBUS.HR1002_vST_V | Voltage B-C | 4743 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage C-A | Inverter | inverter028_MODBUS.HR1003_vTR_V | Voltage C-A | 4744 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Voltage DC | Inverter | inverter028_MODBUS.HR1051_vdcBus_V | Voltage DC | 4745 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV028 | Daggett 3_SUB1_INV028_Fault Code 1 | Inverter | Inverter028_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Warning | Inverter | Inverter028_MODBUS.HRxxxx_currentWarning | Warning | 4747 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Internal Input Status | Inverter | Inverter028_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4748 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Internal Output Status | Inverter | Inverter028_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4749 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Module Fault Code | Inverter | Inverter028_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4750 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Internal Humidity | Inverter | Inverter028_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4751 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Humidity | Inverter | Inverter028_MODBUS.HRxxxx_humidity | Humidity | 4752 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_Comms Fault Time | Inverter | Inverter028_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Status | Inverter | Inverter028_MODBUS.HRxxxx_M1_status | Module Status | 4754 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 IR | Inverter | Inverter028_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 IS | Inverter | Inverter028_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 IT | Inverter | Inverter028_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4759 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4761 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 P | Inverter | Inverter028_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4762 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Q | Inverter | Inverter028_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4763 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4764 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4765 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4766 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M1 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Status | Inverter | Inverter028_MODBUS.HRxxxx_M2_status | Module Status | 4769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 IR | Inverter | Inverter028_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4770 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 IS | Inverter | Inverter028_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 IT | Inverter | Inverter028_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4774 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4775 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4776 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 P | Inverter | Inverter028_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4777 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Q | Inverter | Inverter028_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4778 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4779 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4780 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4781 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4782 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M2 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4783 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Status | Inverter | Inverter028_MODBUS.HRxxxx_M3_status | Module Status | 4784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 IR | Inverter | Inverter028_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4785 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 IS | Inverter | Inverter028_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4786 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 IT | Inverter | Inverter028_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4787 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4788 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4789 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4790 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4791 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 P | Inverter | Inverter028_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4792 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Q | Inverter | Inverter028_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4793 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4794 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4795 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4796 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4797 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M3 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4798 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Status | Inverter | Inverter028_MODBUS.HRxxxx_M4_status | Module Status | 4799 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 IR | Inverter | Inverter028_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4800 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 IS | Inverter | Inverter028_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4801 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 IT | Inverter | Inverter028_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4802 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4803 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4804 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4805 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4806 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 P | Inverter | Inverter028_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4807 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Q | Inverter | Inverter028_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4808 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4809 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4810 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4811 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4812 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M4 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4813 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Status | Inverter | Inverter028_MODBUS.HRxxxx_M5_status | Module Status | 4814 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 IR | Inverter | Inverter028_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 IS | Inverter | Inverter028_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 IT | Inverter | Inverter028_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4818 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4819 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4820 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4821 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 P | Inverter | Inverter028_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4822 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Q | Inverter | Inverter028_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4823 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4824 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4825 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4827 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M5 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4828 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Status | Inverter | Inverter028_MODBUS.HRxxxx_M6_status | Module Status | 4829 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 IR | Inverter | Inverter028_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4830 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 IS | Inverter | Inverter028_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 IT | Inverter | Inverter028_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 IDC | Inverter | Inverter028_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 VDCP | Inverter | Inverter028_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4834 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 VDCN | Inverter | Inverter028_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 VDC | Inverter | Inverter028_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4836 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 P | Inverter | Inverter028_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4837 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Q | Inverter | Inverter028_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4838 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Ambient Temp | Inverter | Inverter028_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4839 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Max IGBT Temp | Inverter | Inverter028_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4840 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 IO Status | Inverter | Inverter028_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4841 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Hardware Version | Inverter | Inverter028_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV028 | Daggett 3_SUB1_INV028_M6 Software Version | Inverter | Inverter028_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_A Phase Current | Inverter | inverter029_MODBUS.HR1004_i1_A | A Phase Current | 4844 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_B Phase Current | Inverter | inverter029_MODBUS.HR1005_i2_A | B Phase Current | 4845 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_C Phase Current | Inverter | inverter029_MODBUS.HR1006_i3_A | C Phase Current | 4846 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Bus Voltage | Inverter | inverter029_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4847 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV029 | Daggett 3_SUB1_INV029_Apparent Power | Inverter | inverter029_MODBUS.HR1010_s3_VA | Apparent Power | 4848 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 1 | Inverter | Inverter029_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC Input 1 | Inverter | Inverter029_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4850 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 2 | Inverter | Inverter029_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4851 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 2 | Inverter | Inverter029_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4852 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 3 | Inverter | Inverter029_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 3 | Inverter | Inverter029_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4854 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 4 | Inverter | Inverter029_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 4 | Inverter | Inverter029_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4856 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 5 | Inverter | Inverter029_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4857 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 5 | Inverter | Inverter029_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4858 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 6 | Inverter | Inverter029_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4859 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 6 | Inverter | Inverter029_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4860 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 7 | Inverter | Inverter029_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 7 | Inverter | Inverter029_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4862 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 8 | Inverter | Inverter029_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4863 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 8 | Inverter | Inverter029_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4864 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 9 | Inverter | Inverter029_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4865 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 9 | Inverter | Inverter029_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4866 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 10 | Inverter | Inverter029_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4867 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 10 | Inverter | Inverter029_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4868 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 11 | Inverter | Inverter029_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 11 | Inverter | Inverter029_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4870 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 12 | Inverter | Inverter029_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 12 | Inverter | Inverter029_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4872 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 13 | Inverter | Inverter029_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4873 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 13 | Inverter | Inverter029_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4874 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 14 | Inverter | Inverter029_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4875 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 14 | Inverter | Inverter029_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4876 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 15 | Inverter | Inverter029_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 15 | Inverter | Inverter029_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4878 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 16 | Inverter | Inverter029_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4879 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 16 | Inverter | Inverter029_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4880 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 17 | Inverter | Inverter029_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4881 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 17 | Inverter | Inverter029_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4882 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 18 | Inverter | Inverter029_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4883 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 18 | Inverter | Inverter029_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4884 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 19 | Inverter | Inverter029_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 19 | Inverter | Inverter029_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4886 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current DC Input 20 | Inverter | Inverter029_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC input 20 | Inverter | Inverter029_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4888 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current-AC | Inverter | inverter029_MODBUS.HR1007_i3Avg_A | Current-AC | 4889 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Current-DC | Inverter | inverter029_MODBUS.HR1062_idcInput_A | Current-DC | 4890 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Daily Energy Delivered | Inverter | inverter029_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4891 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power Set Point | Inverter | inverter029_MODBUS.HR0553_pRef | Real Power Set Point | 4892 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Reactive Power Set Point | Inverter | inverter029_MODBUS.HR0558_qRef | Reactive Power Set Point | 4893 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Frequency | Inverter | inverter029_MODBUS.HR1012_f3_Hz | Frequency | 4894 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV029 | Daggett 3_SUB1_INV029_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Insulation Resistance | Inverter | inverter029_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4895 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Number of DU Channels | Inverter | inverter029_MODBUS.HR0653_duChannels | Number of DU Channels | 4896 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Number of Running Modules | Inverter | inverter029_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4897 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Operating State | Inverter | inverter029_MODBUS.HR1123_currentStatus | Operating State | 4898 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Power Factor | Inverter | inverter029_MODBUS.HR1011_pf3 | Power Factor | 4899 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV029 | Daggett 3_SUB1_INV029_Ramp Down | Inverter | inverter029_MODBUS.HR0286_dropGradient_p | Ramp Down | 4900 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Ramp Up | Inverter | inverter029_MODBUS.HR0282_riseGradient_p | Ramp Up | 4901 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power Delivered | Inverter | inverter029_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4902 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Reactive Power Delivered | Inverter | inverter029_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4903 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power | 4904 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Reactive Power | Inverter | inverter029_MODBUS.HR1009_q3_kvar | Reactive Power | 4905 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Reactive Power Mode | Inverter | inverter029_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4906 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Reactive Power Set Point Percent | Inverter | inverter029_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4907 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power AC Percent | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4908 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power-AC | Inverter | inverter029_MODBUS.HR1008_p3_kW | Real Power-AC | 4909 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power-DC | Inverter | inverter029_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4910 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Air Intake | Inverter | inverter029_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4911 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Cabinet | Inverter | inverter029_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4912 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-IGBT | Inverter | inverter029_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4913 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Temperature-Module | Inverter | inverter029_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4914 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage A-B | Inverter | inverter029_MODBUS.HR1009_vRS_V | Voltage A-B | 4915 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage B-C | Inverter | inverter029_MODBUS.HR1002_vST_V | Voltage B-C | 4916 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage C-A | Inverter | inverter029_MODBUS.HR1003_vTR_V | Voltage C-A | 4917 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Voltage DC | Inverter | inverter029_MODBUS.HR1051_vdcBus_V | Voltage DC | 4918 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV029 | Daggett 3_SUB1_INV029_Fault Code 1 | Inverter | Inverter029_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Warning | Inverter | Inverter029_MODBUS.HRxxxx_currentWarning | Warning | 4920 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Internal Input Status | Inverter | Inverter029_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4921 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Internal Output Status | Inverter | Inverter029_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4922 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Module Fault Code | Inverter | Inverter029_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4923 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Internal Humidity | Inverter | Inverter029_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4924 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Humidity | Inverter | Inverter029_MODBUS.HRxxxx_humidity | Humidity | 4925 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_Comms Fault Time | Inverter | Inverter029_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Status | Inverter | Inverter029_MODBUS.HRxxxx_M1_status | Module Status | 4927 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 IR | Inverter | Inverter029_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 IS | Inverter | Inverter029_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 IT | Inverter | Inverter029_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4932 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4934 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 P | Inverter | Inverter029_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4935 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Q | Inverter | Inverter029_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4936 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4937 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4938 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4939 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M1 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Status | Inverter | Inverter029_MODBUS.HRxxxx_M2_status | Module Status | 4942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 IR | Inverter | Inverter029_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4943 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 IS | Inverter | Inverter029_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 IT | Inverter | Inverter029_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4947 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4948 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4949 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 P | Inverter | Inverter029_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4950 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Q | Inverter | Inverter029_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4951 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4952 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4953 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4954 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4955 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M2 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4956 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Status | Inverter | Inverter029_MODBUS.HRxxxx_M3_status | Module Status | 4957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 IR | Inverter | Inverter029_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4958 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 IS | Inverter | Inverter029_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4959 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 IT | Inverter | Inverter029_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4960 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4961 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4962 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4963 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4964 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 P | Inverter | Inverter029_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4965 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Q | Inverter | Inverter029_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4966 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4967 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4968 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4969 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4970 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M3 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4971 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Status | Inverter | Inverter029_MODBUS.HRxxxx_M4_status | Module Status | 4972 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 IR | Inverter | Inverter029_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4973 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 IS | Inverter | Inverter029_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4974 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 IT | Inverter | Inverter029_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4975 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4976 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4977 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4978 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4979 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 P | Inverter | Inverter029_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4980 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Q | Inverter | Inverter029_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4981 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4982 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4983 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4984 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4985 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M4 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4986 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Status | Inverter | Inverter029_MODBUS.HRxxxx_M5_status | Module Status | 4987 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 IR | Inverter | Inverter029_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 IS | Inverter | Inverter029_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 IT | Inverter | Inverter029_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4991 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4992 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4993 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4994 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 P | Inverter | Inverter029_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4995 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Q | Inverter | Inverter029_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4996 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4997 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4998 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5000 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M5 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5001 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Status | Inverter | Inverter029_MODBUS.HRxxxx_M6_status | Module Status | 5002 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 IR | Inverter | Inverter029_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5003 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 IS | Inverter | Inverter029_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 IT | Inverter | Inverter029_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 IDC | Inverter | Inverter029_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 VDCP | Inverter | Inverter029_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5007 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 VDCN | Inverter | Inverter029_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 VDC | Inverter | Inverter029_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5009 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 P | Inverter | Inverter029_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5010 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Q | Inverter | Inverter029_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5011 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Ambient Temp | Inverter | Inverter029_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5012 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Max IGBT Temp | Inverter | Inverter029_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5013 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 IO Status | Inverter | Inverter029_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5014 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Hardware Version | Inverter | Inverter029_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV029 | Daggett 3_SUB1_INV029_M6 Software Version | Inverter | Inverter029_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_A Phase Current | Inverter | inverter030_MODBUS.HR1004_i1_A | A Phase Current | 5017 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_B Phase Current | Inverter | inverter030_MODBUS.HR1005_i2_A | B Phase Current | 5018 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_C Phase Current | Inverter | inverter030_MODBUS.HR1006_i3_A | C Phase Current | 5019 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Bus Voltage | Inverter | inverter030_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5020 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV030 | Daggett 3_SUB1_INV030_Apparent Power | Inverter | inverter030_MODBUS.HR1010_s3_VA | Apparent Power | 5021 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 1 | Inverter | Inverter030_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC Input 1 | Inverter | Inverter030_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5023 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 2 | Inverter | Inverter030_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5024 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 2 | Inverter | Inverter030_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5025 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 3 | Inverter | Inverter030_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 3 | Inverter | Inverter030_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5027 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 4 | Inverter | Inverter030_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 4 | Inverter | Inverter030_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5029 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 5 | Inverter | Inverter030_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5030 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 5 | Inverter | Inverter030_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5031 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 6 | Inverter | Inverter030_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5032 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 6 | Inverter | Inverter030_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5033 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 7 | Inverter | Inverter030_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 7 | Inverter | Inverter030_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5035 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 8 | Inverter | Inverter030_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5036 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 8 | Inverter | Inverter030_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5037 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 9 | Inverter | Inverter030_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5038 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 9 | Inverter | Inverter030_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5039 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 10 | Inverter | Inverter030_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5040 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 10 | Inverter | Inverter030_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5041 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 11 | Inverter | Inverter030_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 11 | Inverter | Inverter030_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5043 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 12 | Inverter | Inverter030_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 12 | Inverter | Inverter030_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5045 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 13 | Inverter | Inverter030_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5046 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 13 | Inverter | Inverter030_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5047 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 14 | Inverter | Inverter030_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5048 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 14 | Inverter | Inverter030_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5049 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 15 | Inverter | Inverter030_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 15 | Inverter | Inverter030_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5051 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 16 | Inverter | Inverter030_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5052 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 16 | Inverter | Inverter030_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5053 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 17 | Inverter | Inverter030_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5054 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 17 | Inverter | Inverter030_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5055 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 18 | Inverter | Inverter030_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5056 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 18 | Inverter | Inverter030_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5057 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 19 | Inverter | Inverter030_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 19 | Inverter | Inverter030_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5059 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current DC Input 20 | Inverter | Inverter030_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC input 20 | Inverter | Inverter030_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5061 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current-AC | Inverter | inverter030_MODBUS.HR1007_i3Avg_A | Current-AC | 5062 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Current-DC | Inverter | inverter030_MODBUS.HR1062_idcInput_A | Current-DC | 5063 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Daily Energy Delivered | Inverter | inverter030_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5064 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power Set Point | Inverter | inverter030_MODBUS.HR0553_pRef | Real Power Set Point | 5065 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Reactive Power Set Point | Inverter | inverter030_MODBUS.HR0558_qRef | Reactive Power Set Point | 5066 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Frequency | Inverter | inverter030_MODBUS.HR1012_f3_Hz | Frequency | 5067 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV030 | Daggett 3_SUB1_INV030_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Insulation Resistance | Inverter | inverter030_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5068 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Number of DU Channels | Inverter | inverter030_MODBUS.HR0653_duChannels | Number of DU Channels | 5069 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Number of Running Modules | Inverter | inverter030_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5070 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Operating State | Inverter | inverter030_MODBUS.HR1123_currentStatus | Operating State | 5071 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Power Factor | Inverter | inverter030_MODBUS.HR1011_pf3 | Power Factor | 5072 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV030 | Daggett 3_SUB1_INV030_Ramp Down | Inverter | inverter030_MODBUS.HR0286_dropGradient_p | Ramp Down | 5073 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Ramp Up | Inverter | inverter030_MODBUS.HR0282_riseGradient_p | Ramp Up | 5074 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power Delivered | Inverter | inverter030_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5075 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Reactive Power Delivered | Inverter | inverter030_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5076 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power | 5077 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Reactive Power | Inverter | inverter030_MODBUS.HR1009_q3_kvar | Reactive Power | 5078 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Reactive Power Mode | Inverter | inverter030_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5079 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Reactive Power Set Point Percent | Inverter | inverter030_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5080 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power AC Percent | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5081 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power-AC | Inverter | inverter030_MODBUS.HR1008_p3_kW | Real Power-AC | 5082 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power-DC | Inverter | inverter030_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5083 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Air Intake | Inverter | inverter030_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5084 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Cabinet | Inverter | inverter030_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5085 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-IGBT | Inverter | inverter030_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5086 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Temperature-Module | Inverter | inverter030_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5087 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage A-B | Inverter | inverter030_MODBUS.HR1010_vRS_V | Voltage A-B | 5088 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage B-C | Inverter | inverter030_MODBUS.HR1002_vST_V | Voltage B-C | 5089 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage C-A | Inverter | inverter030_MODBUS.HR1003_vTR_V | Voltage C-A | 5090 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Voltage DC | Inverter | inverter030_MODBUS.HR1051_vdcBus_V | Voltage DC | 5091 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV030 | Daggett 3_SUB1_INV030_Fault Code 1 | Inverter | Inverter030_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Warning | Inverter | Inverter030_MODBUS.HRxxxx_currentWarning | Warning | 5093 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Internal Input Status | Inverter | Inverter030_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5094 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Internal Output Status | Inverter | Inverter030_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5095 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Module Fault Code | Inverter | Inverter030_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5096 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Internal Humidity | Inverter | Inverter030_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5097 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Humidity | Inverter | Inverter030_MODBUS.HRxxxx_humidity | Humidity | 5098 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_Comms Fault Time | Inverter | Inverter030_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Status | Inverter | Inverter030_MODBUS.HRxxxx_M1_status | Module Status | 5100 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 IR | Inverter | Inverter030_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 IS | Inverter | Inverter030_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 IT | Inverter | Inverter030_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5107 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 P | Inverter | Inverter030_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5108 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Q | Inverter | Inverter030_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5109 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5110 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5111 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M1 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Status | Inverter | Inverter030_MODBUS.HRxxxx_M2_status | Module Status | 5115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 IR | Inverter | Inverter030_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 IS | Inverter | Inverter030_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 IT | Inverter | Inverter030_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5120 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5121 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5122 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 P | Inverter | Inverter030_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5123 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Q | Inverter | Inverter030_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5124 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5125 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5126 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5127 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M2 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5129 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Status | Inverter | Inverter030_MODBUS.HRxxxx_M3_status | Module Status | 5130 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 IR | Inverter | Inverter030_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 IS | Inverter | Inverter030_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 IT | Inverter | Inverter030_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5133 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5134 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5135 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5136 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5137 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 P | Inverter | Inverter030_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5138 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Q | Inverter | Inverter030_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5139 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5140 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5141 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5142 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5143 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M3 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5144 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Status | Inverter | Inverter030_MODBUS.HRxxxx_M4_status | Module Status | 5145 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 IR | Inverter | Inverter030_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5146 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 IS | Inverter | Inverter030_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 IT | Inverter | Inverter030_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5148 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5149 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5150 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5151 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5152 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 P | Inverter | Inverter030_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5153 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Q | Inverter | Inverter030_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5154 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5155 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5156 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5157 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M4 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5159 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Status | Inverter | Inverter030_MODBUS.HRxxxx_M5_status | Module Status | 5160 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 IR | Inverter | Inverter030_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 IS | Inverter | Inverter030_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 IT | Inverter | Inverter030_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5164 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5166 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5167 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 P | Inverter | Inverter030_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5168 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Q | Inverter | Inverter030_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5169 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5170 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5171 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5173 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M5 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5174 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Status | Inverter | Inverter030_MODBUS.HRxxxx_M6_status | Module Status | 5175 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 IR | Inverter | Inverter030_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5176 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 IS | Inverter | Inverter030_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 IT | Inverter | Inverter030_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 IDC | Inverter | Inverter030_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 VDCP | Inverter | Inverter030_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5180 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 VDCN | Inverter | Inverter030_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 VDC | Inverter | Inverter030_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5182 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 P | Inverter | Inverter030_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5183 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Q | Inverter | Inverter030_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5184 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Ambient Temp | Inverter | Inverter030_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5185 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Max IGBT Temp | Inverter | Inverter030_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5186 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 IO Status | Inverter | Inverter030_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5187 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Hardware Version | Inverter | Inverter030_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV030 | Daggett 3_SUB1_INV030_M6 Software Version | Inverter | Inverter030_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_A Phase Current | Inverter | inverter031_MODBUS.HR1004_i1_A | A Phase Current | 5190 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_B Phase Current | Inverter | inverter031_MODBUS.HR1005_i2_A | B Phase Current | 5191 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_C Phase Current | Inverter | inverter031_MODBUS.HR1006_i3_A | C Phase Current | 5192 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Bus Voltage | Inverter | inverter031_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5193 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV031 | Daggett 3_SUB1_INV031_Apparent Power | Inverter | inverter031_MODBUS.HR1010_s3_VA | Apparent Power | 5194 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 1 | Inverter | Inverter031_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC Input 1 | Inverter | Inverter031_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5196 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 2 | Inverter | Inverter031_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5197 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 2 | Inverter | Inverter031_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5198 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 3 | Inverter | Inverter031_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 3 | Inverter | Inverter031_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5200 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 4 | Inverter | Inverter031_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 4 | Inverter | Inverter031_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5202 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 5 | Inverter | Inverter031_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5203 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 5 | Inverter | Inverter031_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5204 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 6 | Inverter | Inverter031_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5205 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 6 | Inverter | Inverter031_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5206 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 7 | Inverter | Inverter031_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 7 | Inverter | Inverter031_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5208 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 8 | Inverter | Inverter031_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5209 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 8 | Inverter | Inverter031_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5210 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 9 | Inverter | Inverter031_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5211 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 9 | Inverter | Inverter031_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5212 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 10 | Inverter | Inverter031_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5213 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 10 | Inverter | Inverter031_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5214 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 11 | Inverter | Inverter031_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 11 | Inverter | Inverter031_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5216 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 12 | Inverter | Inverter031_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5217 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 12 | Inverter | Inverter031_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5218 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 13 | Inverter | Inverter031_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5219 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 13 | Inverter | Inverter031_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5220 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 14 | Inverter | Inverter031_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5221 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 14 | Inverter | Inverter031_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5222 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 15 | Inverter | Inverter031_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 15 | Inverter | Inverter031_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5224 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 16 | Inverter | Inverter031_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5225 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 16 | Inverter | Inverter031_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5226 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 17 | Inverter | Inverter031_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5227 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 17 | Inverter | Inverter031_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5228 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 18 | Inverter | Inverter031_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5229 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 18 | Inverter | Inverter031_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5230 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 19 | Inverter | Inverter031_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5231 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 19 | Inverter | Inverter031_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5232 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current DC Input 20 | Inverter | Inverter031_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5233 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC input 20 | Inverter | Inverter031_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5234 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current-AC | Inverter | inverter031_MODBUS.HR1007_i3Avg_A | Current-AC | 5235 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Current-DC | Inverter | inverter031_MODBUS.HR1062_idcInput_A | Current-DC | 5236 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Daily Energy Delivered | Inverter | inverter031_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5237 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power Set Point | Inverter | inverter031_MODBUS.HR0553_pRef | Real Power Set Point | 5238 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Reactive Power Set Point | Inverter | inverter031_MODBUS.HR0558_qRef | Reactive Power Set Point | 5239 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Frequency | Inverter | inverter031_MODBUS.HR1012_f3_Hz | Frequency | 5240 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV031 | Daggett 3_SUB1_INV031_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Insulation Resistance | Inverter | inverter031_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5241 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Number of DU Channels | Inverter | inverter031_MODBUS.HR0653_duChannels | Number of DU Channels | 5242 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Number of Running Modules | Inverter | inverter031_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5243 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Operating State | Inverter | inverter031_MODBUS.HR1123_currentStatus | Operating State | 5244 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Power Factor | Inverter | inverter031_MODBUS.HR1011_pf3 | Power Factor | 5245 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV031 | Daggett 3_SUB1_INV031_Ramp Down | Inverter | inverter031_MODBUS.HR0286_dropGradient_p | Ramp Down | 5246 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Ramp Up | Inverter | inverter031_MODBUS.HR0282_riseGradient_p | Ramp Up | 5247 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power Delivered | Inverter | inverter031_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5248 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Reactive Power Delivered | Inverter | inverter031_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5249 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power | 5250 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Reactive Power | Inverter | inverter031_MODBUS.HR1009_q3_kvar | Reactive Power | 5251 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Reactive Power Mode | Inverter | inverter031_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5252 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Reactive Power Set Point Percent | Inverter | inverter031_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5253 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power AC Percent | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5254 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power-AC | Inverter | inverter031_MODBUS.HR1008_p3_kW | Real Power-AC | 5255 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power-DC | Inverter | inverter031_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5256 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Air Intake | Inverter | inverter031_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5257 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Cabinet | Inverter | inverter031_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5258 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-IGBT | Inverter | inverter031_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5259 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Temperature-Module | Inverter | inverter031_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5260 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage A-B | Inverter | inverter031_MODBUS.HR1001_vRS_V | Voltage A-B | 5261 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage B-C | Inverter | inverter031_MODBUS.HR1002_vST_V | Voltage B-C | 5262 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage C-A | Inverter | inverter031_MODBUS.HR1003_vTR_V | Voltage C-A | 5263 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Voltage DC | Inverter | inverter031_MODBUS.HR1051_vdcBus_V | Voltage DC | 5264 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV031 | Daggett 3_SUB1_INV031_Fault Code 1 | Inverter | Inverter031_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Warning | Inverter | Inverter031_MODBUS.HRxxxx_currentWarning | Warning | 5266 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Internal Input Status | Inverter | Inverter031_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5267 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Internal Output Status | Inverter | Inverter031_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5268 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Module Fault Code | Inverter | Inverter031_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Internal Humidity | Inverter | Inverter031_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5270 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Humidity | Inverter | Inverter031_MODBUS.HRxxxx_humidity | Humidity | 5271 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_Comms Fault Time | Inverter | Inverter031_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5272 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Status | Inverter | Inverter031_MODBUS.HRxxxx_M1_status | Module Status | 5273 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 IR | Inverter | Inverter031_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 IS | Inverter | Inverter031_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 IT | Inverter | Inverter031_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5277 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5279 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5280 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 P | Inverter | Inverter031_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5281 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Q | Inverter | Inverter031_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5282 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5283 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5284 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M1 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5287 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Status | Inverter | Inverter031_MODBUS.HRxxxx_M2_status | Module Status | 5288 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 IR | Inverter | Inverter031_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 IS | Inverter | Inverter031_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 IT | Inverter | Inverter031_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5291 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5293 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5294 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5295 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 P | Inverter | Inverter031_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5296 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Q | Inverter | Inverter031_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5297 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5298 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5299 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5300 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5301 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M2 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5302 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Status | Inverter | Inverter031_MODBUS.HRxxxx_M3_status | Module Status | 5303 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 IR | Inverter | Inverter031_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 IS | Inverter | Inverter031_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 IT | Inverter | Inverter031_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5306 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5307 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5308 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5309 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5310 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 P | Inverter | Inverter031_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5311 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Q | Inverter | Inverter031_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5312 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5313 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5314 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5315 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5316 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M3 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5317 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Status | Inverter | Inverter031_MODBUS.HRxxxx_M4_status | Module Status | 5318 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 IR | Inverter | Inverter031_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5319 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 IS | Inverter | Inverter031_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 IT | Inverter | Inverter031_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5321 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5322 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5323 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5324 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5325 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 P | Inverter | Inverter031_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5326 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Q | Inverter | Inverter031_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5327 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5328 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5329 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5330 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M4 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5332 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Status | Inverter | Inverter031_MODBUS.HRxxxx_M5_status | Module Status | 5333 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 IR | Inverter | Inverter031_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 IS | Inverter | Inverter031_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 IT | Inverter | Inverter031_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5337 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5339 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5340 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 P | Inverter | Inverter031_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5341 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Q | Inverter | Inverter031_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5342 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5343 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5344 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5346 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M5 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5347 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Status | Inverter | Inverter031_MODBUS.HRxxxx_M6_status | Module Status | 5348 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 IR | Inverter | Inverter031_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5349 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 IS | Inverter | Inverter031_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 IT | Inverter | Inverter031_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 IDC | Inverter | Inverter031_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 VDCP | Inverter | Inverter031_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5353 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 VDCN | Inverter | Inverter031_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 VDC | Inverter | Inverter031_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5355 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 P | Inverter | Inverter031_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5356 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Q | Inverter | Inverter031_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5357 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Ambient Temp | Inverter | Inverter031_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5358 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Max IGBT Temp | Inverter | Inverter031_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5359 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 IO Status | Inverter | Inverter031_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5360 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Hardware Version | Inverter | Inverter031_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV031 | Daggett 3_SUB1_INV031_M6 Software Version | Inverter | Inverter031_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_A Phase Current | Inverter | inverter032_MODBUS.HR1004_i1_A | A Phase Current | 5363 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_B Phase Current | Inverter | inverter032_MODBUS.HR1005_i2_A | B Phase Current | 5364 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_C Phase Current | Inverter | inverter032_MODBUS.HR1006_i3_A | C Phase Current | 5365 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Bus Voltage | Inverter | inverter032_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5366 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV032 | Daggett 3_SUB1_INV032_Apparent Power | Inverter | inverter032_MODBUS.HR1010_s3_VA | Apparent Power | 5367 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 1 | Inverter | Inverter032_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC Input 1 | Inverter | Inverter032_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5369 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 2 | Inverter | Inverter032_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5370 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 2 | Inverter | Inverter032_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5371 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 3 | Inverter | Inverter032_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 3 | Inverter | Inverter032_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5373 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 4 | Inverter | Inverter032_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 4 | Inverter | Inverter032_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5375 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 5 | Inverter | Inverter032_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5376 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 5 | Inverter | Inverter032_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5377 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 6 | Inverter | Inverter032_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5378 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 6 | Inverter | Inverter032_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5379 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 7 | Inverter | Inverter032_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 7 | Inverter | Inverter032_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5381 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 8 | Inverter | Inverter032_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5382 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 8 | Inverter | Inverter032_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5383 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 9 | Inverter | Inverter032_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5384 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 9 | Inverter | Inverter032_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5385 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 10 | Inverter | Inverter032_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5386 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 10 | Inverter | Inverter032_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5387 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 11 | Inverter | Inverter032_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 11 | Inverter | Inverter032_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5389 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 12 | Inverter | Inverter032_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5390 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 12 | Inverter | Inverter032_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5391 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 13 | Inverter | Inverter032_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5392 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 13 | Inverter | Inverter032_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5393 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 14 | Inverter | Inverter032_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5394 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 14 | Inverter | Inverter032_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5395 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 15 | Inverter | Inverter032_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 15 | Inverter | Inverter032_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5397 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 16 | Inverter | Inverter032_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5398 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 16 | Inverter | Inverter032_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5399 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 17 | Inverter | Inverter032_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5400 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 17 | Inverter | Inverter032_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5401 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 18 | Inverter | Inverter032_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5402 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 18 | Inverter | Inverter032_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5403 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 19 | Inverter | Inverter032_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5404 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 19 | Inverter | Inverter032_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5405 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current DC Input 20 | Inverter | Inverter032_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5406 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC input 20 | Inverter | Inverter032_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5407 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current-AC | Inverter | inverter032_MODBUS.HR1007_i3Avg_A | Current-AC | 5408 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Current-DC | Inverter | inverter032_MODBUS.HR1062_idcInput_A | Current-DC | 5409 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Daily Energy Delivered | Inverter | inverter032_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5410 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power Set Point | Inverter | inverter032_MODBUS.HR0553_pRef | Real Power Set Point | 5411 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Reactive Power Set Point | Inverter | inverter032_MODBUS.HR0558_qRef | Reactive Power Set Point | 5412 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Frequency | Inverter | inverter032_MODBUS.HR1012_f3_Hz | Frequency | 5413 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV032 | Daggett 3_SUB1_INV032_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Insulation Resistance | Inverter | inverter032_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5414 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Number of DU Channels | Inverter | inverter032_MODBUS.HR0653_duChannels | Number of DU Channels | 5415 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Number of Running Modules | Inverter | inverter032_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5416 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Operating State | Inverter | inverter032_MODBUS.HR1123_currentStatus | Operating State | 5417 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Power Factor | Inverter | inverter032_MODBUS.HR1011_pf3 | Power Factor | 5418 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV032 | Daggett 3_SUB1_INV032_Ramp Down | Inverter | inverter032_MODBUS.HR0286_dropGradient_p | Ramp Down | 5419 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Ramp Up | Inverter | inverter032_MODBUS.HR0282_riseGradient_p | Ramp Up | 5420 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power Delivered | Inverter | inverter032_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5421 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Reactive Power Delivered | Inverter | inverter032_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5422 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power | 5423 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Reactive Power | Inverter | inverter032_MODBUS.HR1009_q3_kvar | Reactive Power | 5424 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Reactive Power Mode | Inverter | inverter032_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5425 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Reactive Power Set Point Percent | Inverter | inverter032_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5426 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power AC Percent | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5427 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power-AC | Inverter | inverter032_MODBUS.HR1008_p3_kW | Real Power-AC | 5428 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power-DC | Inverter | inverter032_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5429 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Air Intake | Inverter | inverter032_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5430 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Cabinet | Inverter | inverter032_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5431 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-IGBT | Inverter | inverter032_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5432 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Temperature-Module | Inverter | inverter032_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5433 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage A-B | Inverter | inverter032_MODBUS.HR1002_vRS_V | Voltage A-B | 5434 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage B-C | Inverter | inverter032_MODBUS.HR1002_vST_V | Voltage B-C | 5435 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage C-A | Inverter | inverter032_MODBUS.HR1003_vTR_V | Voltage C-A | 5436 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Voltage DC | Inverter | inverter032_MODBUS.HR1051_vdcBus_V | Voltage DC | 5437 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV032 | Daggett 3_SUB1_INV032_Fault Code 1 | Inverter | Inverter032_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Warning | Inverter | Inverter032_MODBUS.HRxxxx_currentWarning | Warning | 5439 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Internal Input Status | Inverter | Inverter032_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5440 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Internal Output Status | Inverter | Inverter032_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5441 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Module Fault Code | Inverter | Inverter032_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Internal Humidity | Inverter | Inverter032_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5443 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Humidity | Inverter | Inverter032_MODBUS.HRxxxx_humidity | Humidity | 5444 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_Comms Fault Time | Inverter | Inverter032_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5445 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Status | Inverter | Inverter032_MODBUS.HRxxxx_M1_status | Module Status | 5446 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 IR | Inverter | Inverter032_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 IS | Inverter | Inverter032_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 IT | Inverter | Inverter032_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5450 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5452 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5453 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 P | Inverter | Inverter032_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5454 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Q | Inverter | Inverter032_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5455 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5456 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5457 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M1 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5460 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Status | Inverter | Inverter032_MODBUS.HRxxxx_M2_status | Module Status | 5461 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 IR | Inverter | Inverter032_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 IS | Inverter | Inverter032_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 IT | Inverter | Inverter032_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5464 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5466 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5467 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5468 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 P | Inverter | Inverter032_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5469 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Q | Inverter | Inverter032_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5470 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5471 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5472 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5473 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5474 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M2 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5475 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Status | Inverter | Inverter032_MODBUS.HRxxxx_M3_status | Module Status | 5476 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 IR | Inverter | Inverter032_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 IS | Inverter | Inverter032_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 IT | Inverter | Inverter032_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5479 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5480 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5481 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5482 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5483 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 P | Inverter | Inverter032_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5484 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Q | Inverter | Inverter032_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5485 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5486 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5487 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5488 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5489 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M3 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5490 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Status | Inverter | Inverter032_MODBUS.HRxxxx_M4_status | Module Status | 5491 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 IR | Inverter | Inverter032_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5492 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 IS | Inverter | Inverter032_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 IT | Inverter | Inverter032_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5494 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5495 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5496 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5497 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5498 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 P | Inverter | Inverter032_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5499 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Q | Inverter | Inverter032_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5500 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5501 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5502 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5503 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M4 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5505 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Status | Inverter | Inverter032_MODBUS.HRxxxx_M5_status | Module Status | 5506 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 IR | Inverter | Inverter032_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 IS | Inverter | Inverter032_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 IT | Inverter | Inverter032_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5510 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5512 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5513 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 P | Inverter | Inverter032_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5514 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Q | Inverter | Inverter032_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5515 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5516 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5517 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5519 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M5 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5520 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Status | Inverter | Inverter032_MODBUS.HRxxxx_M6_status | Module Status | 5521 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 IR | Inverter | Inverter032_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5522 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 IS | Inverter | Inverter032_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 IT | Inverter | Inverter032_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 IDC | Inverter | Inverter032_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 VDCP | Inverter | Inverter032_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5526 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 VDCN | Inverter | Inverter032_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 VDC | Inverter | Inverter032_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5528 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 P | Inverter | Inverter032_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5529 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Q | Inverter | Inverter032_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5530 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Ambient Temp | Inverter | Inverter032_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5531 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Max IGBT Temp | Inverter | Inverter032_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5532 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 IO Status | Inverter | Inverter032_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5533 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Hardware Version | Inverter | Inverter032_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV032 | Daggett 3_SUB1_INV032_M6 Software Version | Inverter | Inverter032_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_A Phase Current | Inverter | inverter033_MODBUS.HR1004_i1_A | A Phase Current | 5536 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_B Phase Current | Inverter | inverter033_MODBUS.HR1005_i2_A | B Phase Current | 5537 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_C Phase Current | Inverter | inverter033_MODBUS.HR1006_i3_A | C Phase Current | 5538 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Bus Voltage | Inverter | inverter033_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5539 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV033 | Daggett 3_SUB1_INV033_Apparent Power | Inverter | inverter033_MODBUS.HR1010_s3_VA | Apparent Power | 5540 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 1 | Inverter | Inverter033_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC Input 1 | Inverter | Inverter033_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5542 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 2 | Inverter | Inverter033_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5543 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 2 | Inverter | Inverter033_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5544 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 3 | Inverter | Inverter033_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 3 | Inverter | Inverter033_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5546 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 4 | Inverter | Inverter033_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 4 | Inverter | Inverter033_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5548 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 5 | Inverter | Inverter033_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5549 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 5 | Inverter | Inverter033_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5550 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 6 | Inverter | Inverter033_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5551 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 6 | Inverter | Inverter033_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5552 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 7 | Inverter | Inverter033_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 7 | Inverter | Inverter033_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5554 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 8 | Inverter | Inverter033_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5555 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 8 | Inverter | Inverter033_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5556 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 9 | Inverter | Inverter033_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5557 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 9 | Inverter | Inverter033_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5558 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 10 | Inverter | Inverter033_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5559 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 10 | Inverter | Inverter033_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5560 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 11 | Inverter | Inverter033_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 11 | Inverter | Inverter033_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5562 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 12 | Inverter | Inverter033_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5563 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 12 | Inverter | Inverter033_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5564 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 13 | Inverter | Inverter033_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5565 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 13 | Inverter | Inverter033_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5566 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 14 | Inverter | Inverter033_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5567 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 14 | Inverter | Inverter033_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5568 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 15 | Inverter | Inverter033_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 15 | Inverter | Inverter033_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5570 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 16 | Inverter | Inverter033_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5571 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 16 | Inverter | Inverter033_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5572 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 17 | Inverter | Inverter033_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5573 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 17 | Inverter | Inverter033_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5574 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 18 | Inverter | Inverter033_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5575 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 18 | Inverter | Inverter033_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5576 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 19 | Inverter | Inverter033_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5577 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 19 | Inverter | Inverter033_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5578 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current DC Input 20 | Inverter | Inverter033_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5579 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC input 20 | Inverter | Inverter033_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5580 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current-AC | Inverter | inverter033_MODBUS.HR1007_i3Avg_A | Current-AC | 5581 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Current-DC | Inverter | inverter033_MODBUS.HR1062_idcInput_A | Current-DC | 5582 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Daily Energy Delivered | Inverter | inverter033_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5583 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power Set Point | Inverter | inverter033_MODBUS.HR0553_pRef | Real Power Set Point | 5584 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Reactive Power Set Point | Inverter | inverter033_MODBUS.HR0558_qRef | Reactive Power Set Point | 5585 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Frequency | Inverter | inverter033_MODBUS.HR1012_f3_Hz | Frequency | 5586 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV033 | Daggett 3_SUB1_INV033_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Insulation Resistance | Inverter | inverter033_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5587 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Number of DU Channels | Inverter | inverter033_MODBUS.HR0653_duChannels | Number of DU Channels | 5588 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Number of Running Modules | Inverter | inverter033_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5589 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Operating State | Inverter | inverter033_MODBUS.HR1123_currentStatus | Operating State | 5590 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Power Factor | Inverter | inverter033_MODBUS.HR1011_pf3 | Power Factor | 5591 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV033 | Daggett 3_SUB1_INV033_Ramp Down | Inverter | inverter033_MODBUS.HR0286_dropGradient_p | Ramp Down | 5592 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Ramp Up | Inverter | inverter033_MODBUS.HR0282_riseGradient_p | Ramp Up | 5593 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power Delivered | Inverter | inverter033_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5594 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Reactive Power Delivered | Inverter | inverter033_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5595 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power | 5596 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Reactive Power | Inverter | inverter033_MODBUS.HR1009_q3_kvar | Reactive Power | 5597 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Reactive Power Mode | Inverter | inverter033_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5598 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Reactive Power Set Point Percent | Inverter | inverter033_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5599 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power AC Percent | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5600 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power-AC | Inverter | inverter033_MODBUS.HR1008_p3_kW | Real Power-AC | 5601 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power-DC | Inverter | inverter033_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5602 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Air Intake | Inverter | inverter033_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5603 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Cabinet | Inverter | inverter033_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5604 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-IGBT | Inverter | inverter033_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5605 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Temperature-Module | Inverter | inverter033_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5606 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage A-B | Inverter | inverter033_MODBUS.HR1003_vRS_V | Voltage A-B | 5607 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage B-C | Inverter | inverter033_MODBUS.HR1002_vST_V | Voltage B-C | 5608 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage C-A | Inverter | inverter033_MODBUS.HR1003_vTR_V | Voltage C-A | 5609 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Voltage DC | Inverter | inverter033_MODBUS.HR1051_vdcBus_V | Voltage DC | 5610 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV033 | Daggett 3_SUB1_INV033_Fault Code 1 | Inverter | Inverter033_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Warning | Inverter | Inverter033_MODBUS.HRxxxx_currentWarning | Warning | 5612 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Internal Input Status | Inverter | Inverter033_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5613 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Internal Output Status | Inverter | Inverter033_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5614 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Module Fault Code | Inverter | Inverter033_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Internal Humidity | Inverter | Inverter033_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5616 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Humidity | Inverter | Inverter033_MODBUS.HRxxxx_humidity | Humidity | 5617 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_Comms Fault Time | Inverter | Inverter033_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5618 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Status | Inverter | Inverter033_MODBUS.HRxxxx_M1_status | Module Status | 5619 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 IR | Inverter | Inverter033_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 IS | Inverter | Inverter033_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 IT | Inverter | Inverter033_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5623 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5625 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5626 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 P | Inverter | Inverter033_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5627 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Q | Inverter | Inverter033_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5628 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5629 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5630 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M1 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5633 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Status | Inverter | Inverter033_MODBUS.HRxxxx_M2_status | Module Status | 5634 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 IR | Inverter | Inverter033_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 IS | Inverter | Inverter033_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 IT | Inverter | Inverter033_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5637 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5639 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5640 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5641 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 P | Inverter | Inverter033_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5642 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Q | Inverter | Inverter033_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5643 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5644 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5645 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5646 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5647 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M2 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5648 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Status | Inverter | Inverter033_MODBUS.HRxxxx_M3_status | Module Status | 5649 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 IR | Inverter | Inverter033_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 IS | Inverter | Inverter033_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 IT | Inverter | Inverter033_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5652 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5653 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5654 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5655 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5656 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 P | Inverter | Inverter033_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5657 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Q | Inverter | Inverter033_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5658 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5659 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5660 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5661 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5662 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M3 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5663 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Status | Inverter | Inverter033_MODBUS.HRxxxx_M4_status | Module Status | 5664 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 IR | Inverter | Inverter033_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5665 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 IS | Inverter | Inverter033_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 IT | Inverter | Inverter033_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5667 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5668 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5669 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5670 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5671 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 P | Inverter | Inverter033_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5672 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Q | Inverter | Inverter033_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5673 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5674 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5675 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5676 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M4 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5678 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Status | Inverter | Inverter033_MODBUS.HRxxxx_M5_status | Module Status | 5679 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 IR | Inverter | Inverter033_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 IS | Inverter | Inverter033_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 IT | Inverter | Inverter033_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5683 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5685 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5686 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 P | Inverter | Inverter033_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5687 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Q | Inverter | Inverter033_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5688 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5689 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5690 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5692 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M5 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5693 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Status | Inverter | Inverter033_MODBUS.HRxxxx_M6_status | Module Status | 5694 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 IR | Inverter | Inverter033_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5695 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 IS | Inverter | Inverter033_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 IT | Inverter | Inverter033_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 IDC | Inverter | Inverter033_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 VDCP | Inverter | Inverter033_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5699 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 VDCN | Inverter | Inverter033_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 VDC | Inverter | Inverter033_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5701 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 P | Inverter | Inverter033_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5702 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Q | Inverter | Inverter033_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5703 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Ambient Temp | Inverter | Inverter033_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5704 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Max IGBT Temp | Inverter | Inverter033_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5705 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 IO Status | Inverter | Inverter033_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5706 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Hardware Version | Inverter | Inverter033_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV033 | Daggett 3_SUB1_INV033_M6 Software Version | Inverter | Inverter033_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_A Phase Current | Inverter | inverter034_MODBUS.HR1004_i1_A | A Phase Current | 5709 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_B Phase Current | Inverter | inverter034_MODBUS.HR1005_i2_A | B Phase Current | 5710 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_C Phase Current | Inverter | inverter034_MODBUS.HR1006_i3_A | C Phase Current | 5711 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Bus Voltage | Inverter | inverter034_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5712 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV034 | Daggett 3_SUB1_INV034_Apparent Power | Inverter | inverter034_MODBUS.HR1010_s3_VA | Apparent Power | 5713 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 1 | Inverter | Inverter034_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC Input 1 | Inverter | Inverter034_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5715 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 2 | Inverter | Inverter034_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5716 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 2 | Inverter | Inverter034_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5717 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 3 | Inverter | Inverter034_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 3 | Inverter | Inverter034_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5719 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 4 | Inverter | Inverter034_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 4 | Inverter | Inverter034_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5721 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 5 | Inverter | Inverter034_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5722 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 5 | Inverter | Inverter034_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5723 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 6 | Inverter | Inverter034_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5724 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 6 | Inverter | Inverter034_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5725 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 7 | Inverter | Inverter034_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 7 | Inverter | Inverter034_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5727 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 8 | Inverter | Inverter034_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5728 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 8 | Inverter | Inverter034_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5729 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 9 | Inverter | Inverter034_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5730 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 9 | Inverter | Inverter034_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5731 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 10 | Inverter | Inverter034_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5732 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 10 | Inverter | Inverter034_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5733 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 11 | Inverter | Inverter034_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 11 | Inverter | Inverter034_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5735 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 12 | Inverter | Inverter034_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5736 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 12 | Inverter | Inverter034_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5737 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 13 | Inverter | Inverter034_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5738 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 13 | Inverter | Inverter034_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5739 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 14 | Inverter | Inverter034_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5740 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 14 | Inverter | Inverter034_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5741 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 15 | Inverter | Inverter034_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 15 | Inverter | Inverter034_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5743 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 16 | Inverter | Inverter034_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5744 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 16 | Inverter | Inverter034_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5745 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 17 | Inverter | Inverter034_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5746 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 17 | Inverter | Inverter034_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5747 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 18 | Inverter | Inverter034_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5748 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 18 | Inverter | Inverter034_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5749 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 19 | Inverter | Inverter034_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5750 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 19 | Inverter | Inverter034_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5751 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current DC Input 20 | Inverter | Inverter034_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5752 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC input 20 | Inverter | Inverter034_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5753 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current-AC | Inverter | inverter034_MODBUS.HR1007_i3Avg_A | Current-AC | 5754 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Current-DC | Inverter | inverter034_MODBUS.HR1062_idcInput_A | Current-DC | 5755 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Daily Energy Delivered | Inverter | inverter034_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5756 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power Set Point | Inverter | inverter034_MODBUS.HR0553_pRef | Real Power Set Point | 5757 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Reactive Power Set Point | Inverter | inverter034_MODBUS.HR0558_qRef | Reactive Power Set Point | 5758 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Frequency | Inverter | inverter034_MODBUS.HR1012_f3_Hz | Frequency | 5759 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV034 | Daggett 3_SUB1_INV034_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Insulation Resistance | Inverter | inverter034_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5760 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Number of DU Channels | Inverter | inverter034_MODBUS.HR0653_duChannels | Number of DU Channels | 5761 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Number of Running Modules | Inverter | inverter034_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5762 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Operating State | Inverter | inverter034_MODBUS.HR1123_currentStatus | Operating State | 5763 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Power Factor | Inverter | inverter034_MODBUS.HR1011_pf3 | Power Factor | 5764 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV034 | Daggett 3_SUB1_INV034_Ramp Down | Inverter | inverter034_MODBUS.HR0286_dropGradient_p | Ramp Down | 5765 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Ramp Up | Inverter | inverter034_MODBUS.HR0282_riseGradient_p | Ramp Up | 5766 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power Delivered | Inverter | inverter034_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5767 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Reactive Power Delivered | Inverter | inverter034_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5768 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power | 5769 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Reactive Power | Inverter | inverter034_MODBUS.HR1009_q3_kvar | Reactive Power | 5770 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Reactive Power Mode | Inverter | inverter034_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5771 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Reactive Power Set Point Percent | Inverter | inverter034_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5772 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power AC Percent | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5773 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power-AC | Inverter | inverter034_MODBUS.HR1008_p3_kW | Real Power-AC | 5774 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power-DC | Inverter | inverter034_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5775 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Air Intake | Inverter | inverter034_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5776 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Cabinet | Inverter | inverter034_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5777 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-IGBT | Inverter | inverter034_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5778 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Temperature-Module | Inverter | inverter034_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5779 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage A-B | Inverter | inverter034_MODBUS.HR1004_vRS_V | Voltage A-B | 5780 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage B-C | Inverter | inverter034_MODBUS.HR1002_vST_V | Voltage B-C | 5781 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage C-A | Inverter | inverter034_MODBUS.HR1003_vTR_V | Voltage C-A | 5782 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Voltage DC | Inverter | inverter034_MODBUS.HR1051_vdcBus_V | Voltage DC | 5783 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV034 | Daggett 3_SUB1_INV034_Fault Code 1 | Inverter | Inverter034_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Warning | Inverter | Inverter034_MODBUS.HRxxxx_currentWarning | Warning | 5785 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Internal Input Status | Inverter | Inverter034_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5786 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Internal Output Status | Inverter | Inverter034_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5787 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Module Fault Code | Inverter | Inverter034_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Internal Humidity | Inverter | Inverter034_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5789 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Humidity | Inverter | Inverter034_MODBUS.HRxxxx_humidity | Humidity | 5790 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_Comms Fault Time | Inverter | Inverter034_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5791 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Status | Inverter | Inverter034_MODBUS.HRxxxx_M1_status | Module Status | 5792 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 IR | Inverter | Inverter034_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 IS | Inverter | Inverter034_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 IT | Inverter | Inverter034_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5796 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5798 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5799 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 P | Inverter | Inverter034_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5800 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Q | Inverter | Inverter034_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5801 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5802 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5803 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M1 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5806 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Status | Inverter | Inverter034_MODBUS.HRxxxx_M2_status | Module Status | 5807 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 IR | Inverter | Inverter034_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 IS | Inverter | Inverter034_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 IT | Inverter | Inverter034_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5810 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5812 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5813 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5814 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 P | Inverter | Inverter034_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5815 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Q | Inverter | Inverter034_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5816 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5817 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5818 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5819 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5820 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M2 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5821 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Status | Inverter | Inverter034_MODBUS.HRxxxx_M3_status | Module Status | 5822 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 IR | Inverter | Inverter034_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 IS | Inverter | Inverter034_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 IT | Inverter | Inverter034_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5825 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5826 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 5827 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 5828 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 5829 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 P | Inverter | Inverter034_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 5830 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Q | Inverter | Inverter034_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 5831 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 5832 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 5833 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 5834 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 5835 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M3 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 5836 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Status | Inverter | Inverter034_MODBUS.HRxxxx_M4_status | Module Status | 5837 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 IR | Inverter | Inverter034_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 5838 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 IS | Inverter | Inverter034_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 5839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 IT | Inverter | Inverter034_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 5840 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 5841 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 5842 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 5843 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 5844 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 P | Inverter | Inverter034_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 5845 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Q | Inverter | Inverter034_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 5846 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 5847 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 5848 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 5849 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 5850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M4 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 5851 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Status | Inverter | Inverter034_MODBUS.HRxxxx_M5_status | Module Status | 5852 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 IR | Inverter | Inverter034_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 5853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 IS | Inverter | Inverter034_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 5854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 IT | Inverter | Inverter034_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 5855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 5856 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 5857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 5858 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 5859 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 P | Inverter | Inverter034_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 5860 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Q | Inverter | Inverter034_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 5861 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 5862 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 5863 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 5864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 5865 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M5 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 5866 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Status | Inverter | Inverter034_MODBUS.HRxxxx_M6_status | Module Status | 5867 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 IR | Inverter | Inverter034_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 5868 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 IS | Inverter | Inverter034_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 5869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 IT | Inverter | Inverter034_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 5870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 IDC | Inverter | Inverter034_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 5871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 VDCP | Inverter | Inverter034_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 5872 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 VDCN | Inverter | Inverter034_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 5873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 VDC | Inverter | Inverter034_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 5874 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 P | Inverter | Inverter034_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 5875 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Q | Inverter | Inverter034_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 5876 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Ambient Temp | Inverter | Inverter034_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 5877 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Max IGBT Temp | Inverter | Inverter034_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 5878 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 IO Status | Inverter | Inverter034_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 5879 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Hardware Version | Inverter | Inverter034_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 5880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV034 | Daggett 3_SUB1_INV034_M6 Software Version | Inverter | Inverter034_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 5881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_A Phase Current | Inverter | inverter035_MODBUS.HR1004_i1_A | A Phase Current | 5882 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_B Phase Current | Inverter | inverter035_MODBUS.HR1005_i2_A | B Phase Current | 5883 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_C Phase Current | Inverter | inverter035_MODBUS.HR1006_i3_A | C Phase Current | 5884 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Bus Voltage | Inverter | inverter035_MODBUS.HR1051_vdcBus_V | Bus Voltage | 5885 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV035 | Daggett 3_SUB1_INV035_Apparent Power | Inverter | inverter035_MODBUS.HR1010_s3_VA | Apparent Power | 5886 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 1 | Inverter | Inverter035_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC Input 1 | Inverter | Inverter035_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 5888 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 2 | Inverter | Inverter035_MODBUS.HR5811_du2_idc_A | Current DC Input# | 5889 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 2 | Inverter | Inverter035_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 5890 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 3 | Inverter | Inverter035_MODBUS.HR5817_du3_idc_A | Current DC Input# | 5891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 3 | Inverter | Inverter035_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 5892 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 4 | Inverter | Inverter035_MODBUS.HR5823_du4_idc_A | Current DC Input# | 5893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 4 | Inverter | Inverter035_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 5894 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 5 | Inverter | Inverter035_MODBUS.HR5829_du5_idc_A | Current DC Input# | 5895 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 5 | Inverter | Inverter035_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 5896 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 6 | Inverter | Inverter035_MODBUS.HR5835_du6_idc_A | Current DC Input# | 5897 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 6 | Inverter | Inverter035_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 5898 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 7 | Inverter | Inverter035_MODBUS.HR5841_du7_idc_A | Current DC Input# | 5899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 7 | Inverter | Inverter035_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 5900 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 8 | Inverter | Inverter035_MODBUS.HR5847_du8_idc_A | Current DC Input# | 5901 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 8 | Inverter | Inverter035_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 5902 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 9 | Inverter | Inverter035_MODBUS.HR5853_du9_idc_A | Current DC Input# | 5903 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 9 | Inverter | Inverter035_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 5904 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 10 | Inverter | Inverter035_MODBUS.HR5859_du10_idc_A | Current DC Input# | 5905 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 10 | Inverter | Inverter035_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 5906 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 11 | Inverter | Inverter035_MODBUS.HR5865_du11_idc_A | Current DC Input# | 5907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 11 | Inverter | Inverter035_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 5908 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 12 | Inverter | Inverter035_MODBUS.HR5871_du12_idc_A | Current DC Input# | 5909 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 12 | Inverter | Inverter035_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 5910 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 13 | Inverter | Inverter035_MODBUS.HR5877_du13_idc_A | Current DC Input# | 5911 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 13 | Inverter | Inverter035_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 5912 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 14 | Inverter | Inverter035_MODBUS.HR5883_du14_idc_A | Current DC Input# | 5913 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 14 | Inverter | Inverter035_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 5914 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 15 | Inverter | Inverter035_MODBUS.HR5889_du15_idc_A | Current DC Input# | 5915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 15 | Inverter | Inverter035_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 5916 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 16 | Inverter | Inverter035_MODBUS.HR5895_du16_idc_A | Current DC Input# | 5917 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 16 | Inverter | Inverter035_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 5918 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 17 | Inverter | Inverter035_MODBUS.HR5901_du17_idc_A | Current DC Input# | 5919 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 17 | Inverter | Inverter035_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 5920 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 18 | Inverter | Inverter035_MODBUS.HR5907_du18_idc_A | Current DC Input# | 5921 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 18 | Inverter | Inverter035_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 5922 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 19 | Inverter | Inverter035_MODBUS.HR5913_du19_idc_A | Current DC Input# | 5923 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 19 | Inverter | Inverter035_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 5924 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current DC Input 20 | Inverter | Inverter035_MODBUS.HR5919_du20_idc_A | Current DC Input# | 5925 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC input 20 | Inverter | Inverter035_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 5926 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current-AC | Inverter | inverter035_MODBUS.HR1007_i3Avg_A | Current-AC | 5927 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Current-DC | Inverter | inverter035_MODBUS.HR1062_idcInput_A | Current-DC | 5928 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Daily Energy Delivered | Inverter | inverter035_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 5929 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power Set Point | Inverter | inverter035_MODBUS.HR0553_pRef | Real Power Set Point | 5930 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Reactive Power Set Point | Inverter | inverter035_MODBUS.HR0558_qRef | Reactive Power Set Point | 5931 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Frequency | Inverter | inverter035_MODBUS.HR1012_f3_Hz | Frequency | 5932 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV035 | Daggett 3_SUB1_INV035_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Insulation Resistance | Inverter | inverter035_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 5933 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Number of DU Channels | Inverter | inverter035_MODBUS.HR0653_duChannels | Number of DU Channels | 5934 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Number of Running Modules | Inverter | inverter035_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 5935 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Operating State | Inverter | inverter035_MODBUS.HR1123_currentStatus | Operating State | 5936 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Power Factor | Inverter | inverter035_MODBUS.HR1011_pf3 | Power Factor | 5937 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV035 | Daggett 3_SUB1_INV035_Ramp Down | Inverter | inverter035_MODBUS.HR0286_dropGradient_p | Ramp Down | 5938 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Ramp Up | Inverter | inverter035_MODBUS.HR0282_riseGradient_p | Ramp Up | 5939 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power Delivered | Inverter | inverter035_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 5940 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Reactive Power Delivered | Inverter | inverter035_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 5941 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power | 5942 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Reactive Power | Inverter | inverter035_MODBUS.HR1009_q3_kvar | Reactive Power | 5943 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Reactive Power Mode | Inverter | inverter035_MODBUS.HR0552_qControlMode | Reactive Power Mode | 5944 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Reactive Power Set Point Percent | Inverter | inverter035_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 5945 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power AC Percent | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power AC Percent | 5946 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power-AC | Inverter | inverter035_MODBUS.HR1008_p3_kW | Real Power-AC | 5947 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power-DC | Inverter | inverter035_MODBUS.HR1061_pdcInput_W | Real Power-DC | 5948 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Air Intake | Inverter | inverter035_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 5949 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Cabinet | Inverter | inverter035_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 5950 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-IGBT | Inverter | inverter035_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 5951 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Temperature-Module | Inverter | inverter035_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 5952 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage A-B | Inverter | inverter035_MODBUS.HR1005_vRS_V | Voltage A-B | 5953 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage B-C | Inverter | inverter035_MODBUS.HR1002_vST_V | Voltage B-C | 5954 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage C-A | Inverter | inverter035_MODBUS.HR1003_vTR_V | Voltage C-A | 5955 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Voltage DC | Inverter | inverter035_MODBUS.HR1051_vdcBus_V | Voltage DC | 5956 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV035 | Daggett 3_SUB1_INV035_Fault Code 1 | Inverter | Inverter035_MODBUS.HRxxxx_currentFault | Fault Code 1 | 5957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Warning | Inverter | Inverter035_MODBUS.HRxxxx_currentWarning | Warning | 5958 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Internal Input Status | Inverter | Inverter035_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 5959 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Internal Output Status | Inverter | Inverter035_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 5960 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Module Fault Code | Inverter | Inverter035_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 5961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Internal Humidity | Inverter | Inverter035_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 5962 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Humidity | Inverter | Inverter035_MODBUS.HRxxxx_humidity | Humidity | 5963 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_Comms Fault Time | Inverter | Inverter035_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 5964 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Status | Inverter | Inverter035_MODBUS.HRxxxx_M1_status | Module Status | 5965 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 IR | Inverter | Inverter035_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 5966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 IS | Inverter | Inverter035_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 5967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 IT | Inverter | Inverter035_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 5968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 5969 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 5970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 5971 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 5972 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 P | Inverter | Inverter035_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 5973 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Q | Inverter | Inverter035_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 5974 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 5975 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 5976 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 5977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 5978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M1 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 5979 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Status | Inverter | Inverter035_MODBUS.HRxxxx_M2_status | Module Status | 5980 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 IR | Inverter | Inverter035_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 5981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 IS | Inverter | Inverter035_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 5982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 IT | Inverter | Inverter035_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 5983 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 5984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 5985 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 5986 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 5987 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 P | Inverter | Inverter035_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 5988 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Q | Inverter | Inverter035_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 5989 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 5990 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 5991 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 5992 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 5993 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M2 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 5994 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Status | Inverter | Inverter035_MODBUS.HRxxxx_M3_status | Module Status | 5995 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 IR | Inverter | Inverter035_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 5996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 IS | Inverter | Inverter035_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 5997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 IT | Inverter | Inverter035_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 5998 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 5999 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6000 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6001 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6002 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 P | Inverter | Inverter035_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6003 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Q | Inverter | Inverter035_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6004 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6005 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6006 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6007 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6008 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M3 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6009 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Status | Inverter | Inverter035_MODBUS.HRxxxx_M4_status | Module Status | 6010 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 IR | Inverter | Inverter035_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6011 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 IS | Inverter | Inverter035_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 IT | Inverter | Inverter035_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6013 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6014 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6015 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6016 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6017 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 P | Inverter | Inverter035_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6018 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Q | Inverter | Inverter035_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6019 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6020 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6021 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6022 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M4 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6024 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Status | Inverter | Inverter035_MODBUS.HRxxxx_M5_status | Module Status | 6025 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 IR | Inverter | Inverter035_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 IS | Inverter | Inverter035_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 IT | Inverter | Inverter035_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6029 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6031 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6032 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 P | Inverter | Inverter035_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6033 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Q | Inverter | Inverter035_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6034 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6035 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6036 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6038 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M5 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6039 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Status | Inverter | Inverter035_MODBUS.HRxxxx_M6_status | Module Status | 6040 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 IR | Inverter | Inverter035_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6041 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 IS | Inverter | Inverter035_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 IT | Inverter | Inverter035_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 IDC | Inverter | Inverter035_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 VDCP | Inverter | Inverter035_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6045 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 VDCN | Inverter | Inverter035_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 VDC | Inverter | Inverter035_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6047 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 P | Inverter | Inverter035_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6048 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Q | Inverter | Inverter035_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6049 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Ambient Temp | Inverter | Inverter035_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6050 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Max IGBT Temp | Inverter | Inverter035_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6051 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 IO Status | Inverter | Inverter035_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6052 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Hardware Version | Inverter | Inverter035_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV035 | Daggett 3_SUB1_INV035_M6 Software Version | Inverter | Inverter035_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_A Phase Current | Inverter | inverter036_MODBUS.HR1004_i1_A | A Phase Current | 6055 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_B Phase Current | Inverter | inverter036_MODBUS.HR1005_i2_A | B Phase Current | 6056 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_C Phase Current | Inverter | inverter036_MODBUS.HR1006_i3_A | C Phase Current | 6057 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Bus Voltage | Inverter | inverter036_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6058 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV036 | Daggett 3_SUB1_INV036_Apparent Power | Inverter | inverter036_MODBUS.HR1010_s3_VA | Apparent Power | 6059 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 1 | Inverter | Inverter036_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC Input 1 | Inverter | Inverter036_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6061 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 2 | Inverter | Inverter036_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6062 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 2 | Inverter | Inverter036_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6063 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 3 | Inverter | Inverter036_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 3 | Inverter | Inverter036_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6065 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 4 | Inverter | Inverter036_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 4 | Inverter | Inverter036_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6067 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 5 | Inverter | Inverter036_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6068 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 5 | Inverter | Inverter036_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6069 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 6 | Inverter | Inverter036_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6070 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 6 | Inverter | Inverter036_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6071 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 7 | Inverter | Inverter036_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 7 | Inverter | Inverter036_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6073 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 8 | Inverter | Inverter036_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6074 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 8 | Inverter | Inverter036_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6075 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 9 | Inverter | Inverter036_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6076 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 9 | Inverter | Inverter036_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6077 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 10 | Inverter | Inverter036_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6078 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 10 | Inverter | Inverter036_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6079 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 11 | Inverter | Inverter036_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 11 | Inverter | Inverter036_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6081 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 12 | Inverter | Inverter036_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6082 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 12 | Inverter | Inverter036_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6083 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 13 | Inverter | Inverter036_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6084 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 13 | Inverter | Inverter036_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6085 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 14 | Inverter | Inverter036_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6086 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 14 | Inverter | Inverter036_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6087 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 15 | Inverter | Inverter036_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 15 | Inverter | Inverter036_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6089 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 16 | Inverter | Inverter036_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6090 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 16 | Inverter | Inverter036_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6091 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 17 | Inverter | Inverter036_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6092 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 17 | Inverter | Inverter036_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6093 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 18 | Inverter | Inverter036_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6094 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 18 | Inverter | Inverter036_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6095 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 19 | Inverter | Inverter036_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6096 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 19 | Inverter | Inverter036_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6097 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current DC Input 20 | Inverter | Inverter036_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6098 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC input 20 | Inverter | Inverter036_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6099 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current-AC | Inverter | inverter036_MODBUS.HR1007_i3Avg_A | Current-AC | 6100 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Current-DC | Inverter | inverter036_MODBUS.HR1062_idcInput_A | Current-DC | 6101 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Daily Energy Delivered | Inverter | inverter036_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6102 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power Set Point | Inverter | inverter036_MODBUS.HR0553_pRef | Real Power Set Point | 6103 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Reactive Power Set Point | Inverter | inverter036_MODBUS.HR0558_qRef | Reactive Power Set Point | 6104 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Frequency | Inverter | inverter036_MODBUS.HR1012_f3_Hz | Frequency | 6105 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV036 | Daggett 3_SUB1_INV036_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Insulation Resistance | Inverter | inverter036_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6106 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Number of DU Channels | Inverter | inverter036_MODBUS.HR0653_duChannels | Number of DU Channels | 6107 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Number of Running Modules | Inverter | inverter036_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6108 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Operating State | Inverter | inverter036_MODBUS.HR1123_currentStatus | Operating State | 6109 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Power Factor | Inverter | inverter036_MODBUS.HR1011_pf3 | Power Factor | 6110 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV036 | Daggett 3_SUB1_INV036_Ramp Down | Inverter | inverter036_MODBUS.HR0286_dropGradient_p | Ramp Down | 6111 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Ramp Up | Inverter | inverter036_MODBUS.HR0282_riseGradient_p | Ramp Up | 6112 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power Delivered | Inverter | inverter036_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6113 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Reactive Power Delivered | Inverter | inverter036_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6114 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power | 6115 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Reactive Power | Inverter | inverter036_MODBUS.HR1009_q3_kvar | Reactive Power | 6116 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Reactive Power Mode | Inverter | inverter036_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6117 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Reactive Power Set Point Percent | Inverter | inverter036_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6118 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power AC Percent | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6119 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power-AC | Inverter | inverter036_MODBUS.HR1008_p3_kW | Real Power-AC | 6120 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power-DC | Inverter | inverter036_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6121 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Air Intake | Inverter | inverter036_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6122 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Cabinet | Inverter | inverter036_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6123 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-IGBT | Inverter | inverter036_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6124 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Temperature-Module | Inverter | inverter036_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6125 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage A-B | Inverter | inverter036_MODBUS.HR1006_vRS_V | Voltage A-B | 6126 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage B-C | Inverter | inverter036_MODBUS.HR1002_vST_V | Voltage B-C | 6127 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage C-A | Inverter | inverter036_MODBUS.HR1003_vTR_V | Voltage C-A | 6128 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Voltage DC | Inverter | inverter036_MODBUS.HR1051_vdcBus_V | Voltage DC | 6129 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV036 | Daggett 3_SUB1_INV036_Fault Code 1 | Inverter | Inverter036_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6130 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Warning | Inverter | Inverter036_MODBUS.HRxxxx_currentWarning | Warning | 6131 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Internal Input Status | Inverter | Inverter036_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6132 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Internal Output Status | Inverter | Inverter036_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6133 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Module Fault Code | Inverter | Inverter036_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Internal Humidity | Inverter | Inverter036_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6135 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Humidity | Inverter | Inverter036_MODBUS.HRxxxx_humidity | Humidity | 6136 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_Comms Fault Time | Inverter | Inverter036_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6137 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Status | Inverter | Inverter036_MODBUS.HRxxxx_M1_status | Module Status | 6138 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 IR | Inverter | Inverter036_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 IS | Inverter | Inverter036_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 IT | Inverter | Inverter036_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6142 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6144 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6145 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 P | Inverter | Inverter036_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6146 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Q | Inverter | Inverter036_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6147 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6148 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6149 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M1 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6152 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Status | Inverter | Inverter036_MODBUS.HRxxxx_M2_status | Module Status | 6153 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 IR | Inverter | Inverter036_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6154 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 IS | Inverter | Inverter036_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 IT | Inverter | Inverter036_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6156 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6158 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6159 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6160 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 P | Inverter | Inverter036_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6161 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Q | Inverter | Inverter036_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6162 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6163 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6164 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6165 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6166 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M2 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6167 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Status | Inverter | Inverter036_MODBUS.HRxxxx_M3_status | Module Status | 6168 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 IR | Inverter | Inverter036_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 IS | Inverter | Inverter036_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6170 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 IT | Inverter | Inverter036_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6171 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6172 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6173 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6174 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6175 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 P | Inverter | Inverter036_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6176 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Q | Inverter | Inverter036_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6177 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6178 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6179 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6180 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6181 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M3 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6182 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Status | Inverter | Inverter036_MODBUS.HRxxxx_M4_status | Module Status | 6183 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 IR | Inverter | Inverter036_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 IS | Inverter | Inverter036_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 IT | Inverter | Inverter036_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6186 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6187 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6188 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6189 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6190 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 P | Inverter | Inverter036_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6191 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Q | Inverter | Inverter036_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6192 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6193 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6194 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6195 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M4 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6197 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Status | Inverter | Inverter036_MODBUS.HRxxxx_M5_status | Module Status | 6198 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 IR | Inverter | Inverter036_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 IS | Inverter | Inverter036_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 IT | Inverter | Inverter036_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6202 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6204 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6205 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 P | Inverter | Inverter036_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6206 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Q | Inverter | Inverter036_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6207 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6208 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6209 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6211 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M5 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6212 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Status | Inverter | Inverter036_MODBUS.HRxxxx_M6_status | Module Status | 6213 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 IR | Inverter | Inverter036_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 IS | Inverter | Inverter036_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 IT | Inverter | Inverter036_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 IDC | Inverter | Inverter036_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6217 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 VDCP | Inverter | Inverter036_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6218 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 VDCN | Inverter | Inverter036_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6219 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 VDC | Inverter | Inverter036_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6220 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 P | Inverter | Inverter036_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6221 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Q | Inverter | Inverter036_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6222 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Ambient Temp | Inverter | Inverter036_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6223 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Max IGBT Temp | Inverter | Inverter036_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6224 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 IO Status | Inverter | Inverter036_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6225 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Hardware Version | Inverter | Inverter036_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6226 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV036 | Daggett 3_SUB1_INV036_M6 Software Version | Inverter | Inverter036_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_A Phase Current | Inverter | inverter037_MODBUS.HR1004_i1_A | A Phase Current | 6228 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_B Phase Current | Inverter | inverter037_MODBUS.HR1005_i2_A | B Phase Current | 6229 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_C Phase Current | Inverter | inverter037_MODBUS.HR1006_i3_A | C Phase Current | 6230 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Bus Voltage | Inverter | inverter037_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6231 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV037 | Daggett 3_SUB1_INV037_Apparent Power | Inverter | inverter037_MODBUS.HR1010_s3_VA | Apparent Power | 6232 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 1 | Inverter | Inverter037_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6233 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC Input 1 | Inverter | Inverter037_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6234 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 2 | Inverter | Inverter037_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6235 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 2 | Inverter | Inverter037_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6236 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 3 | Inverter | Inverter037_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 3 | Inverter | Inverter037_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6238 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 4 | Inverter | Inverter037_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 4 | Inverter | Inverter037_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6240 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 5 | Inverter | Inverter037_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6241 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 5 | Inverter | Inverter037_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6242 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 6 | Inverter | Inverter037_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6243 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 6 | Inverter | Inverter037_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6244 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 7 | Inverter | Inverter037_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6245 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 7 | Inverter | Inverter037_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6246 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 8 | Inverter | Inverter037_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6247 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 8 | Inverter | Inverter037_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6248 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 9 | Inverter | Inverter037_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6249 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 9 | Inverter | Inverter037_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6250 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 10 | Inverter | Inverter037_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6251 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 10 | Inverter | Inverter037_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6252 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 11 | Inverter | Inverter037_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 11 | Inverter | Inverter037_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6254 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 12 | Inverter | Inverter037_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6255 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 12 | Inverter | Inverter037_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6256 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 13 | Inverter | Inverter037_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6257 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 13 | Inverter | Inverter037_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6258 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 14 | Inverter | Inverter037_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 14 | Inverter | Inverter037_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6260 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 15 | Inverter | Inverter037_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6261 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 15 | Inverter | Inverter037_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6262 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 16 | Inverter | Inverter037_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6263 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 16 | Inverter | Inverter037_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6264 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 17 | Inverter | Inverter037_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6265 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 17 | Inverter | Inverter037_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6266 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 18 | Inverter | Inverter037_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6267 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 18 | Inverter | Inverter037_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6268 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 19 | Inverter | Inverter037_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6269 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 19 | Inverter | Inverter037_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6270 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current DC Input 20 | Inverter | Inverter037_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6271 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC input 20 | Inverter | Inverter037_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6272 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current-AC | Inverter | inverter037_MODBUS.HR1007_i3Avg_A | Current-AC | 6273 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Current-DC | Inverter | inverter037_MODBUS.HR1062_idcInput_A | Current-DC | 6274 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Daily Energy Delivered | Inverter | inverter037_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6275 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power Set Point | Inverter | inverter037_MODBUS.HR0553_pRef | Real Power Set Point | 6276 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Reactive Power Set Point | Inverter | inverter037_MODBUS.HR0558_qRef | Reactive Power Set Point | 6277 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Frequency | Inverter | inverter037_MODBUS.HR1012_f3_Hz | Frequency | 6278 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV037 | Daggett 3_SUB1_INV037_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Insulation Resistance | Inverter | inverter037_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6279 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Number of DU Channels | Inverter | inverter037_MODBUS.HR0653_duChannels | Number of DU Channels | 6280 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Number of Running Modules | Inverter | inverter037_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6281 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Operating State | Inverter | inverter037_MODBUS.HR1123_currentStatus | Operating State | 6282 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Power Factor | Inverter | inverter037_MODBUS.HR1011_pf3 | Power Factor | 6283 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV037 | Daggett 3_SUB1_INV037_Ramp Down | Inverter | inverter037_MODBUS.HR0286_dropGradient_p | Ramp Down | 6284 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Ramp Up | Inverter | inverter037_MODBUS.HR0282_riseGradient_p | Ramp Up | 6285 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power Delivered | Inverter | inverter037_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6286 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Reactive Power Delivered | Inverter | inverter037_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6287 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power | 6288 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Reactive Power | Inverter | inverter037_MODBUS.HR1009_q3_kvar | Reactive Power | 6289 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Reactive Power Mode | Inverter | inverter037_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6290 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Reactive Power Set Point Percent | Inverter | inverter037_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6291 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power AC Percent | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6292 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power-AC | Inverter | inverter037_MODBUS.HR1008_p3_kW | Real Power-AC | 6293 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power-DC | Inverter | inverter037_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6294 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Air Intake | Inverter | inverter037_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6295 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Cabinet | Inverter | inverter037_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6296 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-IGBT | Inverter | inverter037_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6297 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Temperature-Module | Inverter | inverter037_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6298 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage A-B | Inverter | inverter037_MODBUS.HR1007_vRS_V | Voltage A-B | 6299 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage B-C | Inverter | inverter037_MODBUS.HR1002_vST_V | Voltage B-C | 6300 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage C-A | Inverter | inverter037_MODBUS.HR1003_vTR_V | Voltage C-A | 6301 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Voltage DC | Inverter | inverter037_MODBUS.HR1051_vdcBus_V | Voltage DC | 6302 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV037 | Daggett 3_SUB1_INV037_Fault Code 1 | Inverter | Inverter037_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6303 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Warning | Inverter | Inverter037_MODBUS.HRxxxx_currentWarning | Warning | 6304 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Internal Input Status | Inverter | Inverter037_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6305 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Internal Output Status | Inverter | Inverter037_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6306 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Module Fault Code | Inverter | Inverter037_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Internal Humidity | Inverter | Inverter037_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6308 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Humidity | Inverter | Inverter037_MODBUS.HRxxxx_humidity | Humidity | 6309 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_Comms Fault Time | Inverter | Inverter037_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6310 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Status | Inverter | Inverter037_MODBUS.HRxxxx_M1_status | Module Status | 6311 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 IR | Inverter | Inverter037_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 IS | Inverter | Inverter037_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 IT | Inverter | Inverter037_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6315 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6317 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6318 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 P | Inverter | Inverter037_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6319 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Q | Inverter | Inverter037_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6320 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6321 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6322 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M1 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6325 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Status | Inverter | Inverter037_MODBUS.HRxxxx_M2_status | Module Status | 6326 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 IR | Inverter | Inverter037_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6327 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 IS | Inverter | Inverter037_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 IT | Inverter | Inverter037_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6329 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6331 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6332 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6333 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 P | Inverter | Inverter037_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6334 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Q | Inverter | Inverter037_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6335 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6336 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6337 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6338 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6339 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M2 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6340 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Status | Inverter | Inverter037_MODBUS.HRxxxx_M3_status | Module Status | 6341 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 IR | Inverter | Inverter037_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 IS | Inverter | Inverter037_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6343 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 IT | Inverter | Inverter037_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6344 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6345 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6346 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6347 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6348 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 P | Inverter | Inverter037_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6349 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Q | Inverter | Inverter037_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6350 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6351 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6352 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6353 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6354 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M3 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6355 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Status | Inverter | Inverter037_MODBUS.HRxxxx_M4_status | Module Status | 6356 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 IR | Inverter | Inverter037_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 IS | Inverter | Inverter037_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 IT | Inverter | Inverter037_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6359 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6360 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6361 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6362 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6363 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 P | Inverter | Inverter037_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6364 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Q | Inverter | Inverter037_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6365 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6366 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6367 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6368 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M4 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6370 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Status | Inverter | Inverter037_MODBUS.HRxxxx_M5_status | Module Status | 6371 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 IR | Inverter | Inverter037_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 IS | Inverter | Inverter037_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 IT | Inverter | Inverter037_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6375 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6377 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6378 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 P | Inverter | Inverter037_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6379 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Q | Inverter | Inverter037_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6380 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6381 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6382 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6384 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M5 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6385 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Status | Inverter | Inverter037_MODBUS.HRxxxx_M6_status | Module Status | 6386 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 IR | Inverter | Inverter037_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 IS | Inverter | Inverter037_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 IT | Inverter | Inverter037_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 IDC | Inverter | Inverter037_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6390 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 VDCP | Inverter | Inverter037_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6391 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 VDCN | Inverter | Inverter037_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6392 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 VDC | Inverter | Inverter037_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6393 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 P | Inverter | Inverter037_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6394 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Q | Inverter | Inverter037_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6395 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Ambient Temp | Inverter | Inverter037_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6396 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Max IGBT Temp | Inverter | Inverter037_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6397 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 IO Status | Inverter | Inverter037_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6398 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Hardware Version | Inverter | Inverter037_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6399 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV037 | Daggett 3_SUB1_INV037_M6 Software Version | Inverter | Inverter037_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_A Phase Current | Inverter | inverter038_MODBUS.HR1004_i1_A | A Phase Current | 6401 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_B Phase Current | Inverter | inverter038_MODBUS.HR1005_i2_A | B Phase Current | 6402 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_C Phase Current | Inverter | inverter038_MODBUS.HR1006_i3_A | C Phase Current | 6403 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Bus Voltage | Inverter | inverter038_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6404 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV038 | Daggett 3_SUB1_INV038_Apparent Power | Inverter | inverter038_MODBUS.HR1010_s3_VA | Apparent Power | 6405 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 1 | Inverter | Inverter038_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6406 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC Input 1 | Inverter | Inverter038_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6407 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 2 | Inverter | Inverter038_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6408 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 2 | Inverter | Inverter038_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6409 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 3 | Inverter | Inverter038_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 3 | Inverter | Inverter038_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6411 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 4 | Inverter | Inverter038_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 4 | Inverter | Inverter038_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6413 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 5 | Inverter | Inverter038_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6414 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 5 | Inverter | Inverter038_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6415 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 6 | Inverter | Inverter038_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6416 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 6 | Inverter | Inverter038_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6417 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 7 | Inverter | Inverter038_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6418 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 7 | Inverter | Inverter038_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6419 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 8 | Inverter | Inverter038_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6420 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 8 | Inverter | Inverter038_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6421 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 9 | Inverter | Inverter038_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6422 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 9 | Inverter | Inverter038_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6423 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 10 | Inverter | Inverter038_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6424 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 10 | Inverter | Inverter038_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6425 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 11 | Inverter | Inverter038_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 11 | Inverter | Inverter038_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6427 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 12 | Inverter | Inverter038_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6428 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 12 | Inverter | Inverter038_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6429 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 13 | Inverter | Inverter038_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6430 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 13 | Inverter | Inverter038_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6431 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 14 | Inverter | Inverter038_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 14 | Inverter | Inverter038_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6433 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 15 | Inverter | Inverter038_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6434 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 15 | Inverter | Inverter038_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6435 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 16 | Inverter | Inverter038_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6436 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 16 | Inverter | Inverter038_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6437 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 17 | Inverter | Inverter038_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6438 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 17 | Inverter | Inverter038_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6439 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 18 | Inverter | Inverter038_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6440 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 18 | Inverter | Inverter038_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6441 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 19 | Inverter | Inverter038_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6442 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 19 | Inverter | Inverter038_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6443 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current DC Input 20 | Inverter | Inverter038_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6444 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC input 20 | Inverter | Inverter038_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6445 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current-AC | Inverter | inverter038_MODBUS.HR1007_i3Avg_A | Current-AC | 6446 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Current-DC | Inverter | inverter038_MODBUS.HR1062_idcInput_A | Current-DC | 6447 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Daily Energy Delivered | Inverter | inverter038_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6448 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power Set Point | Inverter | inverter038_MODBUS.HR0553_pRef | Real Power Set Point | 6449 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Reactive Power Set Point | Inverter | inverter038_MODBUS.HR0558_qRef | Reactive Power Set Point | 6450 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Frequency | Inverter | inverter038_MODBUS.HR1012_f3_Hz | Frequency | 6451 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV038 | Daggett 3_SUB1_INV038_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Insulation Resistance | Inverter | inverter038_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6452 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Number of DU Channels | Inverter | inverter038_MODBUS.HR0653_duChannels | Number of DU Channels | 6453 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Number of Running Modules | Inverter | inverter038_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6454 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Operating State | Inverter | inverter038_MODBUS.HR1123_currentStatus | Operating State | 6455 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Power Factor | Inverter | inverter038_MODBUS.HR1011_pf3 | Power Factor | 6456 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV038 | Daggett 3_SUB1_INV038_Ramp Down | Inverter | inverter038_MODBUS.HR0286_dropGradient_p | Ramp Down | 6457 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Ramp Up | Inverter | inverter038_MODBUS.HR0282_riseGradient_p | Ramp Up | 6458 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power Delivered | Inverter | inverter038_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6459 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Reactive Power Delivered | Inverter | inverter038_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6460 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power | 6461 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Reactive Power | Inverter | inverter038_MODBUS.HR1009_q3_kvar | Reactive Power | 6462 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Reactive Power Mode | Inverter | inverter038_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6463 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Reactive Power Set Point Percent | Inverter | inverter038_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6464 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power AC Percent | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6465 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power-AC | Inverter | inverter038_MODBUS.HR1008_p3_kW | Real Power-AC | 6466 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power-DC | Inverter | inverter038_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6467 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Air Intake | Inverter | inverter038_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6468 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Cabinet | Inverter | inverter038_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6469 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-IGBT | Inverter | inverter038_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6470 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Temperature-Module | Inverter | inverter038_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6471 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage A-B | Inverter | inverter038_MODBUS.HR1008_vRS_V | Voltage A-B | 6472 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage B-C | Inverter | inverter038_MODBUS.HR1002_vST_V | Voltage B-C | 6473 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage C-A | Inverter | inverter038_MODBUS.HR1003_vTR_V | Voltage C-A | 6474 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Voltage DC | Inverter | inverter038_MODBUS.HR1051_vdcBus_V | Voltage DC | 6475 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV038 | Daggett 3_SUB1_INV038_Fault Code 1 | Inverter | Inverter038_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6476 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Warning | Inverter | Inverter038_MODBUS.HRxxxx_currentWarning | Warning | 6477 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Internal Input Status | Inverter | Inverter038_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6478 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Internal Output Status | Inverter | Inverter038_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6479 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Module Fault Code | Inverter | Inverter038_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Internal Humidity | Inverter | Inverter038_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6481 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Humidity | Inverter | Inverter038_MODBUS.HRxxxx_humidity | Humidity | 6482 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_Comms Fault Time | Inverter | Inverter038_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6483 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Status | Inverter | Inverter038_MODBUS.HRxxxx_M1_status | Module Status | 6484 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 IR | Inverter | Inverter038_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 IS | Inverter | Inverter038_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 IT | Inverter | Inverter038_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6488 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6490 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6491 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 P | Inverter | Inverter038_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6492 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Q | Inverter | Inverter038_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6493 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6494 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6495 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M1 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6498 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Status | Inverter | Inverter038_MODBUS.HRxxxx_M2_status | Module Status | 6499 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 IR | Inverter | Inverter038_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6500 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 IS | Inverter | Inverter038_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 IT | Inverter | Inverter038_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6502 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6504 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6505 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6506 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 P | Inverter | Inverter038_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6507 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Q | Inverter | Inverter038_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6508 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6509 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6510 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6511 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6512 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M2 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6513 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Status | Inverter | Inverter038_MODBUS.HRxxxx_M3_status | Module Status | 6514 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 IR | Inverter | Inverter038_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 IS | Inverter | Inverter038_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6516 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 IT | Inverter | Inverter038_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6517 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6518 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6519 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6520 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6521 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 P | Inverter | Inverter038_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6522 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Q | Inverter | Inverter038_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6523 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6524 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6525 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6526 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6527 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M3 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6528 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Status | Inverter | Inverter038_MODBUS.HRxxxx_M4_status | Module Status | 6529 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 IR | Inverter | Inverter038_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 IS | Inverter | Inverter038_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 IT | Inverter | Inverter038_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6532 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6533 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6534 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6535 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6536 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 P | Inverter | Inverter038_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6537 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Q | Inverter | Inverter038_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6538 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6539 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6540 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6541 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M4 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6543 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Status | Inverter | Inverter038_MODBUS.HRxxxx_M5_status | Module Status | 6544 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 IR | Inverter | Inverter038_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 IS | Inverter | Inverter038_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 IT | Inverter | Inverter038_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6548 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6550 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6551 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 P | Inverter | Inverter038_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6552 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Q | Inverter | Inverter038_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6553 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6554 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6555 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6557 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M5 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6558 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Status | Inverter | Inverter038_MODBUS.HRxxxx_M6_status | Module Status | 6559 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 IR | Inverter | Inverter038_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 IS | Inverter | Inverter038_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 IT | Inverter | Inverter038_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 IDC | Inverter | Inverter038_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6563 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 VDCP | Inverter | Inverter038_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6564 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 VDCN | Inverter | Inverter038_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6565 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 VDC | Inverter | Inverter038_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6566 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 P | Inverter | Inverter038_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6567 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Q | Inverter | Inverter038_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6568 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Ambient Temp | Inverter | Inverter038_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6569 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Max IGBT Temp | Inverter | Inverter038_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6570 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 IO Status | Inverter | Inverter038_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6571 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Hardware Version | Inverter | Inverter038_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6572 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV038 | Daggett 3_SUB1_INV038_M6 Software Version | Inverter | Inverter038_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_A Phase Current | Inverter | inverter039_MODBUS.HR1004_i1_A | A Phase Current | 6574 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_B Phase Current | Inverter | inverter039_MODBUS.HR1005_i2_A | B Phase Current | 6575 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_C Phase Current | Inverter | inverter039_MODBUS.HR1006_i3_A | C Phase Current | 6576 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Bus Voltage | Inverter | inverter039_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6577 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV039 | Daggett 3_SUB1_INV039_Apparent Power | Inverter | inverter039_MODBUS.HR1010_s3_VA | Apparent Power | 6578 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 1 | Inverter | Inverter039_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6579 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC Input 1 | Inverter | Inverter039_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6580 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 2 | Inverter | Inverter039_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6581 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 2 | Inverter | Inverter039_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6582 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 3 | Inverter | Inverter039_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 3 | Inverter | Inverter039_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6584 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 4 | Inverter | Inverter039_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 4 | Inverter | Inverter039_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6586 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 5 | Inverter | Inverter039_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6587 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 5 | Inverter | Inverter039_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6588 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 6 | Inverter | Inverter039_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6589 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 6 | Inverter | Inverter039_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6590 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 7 | Inverter | Inverter039_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6591 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 7 | Inverter | Inverter039_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6592 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 8 | Inverter | Inverter039_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6593 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 8 | Inverter | Inverter039_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6594 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 9 | Inverter | Inverter039_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6595 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 9 | Inverter | Inverter039_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6596 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 10 | Inverter | Inverter039_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6597 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 10 | Inverter | Inverter039_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6598 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 11 | Inverter | Inverter039_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 11 | Inverter | Inverter039_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6600 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 12 | Inverter | Inverter039_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6601 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 12 | Inverter | Inverter039_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6602 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 13 | Inverter | Inverter039_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6603 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 13 | Inverter | Inverter039_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6604 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 14 | Inverter | Inverter039_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 14 | Inverter | Inverter039_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6606 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 15 | Inverter | Inverter039_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6607 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 15 | Inverter | Inverter039_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6608 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 16 | Inverter | Inverter039_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6609 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 16 | Inverter | Inverter039_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6610 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 17 | Inverter | Inverter039_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6611 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 17 | Inverter | Inverter039_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6612 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 18 | Inverter | Inverter039_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6613 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 18 | Inverter | Inverter039_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6614 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 19 | Inverter | Inverter039_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6615 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 19 | Inverter | Inverter039_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6616 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current DC Input 20 | Inverter | Inverter039_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6617 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC input 20 | Inverter | Inverter039_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6618 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current-AC | Inverter | inverter039_MODBUS.HR1007_i3Avg_A | Current-AC | 6619 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Current-DC | Inverter | inverter039_MODBUS.HR1062_idcInput_A | Current-DC | 6620 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Daily Energy Delivered | Inverter | inverter039_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6621 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power Set Point | Inverter | inverter039_MODBUS.HR0553_pRef | Real Power Set Point | 6622 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Reactive Power Set Point | Inverter | inverter039_MODBUS.HR0558_qRef | Reactive Power Set Point | 6623 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Frequency | Inverter | inverter039_MODBUS.HR1012_f3_Hz | Frequency | 6624 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV039 | Daggett 3_SUB1_INV039_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Insulation Resistance | Inverter | inverter039_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6625 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Number of DU Channels | Inverter | inverter039_MODBUS.HR0653_duChannels | Number of DU Channels | 6626 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Number of Running Modules | Inverter | inverter039_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6627 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Operating State | Inverter | inverter039_MODBUS.HR1123_currentStatus | Operating State | 6628 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Power Factor | Inverter | inverter039_MODBUS.HR1011_pf3 | Power Factor | 6629 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV039 | Daggett 3_SUB1_INV039_Ramp Down | Inverter | inverter039_MODBUS.HR0286_dropGradient_p | Ramp Down | 6630 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Ramp Up | Inverter | inverter039_MODBUS.HR0282_riseGradient_p | Ramp Up | 6631 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power Delivered | Inverter | inverter039_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6632 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Reactive Power Delivered | Inverter | inverter039_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6633 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power | 6634 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Reactive Power | Inverter | inverter039_MODBUS.HR1009_q3_kvar | Reactive Power | 6635 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Reactive Power Mode | Inverter | inverter039_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6636 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Reactive Power Set Point Percent | Inverter | inverter039_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6637 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power AC Percent | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6638 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power-AC | Inverter | inverter039_MODBUS.HR1008_p3_kW | Real Power-AC | 6639 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power-DC | Inverter | inverter039_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6640 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Air Intake | Inverter | inverter039_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6641 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Cabinet | Inverter | inverter039_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6642 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-IGBT | Inverter | inverter039_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6643 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Temperature-Module | Inverter | inverter039_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6644 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage A-B | Inverter | inverter039_MODBUS.HR1009_vRS_V | Voltage A-B | 6645 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage B-C | Inverter | inverter039_MODBUS.HR1002_vST_V | Voltage B-C | 6646 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage C-A | Inverter | inverter039_MODBUS.HR1003_vTR_V | Voltage C-A | 6647 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Voltage DC | Inverter | inverter039_MODBUS.HR1051_vdcBus_V | Voltage DC | 6648 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV039 | Daggett 3_SUB1_INV039_Fault Code 1 | Inverter | Inverter039_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6649 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Warning | Inverter | Inverter039_MODBUS.HRxxxx_currentWarning | Warning | 6650 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Internal Input Status | Inverter | Inverter039_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6651 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Internal Output Status | Inverter | Inverter039_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6652 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Module Fault Code | Inverter | Inverter039_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Internal Humidity | Inverter | Inverter039_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6654 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Humidity | Inverter | Inverter039_MODBUS.HRxxxx_humidity | Humidity | 6655 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_Comms Fault Time | Inverter | Inverter039_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6656 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Status | Inverter | Inverter039_MODBUS.HRxxxx_M1_status | Module Status | 6657 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 IR | Inverter | Inverter039_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 IS | Inverter | Inverter039_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 IT | Inverter | Inverter039_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6661 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6663 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6664 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 P | Inverter | Inverter039_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6665 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Q | Inverter | Inverter039_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6666 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6667 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6668 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M1 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6671 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Status | Inverter | Inverter039_MODBUS.HRxxxx_M2_status | Module Status | 6672 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 IR | Inverter | Inverter039_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6673 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 IS | Inverter | Inverter039_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 IT | Inverter | Inverter039_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6675 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6677 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6678 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6679 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 P | Inverter | Inverter039_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6680 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Q | Inverter | Inverter039_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6681 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6682 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6683 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6684 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6685 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M2 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6686 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Status | Inverter | Inverter039_MODBUS.HRxxxx_M3_status | Module Status | 6687 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 IR | Inverter | Inverter039_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 IS | Inverter | Inverter039_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6689 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 IT | Inverter | Inverter039_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6690 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6691 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6692 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6693 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6694 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 P | Inverter | Inverter039_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6695 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Q | Inverter | Inverter039_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6696 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6697 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6698 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6699 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6700 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M3 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6701 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Status | Inverter | Inverter039_MODBUS.HRxxxx_M4_status | Module Status | 6702 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 IR | Inverter | Inverter039_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 IS | Inverter | Inverter039_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 IT | Inverter | Inverter039_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6705 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6706 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6707 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6708 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6709 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 P | Inverter | Inverter039_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6710 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Q | Inverter | Inverter039_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6711 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6712 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6713 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6714 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M4 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6716 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Status | Inverter | Inverter039_MODBUS.HRxxxx_M5_status | Module Status | 6717 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 IR | Inverter | Inverter039_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 IS | Inverter | Inverter039_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 IT | Inverter | Inverter039_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6721 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6723 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6724 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 P | Inverter | Inverter039_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6725 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Q | Inverter | Inverter039_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6726 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6727 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6728 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6730 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M5 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6731 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Status | Inverter | Inverter039_MODBUS.HRxxxx_M6_status | Module Status | 6732 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 IR | Inverter | Inverter039_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 IS | Inverter | Inverter039_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 IT | Inverter | Inverter039_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 IDC | Inverter | Inverter039_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6736 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 VDCP | Inverter | Inverter039_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6737 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 VDCN | Inverter | Inverter039_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6738 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 VDC | Inverter | Inverter039_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6739 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 P | Inverter | Inverter039_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6740 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Q | Inverter | Inverter039_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6741 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Ambient Temp | Inverter | Inverter039_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6742 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Max IGBT Temp | Inverter | Inverter039_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6743 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 IO Status | Inverter | Inverter039_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6744 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Hardware Version | Inverter | Inverter039_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6745 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV039 | Daggett 3_SUB1_INV039_M6 Software Version | Inverter | Inverter039_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_A Phase Current | Inverter | inverter040_MODBUS.HR1004_i1_A | A Phase Current | 6747 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_B Phase Current | Inverter | inverter040_MODBUS.HR1005_i2_A | B Phase Current | 6748 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_C Phase Current | Inverter | inverter040_MODBUS.HR1006_i3_A | C Phase Current | 6749 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Bus Voltage | Inverter | inverter040_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6750 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV040 | Daggett 3_SUB1_INV040_Apparent Power | Inverter | inverter040_MODBUS.HR1010_s3_VA | Apparent Power | 6751 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 1 | Inverter | Inverter040_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6752 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC Input 1 | Inverter | Inverter040_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6753 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 2 | Inverter | Inverter040_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6754 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 2 | Inverter | Inverter040_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6755 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 3 | Inverter | Inverter040_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 3 | Inverter | Inverter040_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6757 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 4 | Inverter | Inverter040_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 4 | Inverter | Inverter040_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6759 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 5 | Inverter | Inverter040_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6760 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 5 | Inverter | Inverter040_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6761 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 6 | Inverter | Inverter040_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6762 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 6 | Inverter | Inverter040_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6763 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 7 | Inverter | Inverter040_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6764 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 7 | Inverter | Inverter040_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6765 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 8 | Inverter | Inverter040_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6766 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 8 | Inverter | Inverter040_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6767 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 9 | Inverter | Inverter040_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6768 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 9 | Inverter | Inverter040_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6769 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 10 | Inverter | Inverter040_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6770 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 10 | Inverter | Inverter040_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6771 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 11 | Inverter | Inverter040_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 11 | Inverter | Inverter040_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6773 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 12 | Inverter | Inverter040_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6774 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 12 | Inverter | Inverter040_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6775 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 13 | Inverter | Inverter040_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6776 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 13 | Inverter | Inverter040_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6777 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 14 | Inverter | Inverter040_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 14 | Inverter | Inverter040_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6779 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 15 | Inverter | Inverter040_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6780 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 15 | Inverter | Inverter040_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6781 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 16 | Inverter | Inverter040_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6782 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 16 | Inverter | Inverter040_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6783 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 17 | Inverter | Inverter040_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6784 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 17 | Inverter | Inverter040_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6785 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 18 | Inverter | Inverter040_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6786 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 18 | Inverter | Inverter040_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6787 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 19 | Inverter | Inverter040_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6788 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 19 | Inverter | Inverter040_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6789 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current DC Input 20 | Inverter | Inverter040_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6790 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC input 20 | Inverter | Inverter040_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6791 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current-AC | Inverter | inverter040_MODBUS.HR1007_i3Avg_A | Current-AC | 6792 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Current-DC | Inverter | inverter040_MODBUS.HR1062_idcInput_A | Current-DC | 6793 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Daily Energy Delivered | Inverter | inverter040_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6794 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power Set Point | Inverter | inverter040_MODBUS.HR0553_pRef | Real Power Set Point | 6795 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Reactive Power Set Point | Inverter | inverter040_MODBUS.HR0558_qRef | Reactive Power Set Point | 6796 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Frequency | Inverter | inverter040_MODBUS.HR1012_f3_Hz | Frequency | 6797 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV040 | Daggett 3_SUB1_INV040_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Insulation Resistance | Inverter | inverter040_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6798 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Number of DU Channels | Inverter | inverter040_MODBUS.HR0653_duChannels | Number of DU Channels | 6799 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Number of Running Modules | Inverter | inverter040_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6800 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Operating State | Inverter | inverter040_MODBUS.HR1123_currentStatus | Operating State | 6801 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Power Factor | Inverter | inverter040_MODBUS.HR1011_pf3 | Power Factor | 6802 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV040 | Daggett 3_SUB1_INV040_Ramp Down | Inverter | inverter040_MODBUS.HR0286_dropGradient_p | Ramp Down | 6803 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Ramp Up | Inverter | inverter040_MODBUS.HR0282_riseGradient_p | Ramp Up | 6804 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power Delivered | Inverter | inverter040_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6805 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Reactive Power Delivered | Inverter | inverter040_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6806 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power | 6807 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Reactive Power | Inverter | inverter040_MODBUS.HR1009_q3_kvar | Reactive Power | 6808 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Reactive Power Mode | Inverter | inverter040_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6809 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Reactive Power Set Point Percent | Inverter | inverter040_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6810 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power AC Percent | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6811 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power-AC | Inverter | inverter040_MODBUS.HR1008_p3_kW | Real Power-AC | 6812 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power-DC | Inverter | inverter040_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6813 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Air Intake | Inverter | inverter040_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6814 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Cabinet | Inverter | inverter040_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6815 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-IGBT | Inverter | inverter040_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6816 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Temperature-Module | Inverter | inverter040_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6817 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage A-B | Inverter | inverter040_MODBUS.HR1010_vRS_V | Voltage A-B | 6818 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage B-C | Inverter | inverter040_MODBUS.HR1002_vST_V | Voltage B-C | 6819 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage C-A | Inverter | inverter040_MODBUS.HR1003_vTR_V | Voltage C-A | 6820 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Voltage DC | Inverter | inverter040_MODBUS.HR1051_vdcBus_V | Voltage DC | 6821 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV040 | Daggett 3_SUB1_INV040_Fault Code 1 | Inverter | Inverter040_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6822 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Warning | Inverter | Inverter040_MODBUS.HRxxxx_currentWarning | Warning | 6823 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Internal Input Status | Inverter | Inverter040_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6824 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Internal Output Status | Inverter | Inverter040_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6825 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Module Fault Code | Inverter | Inverter040_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Internal Humidity | Inverter | Inverter040_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 6827 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Humidity | Inverter | Inverter040_MODBUS.HRxxxx_humidity | Humidity | 6828 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_Comms Fault Time | Inverter | Inverter040_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 6829 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Status | Inverter | Inverter040_MODBUS.HRxxxx_M1_status | Module Status | 6830 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 IR | Inverter | Inverter040_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 6831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 IS | Inverter | Inverter040_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 6832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 IT | Inverter | Inverter040_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 6833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 6834 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 6835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 6836 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 6837 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 P | Inverter | Inverter040_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 6838 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Q | Inverter | Inverter040_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 6839 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 6840 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 6841 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 6842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 6843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M1 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 6844 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Status | Inverter | Inverter040_MODBUS.HRxxxx_M2_status | Module Status | 6845 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 IR | Inverter | Inverter040_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 6846 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 IS | Inverter | Inverter040_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 6847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 IT | Inverter | Inverter040_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 6848 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 6849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 6850 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 6851 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 6852 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 P | Inverter | Inverter040_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 6853 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Q | Inverter | Inverter040_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 6854 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 6855 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 6856 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 6857 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 6858 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M2 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 6859 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Status | Inverter | Inverter040_MODBUS.HRxxxx_M3_status | Module Status | 6860 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 IR | Inverter | Inverter040_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 6861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 IS | Inverter | Inverter040_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 6862 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 IT | Inverter | Inverter040_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 6863 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 6864 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 6865 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 6866 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 6867 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 P | Inverter | Inverter040_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 6868 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Q | Inverter | Inverter040_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 6869 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 6870 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 6871 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 6872 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 6873 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M3 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 6874 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Status | Inverter | Inverter040_MODBUS.HRxxxx_M4_status | Module Status | 6875 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 IR | Inverter | Inverter040_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 6876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 IS | Inverter | Inverter040_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 6877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 IT | Inverter | Inverter040_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 6878 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 6879 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 6880 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 6881 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 6882 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 P | Inverter | Inverter040_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 6883 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Q | Inverter | Inverter040_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 6884 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 6885 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 6886 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 6887 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 6888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M4 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 6889 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Status | Inverter | Inverter040_MODBUS.HRxxxx_M5_status | Module Status | 6890 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 IR | Inverter | Inverter040_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 6891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 IS | Inverter | Inverter040_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 6892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 IT | Inverter | Inverter040_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 6893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 6894 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 6895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 6896 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 6897 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 P | Inverter | Inverter040_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 6898 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Q | Inverter | Inverter040_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 6899 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 6900 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 6901 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 6902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 6903 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M5 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 6904 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Status | Inverter | Inverter040_MODBUS.HRxxxx_M6_status | Module Status | 6905 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 IR | Inverter | Inverter040_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 6906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 IS | Inverter | Inverter040_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 6907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 IT | Inverter | Inverter040_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 6908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 IDC | Inverter | Inverter040_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 6909 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 VDCP | Inverter | Inverter040_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 6910 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 VDCN | Inverter | Inverter040_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 6911 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 VDC | Inverter | Inverter040_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 6912 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 P | Inverter | Inverter040_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 6913 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Q | Inverter | Inverter040_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 6914 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Ambient Temp | Inverter | Inverter040_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 6915 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Max IGBT Temp | Inverter | Inverter040_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 6916 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 IO Status | Inverter | Inverter040_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 6917 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Hardware Version | Inverter | Inverter040_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 6918 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV040 | Daggett 3_SUB1_INV040_M6 Software Version | Inverter | Inverter040_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 6919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_A Phase Current | Inverter | inverter041_MODBUS.HR1004_i1_A | A Phase Current | 6920 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_B Phase Current | Inverter | inverter041_MODBUS.HR1005_i2_A | B Phase Current | 6921 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_C Phase Current | Inverter | inverter041_MODBUS.HR1006_i3_A | C Phase Current | 6922 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Bus Voltage | Inverter | inverter041_MODBUS.HR1051_vdcBus_V | Bus Voltage | 6923 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV041 | Daggett 3_SUB1_INV041_Apparent Power | Inverter | inverter041_MODBUS.HR1010_s3_VA | Apparent Power | 6924 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 1 | Inverter | Inverter041_MODBUS.HR5805_du1_idc_A | Current DC Input# | 6925 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC Input 1 | Inverter | Inverter041_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6926 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 2 | Inverter | Inverter041_MODBUS.HR5811_du2_idc_A | Current DC Input# | 6927 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 2 | Inverter | Inverter041_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 6928 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 3 | Inverter | Inverter041_MODBUS.HR5817_du3_idc_A | Current DC Input# | 6929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 3 | Inverter | Inverter041_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 6930 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 4 | Inverter | Inverter041_MODBUS.HR5823_du4_idc_A | Current DC Input# | 6931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 4 | Inverter | Inverter041_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 6932 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 5 | Inverter | Inverter041_MODBUS.HR5829_du5_idc_A | Current DC Input# | 6933 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 5 | Inverter | Inverter041_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 6934 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 6 | Inverter | Inverter041_MODBUS.HR5835_du6_idc_A | Current DC Input# | 6935 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 6 | Inverter | Inverter041_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 6936 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 7 | Inverter | Inverter041_MODBUS.HR5841_du7_idc_A | Current DC Input# | 6937 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 7 | Inverter | Inverter041_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 6938 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 8 | Inverter | Inverter041_MODBUS.HR5847_du8_idc_A | Current DC Input# | 6939 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 8 | Inverter | Inverter041_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 6940 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 9 | Inverter | Inverter041_MODBUS.HR5853_du9_idc_A | Current DC Input# | 6941 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 9 | Inverter | Inverter041_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 6942 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 10 | Inverter | Inverter041_MODBUS.HR5859_du10_idc_A | Current DC Input# | 6943 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 10 | Inverter | Inverter041_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 6944 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 11 | Inverter | Inverter041_MODBUS.HR5865_du11_idc_A | Current DC Input# | 6945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 11 | Inverter | Inverter041_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 6946 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 12 | Inverter | Inverter041_MODBUS.HR5871_du12_idc_A | Current DC Input# | 6947 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 12 | Inverter | Inverter041_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 6948 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 13 | Inverter | Inverter041_MODBUS.HR5877_du13_idc_A | Current DC Input# | 6949 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 13 | Inverter | Inverter041_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 6950 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 14 | Inverter | Inverter041_MODBUS.HR5883_du14_idc_A | Current DC Input# | 6951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 14 | Inverter | Inverter041_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 6952 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 15 | Inverter | Inverter041_MODBUS.HR5889_du15_idc_A | Current DC Input# | 6953 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 15 | Inverter | Inverter041_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 6954 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 16 | Inverter | Inverter041_MODBUS.HR5895_du16_idc_A | Current DC Input# | 6955 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 16 | Inverter | Inverter041_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 6956 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 17 | Inverter | Inverter041_MODBUS.HR5901_du17_idc_A | Current DC Input# | 6957 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 17 | Inverter | Inverter041_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 6958 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 18 | Inverter | Inverter041_MODBUS.HR5907_du18_idc_A | Current DC Input# | 6959 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 18 | Inverter | Inverter041_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 6960 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 19 | Inverter | Inverter041_MODBUS.HR5913_du19_idc_A | Current DC Input# | 6961 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 19 | Inverter | Inverter041_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 6962 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current DC Input 20 | Inverter | Inverter041_MODBUS.HR5919_du20_idc_A | Current DC Input# | 6963 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC input 20 | Inverter | Inverter041_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 6964 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current-AC | Inverter | inverter041_MODBUS.HR1007_i3Avg_A | Current-AC | 6965 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Current-DC | Inverter | inverter041_MODBUS.HR1062_idcInput_A | Current-DC | 6966 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Daily Energy Delivered | Inverter | inverter041_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 6967 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power Set Point | Inverter | inverter041_MODBUS.HR0553_pRef | Real Power Set Point | 6968 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Reactive Power Set Point | Inverter | inverter041_MODBUS.HR0558_qRef | Reactive Power Set Point | 6969 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Frequency | Inverter | inverter041_MODBUS.HR1012_f3_Hz | Frequency | 6970 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV041 | Daggett 3_SUB1_INV041_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Insulation Resistance | Inverter | inverter041_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 6971 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Number of DU Channels | Inverter | inverter041_MODBUS.HR0653_duChannels | Number of DU Channels | 6972 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Number of Running Modules | Inverter | inverter041_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 6973 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Operating State | Inverter | inverter041_MODBUS.HR1123_currentStatus | Operating State | 6974 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Power Factor | Inverter | inverter041_MODBUS.HR1011_pf3 | Power Factor | 6975 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV041 | Daggett 3_SUB1_INV041_Ramp Down | Inverter | inverter041_MODBUS.HR0286_dropGradient_p | Ramp Down | 6976 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Ramp Up | Inverter | inverter041_MODBUS.HR0282_riseGradient_p | Ramp Up | 6977 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power Delivered | Inverter | inverter041_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 6978 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Reactive Power Delivered | Inverter | inverter041_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 6979 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power | 6980 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Reactive Power | Inverter | inverter041_MODBUS.HR1009_q3_kvar | Reactive Power | 6981 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Reactive Power Mode | Inverter | inverter041_MODBUS.HR0552_qControlMode | Reactive Power Mode | 6982 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Reactive Power Set Point Percent | Inverter | inverter041_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 6983 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power AC Percent | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power AC Percent | 6984 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power-AC | Inverter | inverter041_MODBUS.HR1008_p3_kW | Real Power-AC | 6985 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power-DC | Inverter | inverter041_MODBUS.HR1061_pdcInput_W | Real Power-DC | 6986 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Air Intake | Inverter | inverter041_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 6987 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Cabinet | Inverter | inverter041_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 6988 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-IGBT | Inverter | inverter041_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 6989 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Temperature-Module | Inverter | inverter041_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 6990 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage A-B | Inverter | inverter041_MODBUS.HR1001_vRS_V | Voltage A-B | 6991 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage B-C | Inverter | inverter041_MODBUS.HR1002_vST_V | Voltage B-C | 6992 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage C-A | Inverter | inverter041_MODBUS.HR1003_vTR_V | Voltage C-A | 6993 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Voltage DC | Inverter | inverter041_MODBUS.HR1051_vdcBus_V | Voltage DC | 6994 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV041 | Daggett 3_SUB1_INV041_Fault Code 1 | Inverter | Inverter041_MODBUS.HRxxxx_currentFault | Fault Code 1 | 6995 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Warning | Inverter | Inverter041_MODBUS.HRxxxx_currentWarning | Warning | 6996 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Internal Input Status | Inverter | Inverter041_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 6997 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Internal Output Status | Inverter | Inverter041_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 6998 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Module Fault Code | Inverter | Inverter041_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 6999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Internal Humidity | Inverter | Inverter041_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7000 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Humidity | Inverter | Inverter041_MODBUS.HRxxxx_humidity | Humidity | 7001 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_Comms Fault Time | Inverter | Inverter041_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7002 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Status | Inverter | Inverter041_MODBUS.HRxxxx_M1_status | Module Status | 7003 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 IR | Inverter | Inverter041_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 IS | Inverter | Inverter041_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 IT | Inverter | Inverter041_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7007 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7009 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7010 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 P | Inverter | Inverter041_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7011 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Q | Inverter | Inverter041_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7012 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7013 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7014 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M1 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7017 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Status | Inverter | Inverter041_MODBUS.HRxxxx_M2_status | Module Status | 7018 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 IR | Inverter | Inverter041_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7019 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 IS | Inverter | Inverter041_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 IT | Inverter | Inverter041_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7021 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7023 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7024 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7025 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 P | Inverter | Inverter041_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7026 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Q | Inverter | Inverter041_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7027 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7028 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7029 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7030 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7031 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M2 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7032 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Status | Inverter | Inverter041_MODBUS.HRxxxx_M3_status | Module Status | 7033 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 IR | Inverter | Inverter041_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 IS | Inverter | Inverter041_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7035 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 IT | Inverter | Inverter041_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7036 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7037 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7038 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7039 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7040 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 P | Inverter | Inverter041_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7041 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Q | Inverter | Inverter041_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7042 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7043 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7044 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7045 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7046 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M3 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7047 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Status | Inverter | Inverter041_MODBUS.HRxxxx_M4_status | Module Status | 7048 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 IR | Inverter | Inverter041_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 IS | Inverter | Inverter041_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 IT | Inverter | Inverter041_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7051 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7052 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7053 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7054 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7055 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 P | Inverter | Inverter041_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7056 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Q | Inverter | Inverter041_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7057 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7058 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7059 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7060 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M4 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7062 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Status | Inverter | Inverter041_MODBUS.HRxxxx_M5_status | Module Status | 7063 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 IR | Inverter | Inverter041_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 IS | Inverter | Inverter041_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 IT | Inverter | Inverter041_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7067 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7069 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7070 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 P | Inverter | Inverter041_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7071 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Q | Inverter | Inverter041_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7072 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7073 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7074 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7076 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M5 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7077 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Status | Inverter | Inverter041_MODBUS.HRxxxx_M6_status | Module Status | 7078 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 IR | Inverter | Inverter041_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 IS | Inverter | Inverter041_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 IT | Inverter | Inverter041_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 IDC | Inverter | Inverter041_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7082 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 VDCP | Inverter | Inverter041_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7083 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 VDCN | Inverter | Inverter041_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7084 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 VDC | Inverter | Inverter041_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7085 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 P | Inverter | Inverter041_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7086 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Q | Inverter | Inverter041_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7087 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Ambient Temp | Inverter | Inverter041_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7088 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Max IGBT Temp | Inverter | Inverter041_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7089 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 IO Status | Inverter | Inverter041_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7090 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Hardware Version | Inverter | Inverter041_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7091 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV041 | Daggett 3_SUB1_INV041_M6 Software Version | Inverter | Inverter041_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_A Phase Current | Inverter | inverter042_MODBUS.HR1004_i1_A | A Phase Current | 7093 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_B Phase Current | Inverter | inverter042_MODBUS.HR1005_i2_A | B Phase Current | 7094 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_C Phase Current | Inverter | inverter042_MODBUS.HR1006_i3_A | C Phase Current | 7095 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Bus Voltage | Inverter | inverter042_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7096 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV042 | Daggett 3_SUB1_INV042_Apparent Power | Inverter | inverter042_MODBUS.HR1010_s3_VA | Apparent Power | 7097 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 1 | Inverter | Inverter042_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7098 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC Input 1 | Inverter | Inverter042_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7099 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 2 | Inverter | Inverter042_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 2 | Inverter | Inverter042_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7101 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 3 | Inverter | Inverter042_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 3 | Inverter | Inverter042_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7103 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 4 | Inverter | Inverter042_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 4 | Inverter | Inverter042_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7105 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 5 | Inverter | Inverter042_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7106 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 5 | Inverter | Inverter042_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7107 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 6 | Inverter | Inverter042_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7108 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 6 | Inverter | Inverter042_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7109 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 7 | Inverter | Inverter042_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7110 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 7 | Inverter | Inverter042_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7111 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 8 | Inverter | Inverter042_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7112 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 8 | Inverter | Inverter042_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7113 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 9 | Inverter | Inverter042_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7114 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 9 | Inverter | Inverter042_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7115 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 10 | Inverter | Inverter042_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 10 | Inverter | Inverter042_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7117 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 11 | Inverter | Inverter042_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 11 | Inverter | Inverter042_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7119 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 12 | Inverter | Inverter042_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7120 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 12 | Inverter | Inverter042_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7121 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 13 | Inverter | Inverter042_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7122 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 13 | Inverter | Inverter042_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7123 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 14 | Inverter | Inverter042_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 14 | Inverter | Inverter042_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7125 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 15 | Inverter | Inverter042_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7126 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 15 | Inverter | Inverter042_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7127 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 16 | Inverter | Inverter042_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7128 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 16 | Inverter | Inverter042_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7129 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 17 | Inverter | Inverter042_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7130 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 17 | Inverter | Inverter042_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7131 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 18 | Inverter | Inverter042_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 18 | Inverter | Inverter042_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7133 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 19 | Inverter | Inverter042_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7134 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 19 | Inverter | Inverter042_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7135 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current DC Input 20 | Inverter | Inverter042_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7136 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC input 20 | Inverter | Inverter042_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7137 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current-AC | Inverter | inverter042_MODBUS.HR1007_i3Avg_A | Current-AC | 7138 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Current-DC | Inverter | inverter042_MODBUS.HR1062_idcInput_A | Current-DC | 7139 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Daily Energy Delivered | Inverter | inverter042_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7140 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power Set Point | Inverter | inverter042_MODBUS.HR0553_pRef | Real Power Set Point | 7141 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Reactive Power Set Point | Inverter | inverter042_MODBUS.HR0558_qRef | Reactive Power Set Point | 7142 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Frequency | Inverter | inverter042_MODBUS.HR1012_f3_Hz | Frequency | 7143 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV042 | Daggett 3_SUB1_INV042_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Insulation Resistance | Inverter | inverter042_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7144 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Number of DU Channels | Inverter | inverter042_MODBUS.HR0653_duChannels | Number of DU Channels | 7145 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Number of Running Modules | Inverter | inverter042_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7146 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Operating State | Inverter | inverter042_MODBUS.HR1123_currentStatus | Operating State | 7147 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Power Factor | Inverter | inverter042_MODBUS.HR1011_pf3 | Power Factor | 7148 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV042 | Daggett 3_SUB1_INV042_Ramp Down | Inverter | inverter042_MODBUS.HR0286_dropGradient_p | Ramp Down | 7149 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Ramp Up | Inverter | inverter042_MODBUS.HR0282_riseGradient_p | Ramp Up | 7150 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power Delivered | Inverter | inverter042_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7151 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Reactive Power Delivered | Inverter | inverter042_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7152 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power | 7153 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Reactive Power | Inverter | inverter042_MODBUS.HR1009_q3_kvar | Reactive Power | 7154 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Reactive Power Mode | Inverter | inverter042_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7155 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Reactive Power Set Point Percent | Inverter | inverter042_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7156 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power AC Percent | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7157 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power-AC | Inverter | inverter042_MODBUS.HR1008_p3_kW | Real Power-AC | 7158 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power-DC | Inverter | inverter042_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7159 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Air Intake | Inverter | inverter042_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7160 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Cabinet | Inverter | inverter042_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7161 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-IGBT | Inverter | inverter042_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7162 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Temperature-Module | Inverter | inverter042_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7163 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage A-B | Inverter | inverter042_MODBUS.HR1002_vRS_V | Voltage A-B | 7164 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage B-C | Inverter | inverter042_MODBUS.HR1002_vST_V | Voltage B-C | 7165 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage C-A | Inverter | inverter042_MODBUS.HR1003_vTR_V | Voltage C-A | 7166 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Voltage DC | Inverter | inverter042_MODBUS.HR1051_vdcBus_V | Voltage DC | 7167 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV042 | Daggett 3_SUB1_INV042_Fault Code 1 | Inverter | Inverter042_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7168 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Warning | Inverter | Inverter042_MODBUS.HRxxxx_currentWarning | Warning | 7169 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Internal Input Status | Inverter | Inverter042_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7170 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Internal Output Status | Inverter | Inverter042_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Module Fault Code | Inverter | Inverter042_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Internal Humidity | Inverter | Inverter042_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7173 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Humidity | Inverter | Inverter042_MODBUS.HRxxxx_humidity | Humidity | 7174 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_Comms Fault Time | Inverter | Inverter042_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7175 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Status | Inverter | Inverter042_MODBUS.HRxxxx_M1_status | Module Status | 7176 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 IR | Inverter | Inverter042_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 IS | Inverter | Inverter042_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 IT | Inverter | Inverter042_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7180 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7182 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7183 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 P | Inverter | Inverter042_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7184 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Q | Inverter | Inverter042_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7185 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7186 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7187 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M1 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7190 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Status | Inverter | Inverter042_MODBUS.HRxxxx_M2_status | Module Status | 7191 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 IR | Inverter | Inverter042_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 IS | Inverter | Inverter042_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 IT | Inverter | Inverter042_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7194 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7196 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7197 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7198 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 P | Inverter | Inverter042_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7199 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Q | Inverter | Inverter042_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7200 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7201 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7202 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7203 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7204 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M2 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7205 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Status | Inverter | Inverter042_MODBUS.HRxxxx_M3_status | Module Status | 7206 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 IR | Inverter | Inverter042_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 IS | Inverter | Inverter042_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 IT | Inverter | Inverter042_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7209 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7210 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7211 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7212 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7213 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 P | Inverter | Inverter042_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7214 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Q | Inverter | Inverter042_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7215 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7216 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7217 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7218 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7219 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M3 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7220 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Status | Inverter | Inverter042_MODBUS.HRxxxx_M4_status | Module Status | 7221 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 IR | Inverter | Inverter042_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 IS | Inverter | Inverter042_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 IT | Inverter | Inverter042_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7224 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7225 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7226 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7227 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7228 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 P | Inverter | Inverter042_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7229 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Q | Inverter | Inverter042_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7230 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7231 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7232 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7233 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M4 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7235 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Status | Inverter | Inverter042_MODBUS.HRxxxx_M5_status | Module Status | 7236 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 IR | Inverter | Inverter042_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 IS | Inverter | Inverter042_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 IT | Inverter | Inverter042_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7239 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7240 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7242 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7243 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 P | Inverter | Inverter042_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7244 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Q | Inverter | Inverter042_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7245 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7246 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7247 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M5 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Status | Inverter | Inverter042_MODBUS.HRxxxx_M6_status | Module Status | 7251 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 IR | Inverter | Inverter042_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 IS | Inverter | Inverter042_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7253 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 IT | Inverter | Inverter042_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 IDC | Inverter | Inverter042_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7255 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 VDCP | Inverter | Inverter042_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7256 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 VDCN | Inverter | Inverter042_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7257 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 VDC | Inverter | Inverter042_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7258 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 P | Inverter | Inverter042_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7259 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Q | Inverter | Inverter042_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7260 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Ambient Temp | Inverter | Inverter042_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7261 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Max IGBT Temp | Inverter | Inverter042_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7262 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 IO Status | Inverter | Inverter042_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7263 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Hardware Version | Inverter | Inverter042_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7264 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV042 | Daggett 3_SUB1_INV042_M6 Software Version | Inverter | Inverter042_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7265 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_A Phase Current | Inverter | inverter043_MODBUS.HR1004_i1_A | A Phase Current | 7266 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_B Phase Current | Inverter | inverter043_MODBUS.HR1005_i2_A | B Phase Current | 7267 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_C Phase Current | Inverter | inverter043_MODBUS.HR1006_i3_A | C Phase Current | 7268 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Bus Voltage | Inverter | inverter043_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7269 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV043 | Daggett 3_SUB1_INV043_Apparent Power | Inverter | inverter043_MODBUS.HR1010_s3_VA | Apparent Power | 7270 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 1 | Inverter | Inverter043_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7271 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC Input 1 | Inverter | Inverter043_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7272 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 2 | Inverter | Inverter043_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 2 | Inverter | Inverter043_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7274 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 3 | Inverter | Inverter043_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 3 | Inverter | Inverter043_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7276 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 4 | Inverter | Inverter043_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7277 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 4 | Inverter | Inverter043_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7278 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 5 | Inverter | Inverter043_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7279 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 5 | Inverter | Inverter043_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7280 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 6 | Inverter | Inverter043_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7281 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 6 | Inverter | Inverter043_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7282 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 7 | Inverter | Inverter043_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7283 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 7 | Inverter | Inverter043_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7284 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 8 | Inverter | Inverter043_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7285 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 8 | Inverter | Inverter043_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7286 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 9 | Inverter | Inverter043_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7287 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 9 | Inverter | Inverter043_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7288 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 10 | Inverter | Inverter043_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 10 | Inverter | Inverter043_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7290 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 11 | Inverter | Inverter043_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7291 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 11 | Inverter | Inverter043_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7292 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 12 | Inverter | Inverter043_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7293 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 12 | Inverter | Inverter043_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7294 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 13 | Inverter | Inverter043_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7295 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 13 | Inverter | Inverter043_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7296 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 14 | Inverter | Inverter043_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 14 | Inverter | Inverter043_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7298 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 15 | Inverter | Inverter043_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7299 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 15 | Inverter | Inverter043_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7300 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 16 | Inverter | Inverter043_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7301 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 16 | Inverter | Inverter043_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7302 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 17 | Inverter | Inverter043_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7303 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 17 | Inverter | Inverter043_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7304 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 18 | Inverter | Inverter043_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 18 | Inverter | Inverter043_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7306 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 19 | Inverter | Inverter043_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7307 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 19 | Inverter | Inverter043_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7308 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current DC Input 20 | Inverter | Inverter043_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7309 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC input 20 | Inverter | Inverter043_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7310 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current-AC | Inverter | inverter043_MODBUS.HR1007_i3Avg_A | Current-AC | 7311 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Current-DC | Inverter | inverter043_MODBUS.HR1062_idcInput_A | Current-DC | 7312 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Daily Energy Delivered | Inverter | inverter043_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7313 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power Set Point | Inverter | inverter043_MODBUS.HR0553_pRef | Real Power Set Point | 7314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Reactive Power Set Point | Inverter | inverter043_MODBUS.HR0558_qRef | Reactive Power Set Point | 7315 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Frequency | Inverter | inverter043_MODBUS.HR1012_f3_Hz | Frequency | 7316 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV043 | Daggett 3_SUB1_INV043_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Insulation Resistance | Inverter | inverter043_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7317 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Number of DU Channels | Inverter | inverter043_MODBUS.HR0653_duChannels | Number of DU Channels | 7318 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Number of Running Modules | Inverter | inverter043_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7319 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Operating State | Inverter | inverter043_MODBUS.HR1123_currentStatus | Operating State | 7320 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Power Factor | Inverter | inverter043_MODBUS.HR1011_pf3 | Power Factor | 7321 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV043 | Daggett 3_SUB1_INV043_Ramp Down | Inverter | inverter043_MODBUS.HR0286_dropGradient_p | Ramp Down | 7322 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Ramp Up | Inverter | inverter043_MODBUS.HR0282_riseGradient_p | Ramp Up | 7323 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power Delivered | Inverter | inverter043_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7324 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Reactive Power Delivered | Inverter | inverter043_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7325 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power | 7326 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Reactive Power | Inverter | inverter043_MODBUS.HR1009_q3_kvar | Reactive Power | 7327 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Reactive Power Mode | Inverter | inverter043_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7328 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Reactive Power Set Point Percent | Inverter | inverter043_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7329 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power AC Percent | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7330 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power-AC | Inverter | inverter043_MODBUS.HR1008_p3_kW | Real Power-AC | 7331 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power-DC | Inverter | inverter043_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7332 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Air Intake | Inverter | inverter043_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7333 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Cabinet | Inverter | inverter043_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7334 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-IGBT | Inverter | inverter043_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7335 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Temperature-Module | Inverter | inverter043_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7336 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage A-B | Inverter | inverter043_MODBUS.HR1003_vRS_V | Voltage A-B | 7337 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage B-C | Inverter | inverter043_MODBUS.HR1002_vST_V | Voltage B-C | 7338 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage C-A | Inverter | inverter043_MODBUS.HR1003_vTR_V | Voltage C-A | 7339 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Voltage DC | Inverter | inverter043_MODBUS.HR1051_vdcBus_V | Voltage DC | 7340 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV043 | Daggett 3_SUB1_INV043_Fault Code 1 | Inverter | Inverter043_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7341 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Warning | Inverter | Inverter043_MODBUS.HRxxxx_currentWarning | Warning | 7342 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Internal Input Status | Inverter | Inverter043_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7343 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Internal Output Status | Inverter | Inverter043_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Module Fault Code | Inverter | Inverter043_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Internal Humidity | Inverter | Inverter043_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7346 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Humidity | Inverter | Inverter043_MODBUS.HRxxxx_humidity | Humidity | 7347 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_Comms Fault Time | Inverter | Inverter043_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7348 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Status | Inverter | Inverter043_MODBUS.HRxxxx_M1_status | Module Status | 7349 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 IR | Inverter | Inverter043_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 IS | Inverter | Inverter043_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 IT | Inverter | Inverter043_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7352 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7353 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7355 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7356 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 P | Inverter | Inverter043_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7357 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Q | Inverter | Inverter043_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7358 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7359 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7360 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M1 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7363 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Status | Inverter | Inverter043_MODBUS.HRxxxx_M2_status | Module Status | 7364 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 IR | Inverter | Inverter043_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 IS | Inverter | Inverter043_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 IT | Inverter | Inverter043_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7367 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7368 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7369 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7370 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7371 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 P | Inverter | Inverter043_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7372 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Q | Inverter | Inverter043_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7373 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7374 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7375 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7376 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7377 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M2 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7378 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Status | Inverter | Inverter043_MODBUS.HRxxxx_M3_status | Module Status | 7379 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 IR | Inverter | Inverter043_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 IS | Inverter | Inverter043_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 IT | Inverter | Inverter043_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7382 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7383 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7384 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7385 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7386 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 P | Inverter | Inverter043_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7387 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Q | Inverter | Inverter043_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7388 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7389 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7390 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7391 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7392 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M3 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7393 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Status | Inverter | Inverter043_MODBUS.HRxxxx_M4_status | Module Status | 7394 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 IR | Inverter | Inverter043_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 IS | Inverter | Inverter043_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 IT | Inverter | Inverter043_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7397 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7398 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7399 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7400 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7401 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 P | Inverter | Inverter043_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7402 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Q | Inverter | Inverter043_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7403 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7404 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7405 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7406 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M4 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7408 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Status | Inverter | Inverter043_MODBUS.HRxxxx_M5_status | Module Status | 7409 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 IR | Inverter | Inverter043_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 IS | Inverter | Inverter043_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 IT | Inverter | Inverter043_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7412 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7413 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7415 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7416 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 P | Inverter | Inverter043_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7417 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Q | Inverter | Inverter043_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7418 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7419 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7420 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M5 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Status | Inverter | Inverter043_MODBUS.HRxxxx_M6_status | Module Status | 7424 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 IR | Inverter | Inverter043_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 IS | Inverter | Inverter043_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7426 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 IT | Inverter | Inverter043_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 IDC | Inverter | Inverter043_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7428 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 VDCP | Inverter | Inverter043_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7429 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 VDCN | Inverter | Inverter043_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7430 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 VDC | Inverter | Inverter043_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7431 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 P | Inverter | Inverter043_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7432 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Q | Inverter | Inverter043_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7433 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Ambient Temp | Inverter | Inverter043_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7434 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Max IGBT Temp | Inverter | Inverter043_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7435 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 IO Status | Inverter | Inverter043_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7436 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Hardware Version | Inverter | Inverter043_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7437 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV043 | Daggett 3_SUB1_INV043_M6 Software Version | Inverter | Inverter043_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7438 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_A Phase Current | Inverter | inverter044_MODBUS.HR1004_i1_A | A Phase Current | 7439 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_B Phase Current | Inverter | inverter044_MODBUS.HR1005_i2_A | B Phase Current | 7440 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_C Phase Current | Inverter | inverter044_MODBUS.HR1006_i3_A | C Phase Current | 7441 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Bus Voltage | Inverter | inverter044_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7442 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV044 | Daggett 3_SUB1_INV044_Apparent Power | Inverter | inverter044_MODBUS.HR1010_s3_VA | Apparent Power | 7443 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 1 | Inverter | Inverter044_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7444 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC Input 1 | Inverter | Inverter044_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7445 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 2 | Inverter | Inverter044_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 2 | Inverter | Inverter044_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7447 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 3 | Inverter | Inverter044_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 3 | Inverter | Inverter044_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7449 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 4 | Inverter | Inverter044_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7450 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 4 | Inverter | Inverter044_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7451 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 5 | Inverter | Inverter044_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7452 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 5 | Inverter | Inverter044_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7453 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 6 | Inverter | Inverter044_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7454 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 6 | Inverter | Inverter044_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7455 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 7 | Inverter | Inverter044_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7456 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 7 | Inverter | Inverter044_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7457 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 8 | Inverter | Inverter044_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7458 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 8 | Inverter | Inverter044_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7459 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 9 | Inverter | Inverter044_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7460 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 9 | Inverter | Inverter044_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7461 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 10 | Inverter | Inverter044_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 10 | Inverter | Inverter044_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7463 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 11 | Inverter | Inverter044_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7464 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 11 | Inverter | Inverter044_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7465 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 12 | Inverter | Inverter044_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7466 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 12 | Inverter | Inverter044_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7467 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 13 | Inverter | Inverter044_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7468 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 13 | Inverter | Inverter044_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7469 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 14 | Inverter | Inverter044_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 14 | Inverter | Inverter044_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7471 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 15 | Inverter | Inverter044_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7472 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 15 | Inverter | Inverter044_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7473 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 16 | Inverter | Inverter044_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7474 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 16 | Inverter | Inverter044_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7475 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 17 | Inverter | Inverter044_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7476 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 17 | Inverter | Inverter044_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7477 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 18 | Inverter | Inverter044_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 18 | Inverter | Inverter044_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7479 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 19 | Inverter | Inverter044_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7480 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 19 | Inverter | Inverter044_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7481 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current DC Input 20 | Inverter | Inverter044_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7482 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC input 20 | Inverter | Inverter044_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7483 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current-AC | Inverter | inverter044_MODBUS.HR1007_i3Avg_A | Current-AC | 7484 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Current-DC | Inverter | inverter044_MODBUS.HR1062_idcInput_A | Current-DC | 7485 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Daily Energy Delivered | Inverter | inverter044_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7486 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power Set Point | Inverter | inverter044_MODBUS.HR0553_pRef | Real Power Set Point | 7487 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Reactive Power Set Point | Inverter | inverter044_MODBUS.HR0558_qRef | Reactive Power Set Point | 7488 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Frequency | Inverter | inverter044_MODBUS.HR1012_f3_Hz | Frequency | 7489 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV044 | Daggett 3_SUB1_INV044_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Insulation Resistance | Inverter | inverter044_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7490 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Number of DU Channels | Inverter | inverter044_MODBUS.HR0653_duChannels | Number of DU Channels | 7491 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Number of Running Modules | Inverter | inverter044_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7492 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Operating State | Inverter | inverter044_MODBUS.HR1123_currentStatus | Operating State | 7493 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Power Factor | Inverter | inverter044_MODBUS.HR1011_pf3 | Power Factor | 7494 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV044 | Daggett 3_SUB1_INV044_Ramp Down | Inverter | inverter044_MODBUS.HR0286_dropGradient_p | Ramp Down | 7495 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Ramp Up | Inverter | inverter044_MODBUS.HR0282_riseGradient_p | Ramp Up | 7496 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power Delivered | Inverter | inverter044_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7497 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Reactive Power Delivered | Inverter | inverter044_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7498 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power | 7499 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Reactive Power | Inverter | inverter044_MODBUS.HR1009_q3_kvar | Reactive Power | 7500 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Reactive Power Mode | Inverter | inverter044_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7501 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Reactive Power Set Point Percent | Inverter | inverter044_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7502 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power AC Percent | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7503 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power-AC | Inverter | inverter044_MODBUS.HR1008_p3_kW | Real Power-AC | 7504 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power-DC | Inverter | inverter044_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7505 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Air Intake | Inverter | inverter044_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7506 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Cabinet | Inverter | inverter044_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7507 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-IGBT | Inverter | inverter044_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7508 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Temperature-Module | Inverter | inverter044_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7509 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage A-B | Inverter | inverter044_MODBUS.HR1004_vRS_V | Voltage A-B | 7510 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage B-C | Inverter | inverter044_MODBUS.HR1002_vST_V | Voltage B-C | 7511 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage C-A | Inverter | inverter044_MODBUS.HR1003_vTR_V | Voltage C-A | 7512 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Voltage DC | Inverter | inverter044_MODBUS.HR1051_vdcBus_V | Voltage DC | 7513 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV044 | Daggett 3_SUB1_INV044_Fault Code 1 | Inverter | Inverter044_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7514 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Warning | Inverter | Inverter044_MODBUS.HRxxxx_currentWarning | Warning | 7515 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Internal Input Status | Inverter | Inverter044_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7516 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Internal Output Status | Inverter | Inverter044_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Module Fault Code | Inverter | Inverter044_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Internal Humidity | Inverter | Inverter044_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7519 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Humidity | Inverter | Inverter044_MODBUS.HRxxxx_humidity | Humidity | 7520 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_Comms Fault Time | Inverter | Inverter044_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7521 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Status | Inverter | Inverter044_MODBUS.HRxxxx_M1_status | Module Status | 7522 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 IR | Inverter | Inverter044_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 IS | Inverter | Inverter044_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 IT | Inverter | Inverter044_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7525 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7526 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7528 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7529 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 P | Inverter | Inverter044_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7530 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Q | Inverter | Inverter044_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7531 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7532 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7533 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M1 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7536 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Status | Inverter | Inverter044_MODBUS.HRxxxx_M2_status | Module Status | 7537 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 IR | Inverter | Inverter044_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 IS | Inverter | Inverter044_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 IT | Inverter | Inverter044_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7540 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7541 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7542 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7543 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7544 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 P | Inverter | Inverter044_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7545 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Q | Inverter | Inverter044_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7546 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7547 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7548 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7549 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7550 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M2 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7551 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Status | Inverter | Inverter044_MODBUS.HRxxxx_M3_status | Module Status | 7552 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 IR | Inverter | Inverter044_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 IS | Inverter | Inverter044_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 IT | Inverter | Inverter044_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7555 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7556 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7557 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7558 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7559 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 P | Inverter | Inverter044_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7560 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Q | Inverter | Inverter044_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7561 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7562 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7563 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7564 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7565 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M3 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7566 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Status | Inverter | Inverter044_MODBUS.HRxxxx_M4_status | Module Status | 7567 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 IR | Inverter | Inverter044_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 IS | Inverter | Inverter044_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 IT | Inverter | Inverter044_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7570 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7571 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7572 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7573 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7574 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 P | Inverter | Inverter044_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7575 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Q | Inverter | Inverter044_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7576 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7577 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7578 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7579 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M4 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7581 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Status | Inverter | Inverter044_MODBUS.HRxxxx_M5_status | Module Status | 7582 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 IR | Inverter | Inverter044_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 IS | Inverter | Inverter044_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 IT | Inverter | Inverter044_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7585 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7586 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7588 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7589 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 P | Inverter | Inverter044_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7590 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Q | Inverter | Inverter044_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7591 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7592 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7593 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M5 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Status | Inverter | Inverter044_MODBUS.HRxxxx_M6_status | Module Status | 7597 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 IR | Inverter | Inverter044_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 IS | Inverter | Inverter044_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7599 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 IT | Inverter | Inverter044_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 IDC | Inverter | Inverter044_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7601 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 VDCP | Inverter | Inverter044_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7602 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 VDCN | Inverter | Inverter044_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7603 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 VDC | Inverter | Inverter044_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7604 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 P | Inverter | Inverter044_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7605 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Q | Inverter | Inverter044_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7606 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Ambient Temp | Inverter | Inverter044_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7607 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Max IGBT Temp | Inverter | Inverter044_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7608 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 IO Status | Inverter | Inverter044_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7609 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Hardware Version | Inverter | Inverter044_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7610 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV044 | Daggett 3_SUB1_INV044_M6 Software Version | Inverter | Inverter044_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7611 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_A Phase Current | Inverter | inverter045_MODBUS.HR1004_i1_A | A Phase Current | 7612 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_B Phase Current | Inverter | inverter045_MODBUS.HR1005_i2_A | B Phase Current | 7613 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_C Phase Current | Inverter | inverter045_MODBUS.HR1006_i3_A | C Phase Current | 7614 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Bus Voltage | Inverter | inverter045_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7615 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV045 | Daggett 3_SUB1_INV045_Apparent Power | Inverter | inverter045_MODBUS.HR1010_s3_VA | Apparent Power | 7616 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 1 | Inverter | Inverter045_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7617 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC Input 1 | Inverter | Inverter045_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7618 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 2 | Inverter | Inverter045_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 2 | Inverter | Inverter045_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7620 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 3 | Inverter | Inverter045_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 3 | Inverter | Inverter045_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7622 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 4 | Inverter | Inverter045_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7623 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 4 | Inverter | Inverter045_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7624 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 5 | Inverter | Inverter045_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7625 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 5 | Inverter | Inverter045_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7626 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 6 | Inverter | Inverter045_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7627 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 6 | Inverter | Inverter045_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7628 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 7 | Inverter | Inverter045_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7629 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 7 | Inverter | Inverter045_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7630 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 8 | Inverter | Inverter045_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7631 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 8 | Inverter | Inverter045_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7632 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 9 | Inverter | Inverter045_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7633 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 9 | Inverter | Inverter045_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7634 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 10 | Inverter | Inverter045_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 10 | Inverter | Inverter045_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7636 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 11 | Inverter | Inverter045_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7637 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 11 | Inverter | Inverter045_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7638 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 12 | Inverter | Inverter045_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7639 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 12 | Inverter | Inverter045_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7640 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 13 | Inverter | Inverter045_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7641 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 13 | Inverter | Inverter045_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7642 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 14 | Inverter | Inverter045_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 14 | Inverter | Inverter045_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7644 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 15 | Inverter | Inverter045_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7645 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 15 | Inverter | Inverter045_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7646 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 16 | Inverter | Inverter045_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7647 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 16 | Inverter | Inverter045_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7648 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 17 | Inverter | Inverter045_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7649 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 17 | Inverter | Inverter045_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7650 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 18 | Inverter | Inverter045_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 18 | Inverter | Inverter045_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7652 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 19 | Inverter | Inverter045_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7653 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 19 | Inverter | Inverter045_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7654 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current DC Input 20 | Inverter | Inverter045_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7655 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC input 20 | Inverter | Inverter045_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7656 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current-AC | Inverter | inverter045_MODBUS.HR1007_i3Avg_A | Current-AC | 7657 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Current-DC | Inverter | inverter045_MODBUS.HR1062_idcInput_A | Current-DC | 7658 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Daily Energy Delivered | Inverter | inverter045_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7659 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power Set Point | Inverter | inverter045_MODBUS.HR0553_pRef | Real Power Set Point | 7660 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Reactive Power Set Point | Inverter | inverter045_MODBUS.HR0558_qRef | Reactive Power Set Point | 7661 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Frequency | Inverter | inverter045_MODBUS.HR1012_f3_Hz | Frequency | 7662 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV045 | Daggett 3_SUB1_INV045_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Insulation Resistance | Inverter | inverter045_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7663 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Number of DU Channels | Inverter | inverter045_MODBUS.HR0653_duChannels | Number of DU Channels | 7664 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Number of Running Modules | Inverter | inverter045_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7665 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Operating State | Inverter | inverter045_MODBUS.HR1123_currentStatus | Operating State | 7666 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Power Factor | Inverter | inverter045_MODBUS.HR1011_pf3 | Power Factor | 7667 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV045 | Daggett 3_SUB1_INV045_Ramp Down | Inverter | inverter045_MODBUS.HR0286_dropGradient_p | Ramp Down | 7668 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Ramp Up | Inverter | inverter045_MODBUS.HR0282_riseGradient_p | Ramp Up | 7669 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power Delivered | Inverter | inverter045_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7670 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Reactive Power Delivered | Inverter | inverter045_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7671 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power | 7672 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Reactive Power | Inverter | inverter045_MODBUS.HR1009_q3_kvar | Reactive Power | 7673 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Reactive Power Mode | Inverter | inverter045_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7674 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Reactive Power Set Point Percent | Inverter | inverter045_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7675 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power AC Percent | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7676 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power-AC | Inverter | inverter045_MODBUS.HR1008_p3_kW | Real Power-AC | 7677 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power-DC | Inverter | inverter045_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7678 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Air Intake | Inverter | inverter045_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7679 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Cabinet | Inverter | inverter045_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7680 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-IGBT | Inverter | inverter045_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7681 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Temperature-Module | Inverter | inverter045_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7682 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage A-B | Inverter | inverter045_MODBUS.HR1005_vRS_V | Voltage A-B | 7683 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage B-C | Inverter | inverter045_MODBUS.HR1002_vST_V | Voltage B-C | 7684 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage C-A | Inverter | inverter045_MODBUS.HR1003_vTR_V | Voltage C-A | 7685 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Voltage DC | Inverter | inverter045_MODBUS.HR1051_vdcBus_V | Voltage DC | 7686 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV045 | Daggett 3_SUB1_INV045_Fault Code 1 | Inverter | Inverter045_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7687 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Warning | Inverter | Inverter045_MODBUS.HRxxxx_currentWarning | Warning | 7688 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Internal Input Status | Inverter | Inverter045_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7689 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Internal Output Status | Inverter | Inverter045_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Module Fault Code | Inverter | Inverter045_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Internal Humidity | Inverter | Inverter045_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7692 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Humidity | Inverter | Inverter045_MODBUS.HRxxxx_humidity | Humidity | 7693 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_Comms Fault Time | Inverter | Inverter045_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7694 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Status | Inverter | Inverter045_MODBUS.HRxxxx_M1_status | Module Status | 7695 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 IR | Inverter | Inverter045_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 IS | Inverter | Inverter045_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 IT | Inverter | Inverter045_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7698 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7699 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7701 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7702 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 P | Inverter | Inverter045_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7703 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Q | Inverter | Inverter045_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7704 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7705 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7706 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M1 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7709 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Status | Inverter | Inverter045_MODBUS.HRxxxx_M2_status | Module Status | 7710 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 IR | Inverter | Inverter045_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 IS | Inverter | Inverter045_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 IT | Inverter | Inverter045_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7713 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7714 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7715 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7716 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7717 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 P | Inverter | Inverter045_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7718 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Q | Inverter | Inverter045_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7719 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7720 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7721 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7722 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7723 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M2 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7724 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Status | Inverter | Inverter045_MODBUS.HRxxxx_M3_status | Module Status | 7725 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 IR | Inverter | Inverter045_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 IS | Inverter | Inverter045_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 IT | Inverter | Inverter045_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7728 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7729 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7730 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7731 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7732 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 P | Inverter | Inverter045_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7733 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Q | Inverter | Inverter045_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7734 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7735 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7736 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7737 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7738 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M3 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7739 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Status | Inverter | Inverter045_MODBUS.HRxxxx_M4_status | Module Status | 7740 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 IR | Inverter | Inverter045_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 IS | Inverter | Inverter045_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 IT | Inverter | Inverter045_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7743 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7744 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7745 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7746 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7747 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 P | Inverter | Inverter045_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7748 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Q | Inverter | Inverter045_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7749 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7750 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7751 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7752 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M4 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7754 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Status | Inverter | Inverter045_MODBUS.HRxxxx_M5_status | Module Status | 7755 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 IR | Inverter | Inverter045_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 IS | Inverter | Inverter045_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 IT | Inverter | Inverter045_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7758 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7759 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7761 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7762 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 P | Inverter | Inverter045_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7763 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Q | Inverter | Inverter045_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7764 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7765 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7766 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M5 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Status | Inverter | Inverter045_MODBUS.HRxxxx_M6_status | Module Status | 7770 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 IR | Inverter | Inverter045_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 IS | Inverter | Inverter045_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7772 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 IT | Inverter | Inverter045_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 IDC | Inverter | Inverter045_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7774 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 VDCP | Inverter | Inverter045_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7775 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 VDCN | Inverter | Inverter045_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7776 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 VDC | Inverter | Inverter045_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7777 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 P | Inverter | Inverter045_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7778 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Q | Inverter | Inverter045_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7779 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Ambient Temp | Inverter | Inverter045_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7780 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Max IGBT Temp | Inverter | Inverter045_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7781 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 IO Status | Inverter | Inverter045_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7782 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Hardware Version | Inverter | Inverter045_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7783 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV045 | Daggett 3_SUB1_INV045_M6 Software Version | Inverter | Inverter045_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7784 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_A Phase Current | Inverter | inverter046_MODBUS.HR1004_i1_A | A Phase Current | 7785 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_B Phase Current | Inverter | inverter046_MODBUS.HR1005_i2_A | B Phase Current | 7786 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_C Phase Current | Inverter | inverter046_MODBUS.HR1006_i3_A | C Phase Current | 7787 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Bus Voltage | Inverter | inverter046_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7788 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV046 | Daggett 3_SUB1_INV046_Apparent Power | Inverter | inverter046_MODBUS.HR1010_s3_VA | Apparent Power | 7789 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 1 | Inverter | Inverter046_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7790 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC Input 1 | Inverter | Inverter046_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7791 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 2 | Inverter | Inverter046_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 2 | Inverter | Inverter046_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7793 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 3 | Inverter | Inverter046_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 3 | Inverter | Inverter046_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7795 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 4 | Inverter | Inverter046_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7796 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 4 | Inverter | Inverter046_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7797 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 5 | Inverter | Inverter046_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7798 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 5 | Inverter | Inverter046_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7799 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 6 | Inverter | Inverter046_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7800 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 6 | Inverter | Inverter046_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7801 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 7 | Inverter | Inverter046_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7802 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 7 | Inverter | Inverter046_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7803 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 8 | Inverter | Inverter046_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7804 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 8 | Inverter | Inverter046_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7805 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 9 | Inverter | Inverter046_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7806 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 9 | Inverter | Inverter046_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7807 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 10 | Inverter | Inverter046_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 10 | Inverter | Inverter046_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7809 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 11 | Inverter | Inverter046_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7810 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 11 | Inverter | Inverter046_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7811 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 12 | Inverter | Inverter046_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7812 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 12 | Inverter | Inverter046_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7813 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 13 | Inverter | Inverter046_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7814 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 13 | Inverter | Inverter046_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7815 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 14 | Inverter | Inverter046_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 14 | Inverter | Inverter046_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7817 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 15 | Inverter | Inverter046_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7818 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 15 | Inverter | Inverter046_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7819 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 16 | Inverter | Inverter046_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7820 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 16 | Inverter | Inverter046_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7821 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 17 | Inverter | Inverter046_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7822 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 17 | Inverter | Inverter046_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7823 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 18 | Inverter | Inverter046_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 18 | Inverter | Inverter046_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7825 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 19 | Inverter | Inverter046_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7826 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 19 | Inverter | Inverter046_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 7827 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current DC Input 20 | Inverter | Inverter046_MODBUS.HR5919_du20_idc_A | Current DC Input# | 7828 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC input 20 | Inverter | Inverter046_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 7829 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current-AC | Inverter | inverter046_MODBUS.HR1007_i3Avg_A | Current-AC | 7830 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Current-DC | Inverter | inverter046_MODBUS.HR1062_idcInput_A | Current-DC | 7831 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Daily Energy Delivered | Inverter | inverter046_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 7832 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power Set Point | Inverter | inverter046_MODBUS.HR0553_pRef | Real Power Set Point | 7833 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Reactive Power Set Point | Inverter | inverter046_MODBUS.HR0558_qRef | Reactive Power Set Point | 7834 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Frequency | Inverter | inverter046_MODBUS.HR1012_f3_Hz | Frequency | 7835 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV046 | Daggett 3_SUB1_INV046_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Insulation Resistance | Inverter | inverter046_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 7836 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Number of DU Channels | Inverter | inverter046_MODBUS.HR0653_duChannels | Number of DU Channels | 7837 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Number of Running Modules | Inverter | inverter046_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 7838 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Operating State | Inverter | inverter046_MODBUS.HR1123_currentStatus | Operating State | 7839 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Power Factor | Inverter | inverter046_MODBUS.HR1011_pf3 | Power Factor | 7840 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV046 | Daggett 3_SUB1_INV046_Ramp Down | Inverter | inverter046_MODBUS.HR0286_dropGradient_p | Ramp Down | 7841 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Ramp Up | Inverter | inverter046_MODBUS.HR0282_riseGradient_p | Ramp Up | 7842 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power Delivered | Inverter | inverter046_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 7843 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Reactive Power Delivered | Inverter | inverter046_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 7844 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power | 7845 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Reactive Power | Inverter | inverter046_MODBUS.HR1009_q3_kvar | Reactive Power | 7846 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Reactive Power Mode | Inverter | inverter046_MODBUS.HR0552_qControlMode | Reactive Power Mode | 7847 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Reactive Power Set Point Percent | Inverter | inverter046_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 7848 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power AC Percent | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power AC Percent | 7849 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power-AC | Inverter | inverter046_MODBUS.HR1008_p3_kW | Real Power-AC | 7850 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power-DC | Inverter | inverter046_MODBUS.HR1061_pdcInput_W | Real Power-DC | 7851 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Air Intake | Inverter | inverter046_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 7852 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Cabinet | Inverter | inverter046_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 7853 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-IGBT | Inverter | inverter046_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 7854 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Temperature-Module | Inverter | inverter046_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 7855 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage A-B | Inverter | inverter046_MODBUS.HR1006_vRS_V | Voltage A-B | 7856 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage B-C | Inverter | inverter046_MODBUS.HR1002_vST_V | Voltage B-C | 7857 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage C-A | Inverter | inverter046_MODBUS.HR1003_vTR_V | Voltage C-A | 7858 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Voltage DC | Inverter | inverter046_MODBUS.HR1051_vdcBus_V | Voltage DC | 7859 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV046 | Daggett 3_SUB1_INV046_Fault Code 1 | Inverter | Inverter046_MODBUS.HRxxxx_currentFault | Fault Code 1 | 7860 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Warning | Inverter | Inverter046_MODBUS.HRxxxx_currentWarning | Warning | 7861 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Internal Input Status | Inverter | Inverter046_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 7862 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Internal Output Status | Inverter | Inverter046_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 7863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Module Fault Code | Inverter | Inverter046_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 7864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Internal Humidity | Inverter | Inverter046_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 7865 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Humidity | Inverter | Inverter046_MODBUS.HRxxxx_humidity | Humidity | 7866 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_Comms Fault Time | Inverter | Inverter046_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 7867 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Status | Inverter | Inverter046_MODBUS.HRxxxx_M1_status | Module Status | 7868 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 IR | Inverter | Inverter046_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 7869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 IS | Inverter | Inverter046_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 7870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 IT | Inverter | Inverter046_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 7871 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 7872 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 7873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 7874 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 7875 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 P | Inverter | Inverter046_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 7876 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Q | Inverter | Inverter046_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 7877 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 7878 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 7879 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 7880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 7881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M1 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 7882 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Status | Inverter | Inverter046_MODBUS.HRxxxx_M2_status | Module Status | 7883 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 IR | Inverter | Inverter046_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 7884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 IS | Inverter | Inverter046_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 7885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 IT | Inverter | Inverter046_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 7886 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 7887 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 7888 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 7889 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 7890 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 P | Inverter | Inverter046_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 7891 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Q | Inverter | Inverter046_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 7892 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 7893 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 7894 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 7895 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 7896 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M2 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 7897 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Status | Inverter | Inverter046_MODBUS.HRxxxx_M3_status | Module Status | 7898 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 IR | Inverter | Inverter046_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 7899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 IS | Inverter | Inverter046_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 7900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 IT | Inverter | Inverter046_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 7901 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 7902 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 7903 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 7904 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 7905 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 P | Inverter | Inverter046_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 7906 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Q | Inverter | Inverter046_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 7907 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 7908 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 7909 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 7910 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 7911 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M3 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 7912 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Status | Inverter | Inverter046_MODBUS.HRxxxx_M4_status | Module Status | 7913 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 IR | Inverter | Inverter046_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 7914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 IS | Inverter | Inverter046_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 7915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 IT | Inverter | Inverter046_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 7916 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 7917 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 7918 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 7919 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 7920 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 P | Inverter | Inverter046_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 7921 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Q | Inverter | Inverter046_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 7922 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 7923 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 7924 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 7925 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 7926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M4 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 7927 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Status | Inverter | Inverter046_MODBUS.HRxxxx_M5_status | Module Status | 7928 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 IR | Inverter | Inverter046_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 7929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 IS | Inverter | Inverter046_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 7930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 IT | Inverter | Inverter046_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 7931 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 7932 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 7933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 7934 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 7935 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 P | Inverter | Inverter046_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 7936 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Q | Inverter | Inverter046_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 7937 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 7938 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 7939 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 7940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 7941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M5 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 7942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Status | Inverter | Inverter046_MODBUS.HRxxxx_M6_status | Module Status | 7943 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 IR | Inverter | Inverter046_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 7944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 IS | Inverter | Inverter046_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 7945 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 IT | Inverter | Inverter046_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 7946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 IDC | Inverter | Inverter046_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 7947 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 VDCP | Inverter | Inverter046_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 7948 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 VDCN | Inverter | Inverter046_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 7949 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 VDC | Inverter | Inverter046_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 7950 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 P | Inverter | Inverter046_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 7951 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Q | Inverter | Inverter046_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 7952 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Ambient Temp | Inverter | Inverter046_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 7953 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Max IGBT Temp | Inverter | Inverter046_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 7954 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 IO Status | Inverter | Inverter046_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 7955 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Hardware Version | Inverter | Inverter046_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 7956 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV046 | Daggett 3_SUB1_INV046_M6 Software Version | Inverter | Inverter046_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 7957 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_A Phase Current | Inverter | inverter047_MODBUS.HR1004_i1_A | A Phase Current | 7958 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_B Phase Current | Inverter | inverter047_MODBUS.HR1005_i2_A | B Phase Current | 7959 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_C Phase Current | Inverter | inverter047_MODBUS.HR1006_i3_A | C Phase Current | 7960 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Bus Voltage | Inverter | inverter047_MODBUS.HR1051_vdcBus_V | Bus Voltage | 7961 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV047 | Daggett 3_SUB1_INV047_Apparent Power | Inverter | inverter047_MODBUS.HR1010_s3_VA | Apparent Power | 7962 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 1 | Inverter | Inverter047_MODBUS.HR5805_du1_idc_A | Current DC Input# | 7963 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC Input 1 | Inverter | Inverter047_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 7964 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 2 | Inverter | Inverter047_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 2 | Inverter | Inverter047_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 7966 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 3 | Inverter | Inverter047_MODBUS.HR5817_du3_idc_A | Current DC Input# | 7967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 3 | Inverter | Inverter047_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 7968 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 4 | Inverter | Inverter047_MODBUS.HR5823_du4_idc_A | Current DC Input# | 7969 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 4 | Inverter | Inverter047_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 7970 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 5 | Inverter | Inverter047_MODBUS.HR5829_du5_idc_A | Current DC Input# | 7971 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 5 | Inverter | Inverter047_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 7972 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 6 | Inverter | Inverter047_MODBUS.HR5835_du6_idc_A | Current DC Input# | 7973 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 6 | Inverter | Inverter047_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 7974 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 7 | Inverter | Inverter047_MODBUS.HR5841_du7_idc_A | Current DC Input# | 7975 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 7 | Inverter | Inverter047_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 7976 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 8 | Inverter | Inverter047_MODBUS.HR5847_du8_idc_A | Current DC Input# | 7977 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 8 | Inverter | Inverter047_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 7978 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 9 | Inverter | Inverter047_MODBUS.HR5853_du9_idc_A | Current DC Input# | 7979 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 9 | Inverter | Inverter047_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 7980 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 10 | Inverter | Inverter047_MODBUS.HR5859_du10_idc_A | Current DC Input# | 7981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 10 | Inverter | Inverter047_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 7982 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 11 | Inverter | Inverter047_MODBUS.HR5865_du11_idc_A | Current DC Input# | 7983 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 11 | Inverter | Inverter047_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 7984 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 12 | Inverter | Inverter047_MODBUS.HR5871_du12_idc_A | Current DC Input# | 7985 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 12 | Inverter | Inverter047_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 7986 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 13 | Inverter | Inverter047_MODBUS.HR5877_du13_idc_A | Current DC Input# | 7987 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 13 | Inverter | Inverter047_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 7988 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 14 | Inverter | Inverter047_MODBUS.HR5883_du14_idc_A | Current DC Input# | 7989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 14 | Inverter | Inverter047_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 7990 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 15 | Inverter | Inverter047_MODBUS.HR5889_du15_idc_A | Current DC Input# | 7991 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 15 | Inverter | Inverter047_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 7992 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 16 | Inverter | Inverter047_MODBUS.HR5895_du16_idc_A | Current DC Input# | 7993 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 16 | Inverter | Inverter047_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 7994 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 17 | Inverter | Inverter047_MODBUS.HR5901_du17_idc_A | Current DC Input# | 7995 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 17 | Inverter | Inverter047_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 7996 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 18 | Inverter | Inverter047_MODBUS.HR5907_du18_idc_A | Current DC Input# | 7997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 18 | Inverter | Inverter047_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 7998 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 19 | Inverter | Inverter047_MODBUS.HR5913_du19_idc_A | Current DC Input# | 7999 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 19 | Inverter | Inverter047_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 8000 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current DC Input 20 | Inverter | Inverter047_MODBUS.HR5919_du20_idc_A | Current DC Input# | 8001 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC input 20 | Inverter | Inverter047_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 8002 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current-AC | Inverter | inverter047_MODBUS.HR1007_i3Avg_A | Current-AC | 8003 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Current-DC | Inverter | inverter047_MODBUS.HR1062_idcInput_A | Current-DC | 8004 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Daily Energy Delivered | Inverter | inverter047_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 8005 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power Set Point | Inverter | inverter047_MODBUS.HR0553_pRef | Real Power Set Point | 8006 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Reactive Power Set Point | Inverter | inverter047_MODBUS.HR0558_qRef | Reactive Power Set Point | 8007 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Frequency | Inverter | inverter047_MODBUS.HR1012_f3_Hz | Frequency | 8008 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV047 | Daggett 3_SUB1_INV047_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Insulation Resistance | Inverter | inverter047_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 8009 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Number of DU Channels | Inverter | inverter047_MODBUS.HR0653_duChannels | Number of DU Channels | 8010 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Number of Running Modules | Inverter | inverter047_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 8011 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Operating State | Inverter | inverter047_MODBUS.HR1123_currentStatus | Operating State | 8012 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Power Factor | Inverter | inverter047_MODBUS.HR1011_pf3 | Power Factor | 8013 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV047 | Daggett 3_SUB1_INV047_Ramp Down | Inverter | inverter047_MODBUS.HR0286_dropGradient_p | Ramp Down | 8014 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Ramp Up | Inverter | inverter047_MODBUS.HR0282_riseGradient_p | Ramp Up | 8015 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power Delivered | Inverter | inverter047_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 8016 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Reactive Power Delivered | Inverter | inverter047_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 8017 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power | 8018 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Reactive Power | Inverter | inverter047_MODBUS.HR1009_q3_kvar | Reactive Power | 8019 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Reactive Power Mode | Inverter | inverter047_MODBUS.HR0552_qControlMode | Reactive Power Mode | 8020 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Reactive Power Set Point Percent | Inverter | inverter047_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 8021 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power AC Percent | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power AC Percent | 8022 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power-AC | Inverter | inverter047_MODBUS.HR1008_p3_kW | Real Power-AC | 8023 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power-DC | Inverter | inverter047_MODBUS.HR1061_pdcInput_W | Real Power-DC | 8024 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Air Intake | Inverter | inverter047_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 8025 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Cabinet | Inverter | inverter047_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 8026 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-IGBT | Inverter | inverter047_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 8027 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Temperature-Module | Inverter | inverter047_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 8028 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage A-B | Inverter | inverter047_MODBUS.HR1007_vRS_V | Voltage A-B | 8029 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage B-C | Inverter | inverter047_MODBUS.HR1002_vST_V | Voltage B-C | 8030 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage C-A | Inverter | inverter047_MODBUS.HR1003_vTR_V | Voltage C-A | 8031 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Voltage DC | Inverter | inverter047_MODBUS.HR1051_vdcBus_V | Voltage DC | 8032 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV047 | Daggett 3_SUB1_INV047_Fault Code 1 | Inverter | Inverter047_MODBUS.HRxxxx_currentFault | Fault Code 1 | 8033 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Warning | Inverter | Inverter047_MODBUS.HRxxxx_currentWarning | Warning | 8034 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Internal Input Status | Inverter | Inverter047_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 8035 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Internal Output Status | Inverter | Inverter047_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 8036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Module Fault Code | Inverter | Inverter047_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 8037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Internal Humidity | Inverter | Inverter047_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 8038 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Humidity | Inverter | Inverter047_MODBUS.HRxxxx_humidity | Humidity | 8039 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_Comms Fault Time | Inverter | Inverter047_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 8040 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Status | Inverter | Inverter047_MODBUS.HRxxxx_M1_status | Module Status | 8041 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 IR | Inverter | Inverter047_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 8042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 IS | Inverter | Inverter047_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 8043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 IT | Inverter | Inverter047_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 8044 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 8045 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 8046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 8047 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 8048 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 P | Inverter | Inverter047_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 8049 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Q | Inverter | Inverter047_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 8050 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 8051 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 8052 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 8053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 8054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M1 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 8055 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Status | Inverter | Inverter047_MODBUS.HRxxxx_M2_status | Module Status | 8056 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 IR | Inverter | Inverter047_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 8057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 IS | Inverter | Inverter047_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 8058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 IT | Inverter | Inverter047_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 8059 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 8060 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 8061 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 8062 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 8063 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 P | Inverter | Inverter047_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 8064 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Q | Inverter | Inverter047_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 8065 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 8066 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 8067 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 8068 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 8069 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M2 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 8070 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Status | Inverter | Inverter047_MODBUS.HRxxxx_M3_status | Module Status | 8071 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 IR | Inverter | Inverter047_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 8072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 IS | Inverter | Inverter047_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 8073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 IT | Inverter | Inverter047_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 8074 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 8075 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 8076 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 8077 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 8078 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 P | Inverter | Inverter047_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 8079 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Q | Inverter | Inverter047_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 8080 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 8081 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 8082 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 8083 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 8084 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M3 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 8085 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Status | Inverter | Inverter047_MODBUS.HRxxxx_M4_status | Module Status | 8086 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 IR | Inverter | Inverter047_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 8087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 IS | Inverter | Inverter047_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 8088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 IT | Inverter | Inverter047_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 8089 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 8090 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 8091 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 8092 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 8093 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 P | Inverter | Inverter047_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 8094 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Q | Inverter | Inverter047_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 8095 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 8096 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 8097 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 8098 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 8099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M4 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 8100 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Status | Inverter | Inverter047_MODBUS.HRxxxx_M5_status | Module Status | 8101 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 IR | Inverter | Inverter047_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 8102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 IS | Inverter | Inverter047_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 8103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 IT | Inverter | Inverter047_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 8104 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 8105 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 8106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 8107 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 8108 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 P | Inverter | Inverter047_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 8109 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Q | Inverter | Inverter047_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 8110 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 8111 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 8112 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 8113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 8114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M5 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 8115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Status | Inverter | Inverter047_MODBUS.HRxxxx_M6_status | Module Status | 8116 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 IR | Inverter | Inverter047_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 8117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 IS | Inverter | Inverter047_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 8118 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 IT | Inverter | Inverter047_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 8119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 IDC | Inverter | Inverter047_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 8120 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 VDCP | Inverter | Inverter047_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 8121 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 VDCN | Inverter | Inverter047_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 8122 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 VDC | Inverter | Inverter047_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 8123 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 P | Inverter | Inverter047_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 8124 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Q | Inverter | Inverter047_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 8125 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Ambient Temp | Inverter | Inverter047_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 8126 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Max IGBT Temp | Inverter | Inverter047_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 8127 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 IO Status | Inverter | Inverter047_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 8128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Hardware Version | Inverter | Inverter047_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 8129 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV047 | Daggett 3_SUB1_INV047_M6 Software Version | Inverter | Inverter047_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 8130 |  | Requested-Available | 0 | 65535 | 1
Digital Inputs
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV001 | Daggett 3_SUB1_INV001_AutoStart On | Inverter | Inverter001_MODBUS.HR0501_restartEn | AutoStart On | 0 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Comm Fail | Inverter | Inverter001_commsFail | Comm Fail | 1 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Faulted | Inverter | Inverter001_fault | Faulted | 2 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Locked Out | Inverter | Inverter001_lockout | Locked Out | 3 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Master Control Enabled | Inverter | Inverter001_masterControl | Master Control Enabled | 4 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Offline | Inverter | Inverter001_offline | Offline | 5 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Ramp Up Enabled | Inverter | Inverter001_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 6 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Ramp Down Enabled | Inverter | Inverter001_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 7 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Real Power Curtailment Flag | Inverter | Inverter001_curtailed | Real Power Curtailment Flag | 8 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Following Setpoint | Inverter | Inverter001_follwing | Following Setpoint | 9 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_AutoStart On | Inverter | Inverter002_MODBUS.HR0501_restartEn | AutoStart On | 10 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Comm Fail | Inverter | Inverter002_commsFail | Comm Fail | 11 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Faulted | Inverter | Inverter002_fault | Faulted | 12 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Locked Out | Inverter | Inverter002_lockout | Locked Out | 13 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Master Control Enabled | Inverter | Inverter002_masterControl | Master Control Enabled | 14 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Offline | Inverter | Inverter002_offline | Offline | 15 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Ramp Up Enabled | Inverter | Inverter002_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 16 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Ramp Down Enabled | Inverter | Inverter002_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 17 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Real Power Curtailment Flag | Inverter | Inverter002_curtailed | Real Power Curtailment Flag | 18 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Following Setpoint | Inverter | Inverter002_follwing | Following Setpoint | 19 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_AutoStart On | Inverter | Inverter003_MODBUS.HR0501_restartEn | AutoStart On | 20 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Comm Fail | Inverter | Inverter003_commsFail | Comm Fail | 21 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Faulted | Inverter | Inverter003_fault | Faulted | 22 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Locked Out | Inverter | Inverter003_lockout | Locked Out | 23 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Master Control Enabled | Inverter | Inverter003_masterControl | Master Control Enabled | 24 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Offline | Inverter | Inverter003_offline | Offline | 25 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Ramp Up Enabled | Inverter | Inverter003_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 26 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Ramp Down Enabled | Inverter | Inverter003_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 27 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Real Power Curtailment Flag | Inverter | Inverter003_curtailed | Real Power Curtailment Flag | 28 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Following Setpoint | Inverter | Inverter003_follwing | Following Setpoint | 29 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_AutoStart On | Inverter | Inverter004_MODBUS.HR0501_restartEn | AutoStart On | 30 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Comm Fail | Inverter | Inverter004_commsFail | Comm Fail | 31 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Faulted | Inverter | Inverter004_fault | Faulted | 32 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Locked Out | Inverter | Inverter004_lockout | Locked Out | 33 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Master Control Enabled | Inverter | Inverter004_masterControl | Master Control Enabled | 34 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Offline | Inverter | Inverter004_offline | Offline | 35 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Ramp Up Enabled | Inverter | Inverter004_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 36 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Ramp Down Enabled | Inverter | Inverter004_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 37 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Real Power Curtailment Flag | Inverter | Inverter004_curtailed | Real Power Curtailment Flag | 38 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Following Setpoint | Inverter | Inverter004_follwing | Following Setpoint | 39 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_AutoStart On | Inverter | Inverter005_MODBUS.HR0501_restartEn | AutoStart On | 40 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Comm Fail | Inverter | Inverter005_commsFail | Comm Fail | 41 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Faulted | Inverter | Inverter005_fault | Faulted | 42 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Locked Out | Inverter | Inverter005_lockout | Locked Out | 43 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Master Control Enabled | Inverter | Inverter005_masterControl | Master Control Enabled | 44 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Offline | Inverter | Inverter005_offline | Offline | 45 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Ramp Up Enabled | Inverter | Inverter005_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 46 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Ramp Down Enabled | Inverter | Inverter005_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 47 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Real Power Curtailment Flag | Inverter | Inverter005_curtailed | Real Power Curtailment Flag | 48 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Following Setpoint | Inverter | Inverter005_follwing | Following Setpoint | 49 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_AutoStart On | Inverter | Inverter006_MODBUS.HR0501_restartEn | AutoStart On | 50 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Comm Fail | Inverter | Inverter006_commsFail | Comm Fail | 51 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Faulted | Inverter | Inverter006_fault | Faulted | 52 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Locked Out | Inverter | Inverter006_lockout | Locked Out | 53 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Master Control Enabled | Inverter | Inverter006_masterControl | Master Control Enabled | 54 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Offline | Inverter | Inverter006_offline | Offline | 55 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Ramp Up Enabled | Inverter | Inverter006_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 56 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Ramp Down Enabled | Inverter | Inverter006_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 57 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Real Power Curtailment Flag | Inverter | Inverter006_curtailed | Real Power Curtailment Flag | 58 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Following Setpoint | Inverter | Inverter006_follwing | Following Setpoint | 59 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_AutoStart On | Inverter | Inverter007_MODBUS.HR0501_restartEn | AutoStart On | 60 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Comm Fail | Inverter | Inverter007_commsFail | Comm Fail | 61 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Faulted | Inverter | Inverter007_fault | Faulted | 62 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Locked Out | Inverter | Inverter007_lockout | Locked Out | 63 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Master Control Enabled | Inverter | Inverter007_masterControl | Master Control Enabled | 64 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Offline | Inverter | Inverter007_offline | Offline | 65 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Ramp Up Enabled | Inverter | Inverter007_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 66 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Ramp Down Enabled | Inverter | Inverter007_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 67 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Real Power Curtailment Flag | Inverter | Inverter007_curtailed | Real Power Curtailment Flag | 68 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Following Setpoint | Inverter | Inverter007_follwing | Following Setpoint | 69 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_AutoStart On | Inverter | Inverter008_MODBUS.HR0501_restartEn | AutoStart On | 70 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Comm Fail | Inverter | Inverter008_commsFail | Comm Fail | 71 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Faulted | Inverter | Inverter008_fault | Faulted | 72 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Locked Out | Inverter | Inverter008_lockout | Locked Out | 73 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Master Control Enabled | Inverter | Inverter008_masterControl | Master Control Enabled | 74 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Offline | Inverter | Inverter008_offline | Offline | 75 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Ramp Up Enabled | Inverter | Inverter008_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 76 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Ramp Down Enabled | Inverter | Inverter008_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 77 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Real Power Curtailment Flag | Inverter | Inverter008_curtailed | Real Power Curtailment Flag | 78 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Following Setpoint | Inverter | Inverter008_follwing | Following Setpoint | 79 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_AutoStart On | Inverter | Inverter009_MODBUS.HR0501_restartEn | AutoStart On | 80 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Comm Fail | Inverter | Inverter009_commsFail | Comm Fail | 81 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Faulted | Inverter | Inverter009_fault | Faulted | 82 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Locked Out | Inverter | Inverter009_lockout | Locked Out | 83 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Master Control Enabled | Inverter | Inverter009_masterControl | Master Control Enabled | 84 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Offline | Inverter | Inverter009_offline | Offline | 85 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Ramp Up Enabled | Inverter | Inverter009_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 86 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Ramp Down Enabled | Inverter | Inverter009_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 87 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Real Power Curtailment Flag | Inverter | Inverter009_curtailed | Real Power Curtailment Flag | 88 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Following Setpoint | Inverter | Inverter009_follwing | Following Setpoint | 89 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_AutoStart On | Inverter | Inverter010_MODBUS.HR0501_restartEn | AutoStart On | 90 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Comm Fail | Inverter | Inverter010_commsFail | Comm Fail | 91 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Faulted | Inverter | Inverter010_fault | Faulted | 92 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Locked Out | Inverter | Inverter010_lockout | Locked Out | 93 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Master Control Enabled | Inverter | Inverter010_masterControl | Master Control Enabled | 94 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Offline | Inverter | Inverter010_offline | Offline | 95 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Ramp Up Enabled | Inverter | Inverter010_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 96 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Ramp Down Enabled | Inverter | Inverter010_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 97 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Real Power Curtailment Flag | Inverter | Inverter010_curtailed | Real Power Curtailment Flag | 98 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Following Setpoint | Inverter | Inverter010_follwing | Following Setpoint | 99 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_AutoStart On | Inverter | inverter011_MODBUS.HR0501_restartEn | AutoStart On | 100 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Comm Fail | Inverter | inverter011_commsFail | Comm Fail | 101 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Faulted | Inverter | inverter011_fault | Faulted | 102 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Locked Out | Inverter | inverter011_lockout | Locked Out | 103 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Master Control Enabled | Inverter | inverter011_masterControl | Master Control Enabled | 104 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Offline | Inverter | inverter011_offline | Offline | 105 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Ramp Up Enabled | Inverter | inverter011_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 106 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Ramp Down Enabled | Inverter | inverter011_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 107 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Real Power Curtailment Flag | Inverter | inverter011_curtailed | Real Power Curtailment Flag | 108 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Following Setpoint | Inverter | inverter011_follwing | Following Setpoint | 109 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_AutoStart On | Inverter | inverter012_MODBUS.HR0501_restartEn | AutoStart On | 110 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Comm Fail | Inverter | inverter012_commsFail | Comm Fail | 111 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Faulted | Inverter | inverter012_fault | Faulted | 112 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Locked Out | Inverter | inverter012_lockout | Locked Out | 113 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Master Control Enabled | Inverter | inverter012_masterControl | Master Control Enabled | 114 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Offline | Inverter | inverter012_offline | Offline | 115 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Ramp Up Enabled | Inverter | inverter012_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 116 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Ramp Down Enabled | Inverter | inverter012_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 117 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Real Power Curtailment Flag | Inverter | inverter012_curtailed | Real Power Curtailment Flag | 118 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Following Setpoint | Inverter | inverter012_follwing | Following Setpoint | 119 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_AutoStart On | Inverter | inverter013_MODBUS.HR0501_restartEn | AutoStart On | 120 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Comm Fail | Inverter | inverter013_commsFail | Comm Fail | 121 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Faulted | Inverter | inverter013_fault | Faulted | 122 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Locked Out | Inverter | inverter013_lockout | Locked Out | 123 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Master Control Enabled | Inverter | inverter013_masterControl | Master Control Enabled | 124 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Offline | Inverter | inverter013_offline | Offline | 125 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Ramp Up Enabled | Inverter | inverter013_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 126 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Ramp Down Enabled | Inverter | inverter013_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 127 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Real Power Curtailment Flag | Inverter | inverter013_curtailed | Real Power Curtailment Flag | 128 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Following Setpoint | Inverter | inverter013_follwing | Following Setpoint | 129 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_AutoStart On | Inverter | inverter014_MODBUS.HR0501_restartEn | AutoStart On | 130 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Comm Fail | Inverter | inverter014_commsFail | Comm Fail | 131 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Faulted | Inverter | inverter014_fault | Faulted | 132 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Locked Out | Inverter | inverter014_lockout | Locked Out | 133 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Master Control Enabled | Inverter | inverter014_masterControl | Master Control Enabled | 134 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Offline | Inverter | inverter014_offline | Offline | 135 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Ramp Up Enabled | Inverter | inverter014_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 136 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Ramp Down Enabled | Inverter | inverter014_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 137 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Real Power Curtailment Flag | Inverter | inverter014_curtailed | Real Power Curtailment Flag | 138 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Following Setpoint | Inverter | inverter014_follwing | Following Setpoint | 139 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_AutoStart On | Inverter | inverter015_MODBUS.HR0501_restartEn | AutoStart On | 140 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Comm Fail | Inverter | inverter015_commsFail | Comm Fail | 141 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Faulted | Inverter | inverter015_fault | Faulted | 142 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Locked Out | Inverter | inverter015_lockout | Locked Out | 143 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Master Control Enabled | Inverter | inverter015_masterControl | Master Control Enabled | 144 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Offline | Inverter | inverter015_offline | Offline | 145 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Ramp Up Enabled | Inverter | inverter015_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 146 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Ramp Down Enabled | Inverter | inverter015_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 147 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Real Power Curtailment Flag | Inverter | inverter015_curtailed | Real Power Curtailment Flag | 148 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Following Setpoint | Inverter | inverter015_follwing | Following Setpoint | 149 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_AutoStart On | Inverter | inverter016_MODBUS.HR0501_restartEn | AutoStart On | 150 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Comm Fail | Inverter | inverter016_commsFail | Comm Fail | 151 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Faulted | Inverter | inverter016_fault | Faulted | 152 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Locked Out | Inverter | inverter016_lockout | Locked Out | 153 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Master Control Enabled | Inverter | inverter016_masterControl | Master Control Enabled | 154 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Offline | Inverter | inverter016_offline | Offline | 155 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Ramp Up Enabled | Inverter | inverter016_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 156 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Ramp Down Enabled | Inverter | inverter016_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 157 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Real Power Curtailment Flag | Inverter | inverter016_curtailed | Real Power Curtailment Flag | 158 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Following Setpoint | Inverter | inverter016_follwing | Following Setpoint | 159 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_AutoStart On | Inverter | inverter017_MODBUS.HR0501_restartEn | AutoStart On | 160 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Comm Fail | Inverter | inverter017_commsFail | Comm Fail | 161 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Faulted | Inverter | inverter017_fault | Faulted | 162 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Locked Out | Inverter | inverter017_lockout | Locked Out | 163 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Master Control Enabled | Inverter | inverter017_masterControl | Master Control Enabled | 164 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Offline | Inverter | inverter017_offline | Offline | 165 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Ramp Up Enabled | Inverter | inverter017_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 166 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Ramp Down Enabled | Inverter | inverter017_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 167 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Real Power Curtailment Flag | Inverter | inverter017_curtailed | Real Power Curtailment Flag | 168 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Following Setpoint | Inverter | inverter017_follwing | Following Setpoint | 169 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_AutoStart On | Inverter | inverter018_MODBUS.HR0501_restartEn | AutoStart On | 170 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Comm Fail | Inverter | inverter018_commsFail | Comm Fail | 171 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Faulted | Inverter | inverter018_fault | Faulted | 172 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Locked Out | Inverter | inverter018_lockout | Locked Out | 173 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Master Control Enabled | Inverter | inverter018_masterControl | Master Control Enabled | 174 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Offline | Inverter | inverter018_offline | Offline | 175 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Ramp Up Enabled | Inverter | inverter018_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 176 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Ramp Down Enabled | Inverter | inverter018_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 177 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Real Power Curtailment Flag | Inverter | inverter018_curtailed | Real Power Curtailment Flag | 178 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Following Setpoint | Inverter | inverter018_follwing | Following Setpoint | 179 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_AutoStart On | Inverter | inverter019_MODBUS.HR0501_restartEn | AutoStart On | 180 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Comm Fail | Inverter | inverter019_commsFail | Comm Fail | 181 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Faulted | Inverter | inverter019_fault | Faulted | 182 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Locked Out | Inverter | inverter019_lockout | Locked Out | 183 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Master Control Enabled | Inverter | inverter019_masterControl | Master Control Enabled | 184 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Offline | Inverter | inverter019_offline | Offline | 185 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Ramp Up Enabled | Inverter | inverter019_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 186 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Ramp Down Enabled | Inverter | inverter019_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 187 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Real Power Curtailment Flag | Inverter | inverter019_curtailed | Real Power Curtailment Flag | 188 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Following Setpoint | Inverter | inverter019_follwing | Following Setpoint | 189 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_AutoStart On | Inverter | inverter020_MODBUS.HR0501_restartEn | AutoStart On | 190 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Comm Fail | Inverter | inverter020_commsFail | Comm Fail | 191 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Faulted | Inverter | inverter020_fault | Faulted | 192 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Locked Out | Inverter | inverter020_lockout | Locked Out | 193 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Master Control Enabled | Inverter | inverter020_masterControl | Master Control Enabled | 194 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Offline | Inverter | inverter020_offline | Offline | 195 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Ramp Up Enabled | Inverter | inverter020_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 196 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Ramp Down Enabled | Inverter | inverter020_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 197 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Real Power Curtailment Flag | Inverter | inverter020_curtailed | Real Power Curtailment Flag | 198 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Following Setpoint | Inverter | inverter020_follwing | Following Setpoint | 199 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_AutoStart On | Inverter | inverter021_MODBUS.HR0501_restartEn | AutoStart On | 200 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Comm Fail | Inverter | inverter021_commsFail | Comm Fail | 201 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Faulted | Inverter | inverter021_fault | Faulted | 202 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Locked Out | Inverter | inverter021_lockout | Locked Out | 203 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Master Control Enabled | Inverter | inverter021_masterControl | Master Control Enabled | 204 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Offline | Inverter | inverter021_offline | Offline | 205 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Ramp Up Enabled | Inverter | inverter021_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 206 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Ramp Down Enabled | Inverter | inverter021_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 207 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Real Power Curtailment Flag | Inverter | inverter021_curtailed | Real Power Curtailment Flag | 208 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Following Setpoint | Inverter | inverter021_follwing | Following Setpoint | 209 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_AutoStart On | Inverter | inverter022_MODBUS.HR0501_restartEn | AutoStart On | 210 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Comm Fail | Inverter | inverter022_commsFail | Comm Fail | 211 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Faulted | Inverter | inverter022_fault | Faulted | 212 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Locked Out | Inverter | inverter022_lockout | Locked Out | 213 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Master Control Enabled | Inverter | inverter022_masterControl | Master Control Enabled | 214 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Offline | Inverter | inverter022_offline | Offline | 215 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Ramp Up Enabled | Inverter | inverter022_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 216 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Ramp Down Enabled | Inverter | inverter022_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 217 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Real Power Curtailment Flag | Inverter | inverter022_curtailed | Real Power Curtailment Flag | 218 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Following Setpoint | Inverter | inverter022_follwing | Following Setpoint | 219 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_AutoStart On | Inverter | inverter023_MODBUS.HR0501_restartEn | AutoStart On | 220 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Comm Fail | Inverter | inverter023_commsFail | Comm Fail | 221 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Faulted | Inverter | inverter023_fault | Faulted | 222 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Locked Out | Inverter | inverter023_lockout | Locked Out | 223 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Master Control Enabled | Inverter | inverter023_masterControl | Master Control Enabled | 224 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Offline | Inverter | inverter023_offline | Offline | 225 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Ramp Up Enabled | Inverter | inverter023_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 226 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Ramp Down Enabled | Inverter | inverter023_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 227 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Real Power Curtailment Flag | Inverter | inverter023_curtailed | Real Power Curtailment Flag | 228 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Following Setpoint | Inverter | inverter023_follwing | Following Setpoint | 229 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_AutoStart On | Inverter | inverter024_MODBUS.HR0501_restartEn | AutoStart On | 230 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Comm Fail | Inverter | inverter024_commsFail | Comm Fail | 231 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Faulted | Inverter | inverter024_fault | Faulted | 232 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Locked Out | Inverter | inverter024_lockout | Locked Out | 233 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Master Control Enabled | Inverter | inverter024_masterControl | Master Control Enabled | 234 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Offline | Inverter | inverter024_offline | Offline | 235 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Ramp Up Enabled | Inverter | inverter024_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 236 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Ramp Down Enabled | Inverter | inverter024_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 237 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Real Power Curtailment Flag | Inverter | inverter024_curtailed | Real Power Curtailment Flag | 238 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Following Setpoint | Inverter | inverter024_follwing | Following Setpoint | 239 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_AutoStart On | Inverter | inverter025_MODBUS.HR0501_restartEn | AutoStart On | 240 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Comm Fail | Inverter | inverter025_commsFail | Comm Fail | 241 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Faulted | Inverter | inverter025_fault | Faulted | 242 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Locked Out | Inverter | inverter025_lockout | Locked Out | 243 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Master Control Enabled | Inverter | inverter025_masterControl | Master Control Enabled | 244 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Offline | Inverter | inverter025_offline | Offline | 245 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Ramp Up Enabled | Inverter | inverter025_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 246 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Ramp Down Enabled | Inverter | inverter025_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 247 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Real Power Curtailment Flag | Inverter | inverter025_curtailed | Real Power Curtailment Flag | 248 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Following Setpoint | Inverter | inverter025_follwing | Following Setpoint | 249 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_AutoStart On | Inverter | inverter026_MODBUS.HR0501_restartEn | AutoStart On | 250 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Comm Fail | Inverter | inverter026_commsFail | Comm Fail | 251 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Faulted | Inverter | inverter026_fault | Faulted | 252 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Locked Out | Inverter | inverter026_lockout | Locked Out | 253 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Master Control Enabled | Inverter | inverter026_masterControl | Master Control Enabled | 254 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Offline | Inverter | inverter026_offline | Offline | 255 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Ramp Up Enabled | Inverter | inverter026_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 256 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Ramp Down Enabled | Inverter | inverter026_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 257 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Real Power Curtailment Flag | Inverter | inverter026_curtailed | Real Power Curtailment Flag | 258 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Following Setpoint | Inverter | inverter026_follwing | Following Setpoint | 259 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_AutoStart On | Inverter | inverter027_MODBUS.HR0501_restartEn | AutoStart On | 260 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Comm Fail | Inverter | inverter027_commsFail | Comm Fail | 261 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Faulted | Inverter | inverter027_fault | Faulted | 262 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Locked Out | Inverter | inverter027_lockout | Locked Out | 263 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Master Control Enabled | Inverter | inverter027_masterControl | Master Control Enabled | 264 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Offline | Inverter | inverter027_offline | Offline | 265 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Ramp Up Enabled | Inverter | inverter027_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 266 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Ramp Down Enabled | Inverter | inverter027_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 267 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Real Power Curtailment Flag | Inverter | inverter027_curtailed | Real Power Curtailment Flag | 268 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Following Setpoint | Inverter | inverter027_follwing | Following Setpoint | 269 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_AutoStart On | Inverter | inverter028_MODBUS.HR0501_restartEn | AutoStart On | 270 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Comm Fail | Inverter | inverter028_commsFail | Comm Fail | 271 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Faulted | Inverter | inverter028_fault | Faulted | 272 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Locked Out | Inverter | inverter028_lockout | Locked Out | 273 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Master Control Enabled | Inverter | inverter028_masterControl | Master Control Enabled | 274 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Offline | Inverter | inverter028_offline | Offline | 275 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Ramp Up Enabled | Inverter | inverter028_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 276 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Ramp Down Enabled | Inverter | inverter028_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 277 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Real Power Curtailment Flag | Inverter | inverter028_curtailed | Real Power Curtailment Flag | 278 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Following Setpoint | Inverter | inverter028_follwing | Following Setpoint | 279 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_AutoStart On | Inverter | inverter029_MODBUS.HR0501_restartEn | AutoStart On | 280 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Comm Fail | Inverter | inverter029_commsFail | Comm Fail | 281 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Faulted | Inverter | inverter029_fault | Faulted | 282 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Locked Out | Inverter | inverter029_lockout | Locked Out | 283 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Master Control Enabled | Inverter | inverter029_masterControl | Master Control Enabled | 284 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Offline | Inverter | inverter029_offline | Offline | 285 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Ramp Up Enabled | Inverter | inverter029_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 286 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Ramp Down Enabled | Inverter | inverter029_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 287 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Real Power Curtailment Flag | Inverter | inverter029_curtailed | Real Power Curtailment Flag | 288 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Following Setpoint | Inverter | inverter029_follwing | Following Setpoint | 289 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_AutoStart On | Inverter | inverter030_MODBUS.HR0501_restartEn | AutoStart On | 290 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Comm Fail | Inverter | inverter030_commsFail | Comm Fail | 291 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Faulted | Inverter | inverter030_fault | Faulted | 292 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Locked Out | Inverter | inverter030_lockout | Locked Out | 293 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Master Control Enabled | Inverter | inverter030_masterControl | Master Control Enabled | 294 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Offline | Inverter | inverter030_offline | Offline | 295 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Ramp Up Enabled | Inverter | inverter030_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 296 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Ramp Down Enabled | Inverter | inverter030_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 297 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Real Power Curtailment Flag | Inverter | inverter030_curtailed | Real Power Curtailment Flag | 298 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Following Setpoint | Inverter | inverter030_follwing | Following Setpoint | 299 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_AutoStart On | Inverter | inverter031_MODBUS.HR0501_restartEn | AutoStart On | 300 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Comm Fail | Inverter | inverter031_commsFail | Comm Fail | 301 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Faulted | Inverter | inverter031_fault | Faulted | 302 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Locked Out | Inverter | inverter031_lockout | Locked Out | 303 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Master Control Enabled | Inverter | inverter031_masterControl | Master Control Enabled | 304 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Offline | Inverter | inverter031_offline | Offline | 305 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Ramp Up Enabled | Inverter | inverter031_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 306 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Ramp Down Enabled | Inverter | inverter031_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 307 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Real Power Curtailment Flag | Inverter | inverter031_curtailed | Real Power Curtailment Flag | 308 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Following Setpoint | Inverter | inverter031_follwing | Following Setpoint | 309 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_AutoStart On | Inverter | inverter032_MODBUS.HR0501_restartEn | AutoStart On | 310 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Comm Fail | Inverter | inverter032_commsFail | Comm Fail | 311 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Faulted | Inverter | inverter032_fault | Faulted | 312 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Locked Out | Inverter | inverter032_lockout | Locked Out | 313 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Master Control Enabled | Inverter | inverter032_masterControl | Master Control Enabled | 314 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Offline | Inverter | inverter032_offline | Offline | 315 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Ramp Up Enabled | Inverter | inverter032_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 316 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Ramp Down Enabled | Inverter | inverter032_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 317 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Real Power Curtailment Flag | Inverter | inverter032_curtailed | Real Power Curtailment Flag | 318 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Following Setpoint | Inverter | inverter032_follwing | Following Setpoint | 319 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_AutoStart On | Inverter | inverter033_MODBUS.HR0501_restartEn | AutoStart On | 320 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Comm Fail | Inverter | inverter033_commsFail | Comm Fail | 321 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Faulted | Inverter | inverter033_fault | Faulted | 322 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Locked Out | Inverter | inverter033_lockout | Locked Out | 323 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Master Control Enabled | Inverter | inverter033_masterControl | Master Control Enabled | 324 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Offline | Inverter | inverter033_offline | Offline | 325 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Ramp Up Enabled | Inverter | inverter033_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 326 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Ramp Down Enabled | Inverter | inverter033_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 327 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Real Power Curtailment Flag | Inverter | inverter033_curtailed | Real Power Curtailment Flag | 328 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Following Setpoint | Inverter | inverter033_follwing | Following Setpoint | 329 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_AutoStart On | Inverter | inverter034_MODBUS.HR0501_restartEn | AutoStart On | 330 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Comm Fail | Inverter | inverter034_commsFail | Comm Fail | 331 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Faulted | Inverter | inverter034_fault | Faulted | 332 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Locked Out | Inverter | inverter034_lockout | Locked Out | 333 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Master Control Enabled | Inverter | inverter034_masterControl | Master Control Enabled | 334 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Offline | Inverter | inverter034_offline | Offline | 335 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Ramp Up Enabled | Inverter | inverter034_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 336 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Ramp Down Enabled | Inverter | inverter034_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 337 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Real Power Curtailment Flag | Inverter | inverter034_curtailed | Real Power Curtailment Flag | 338 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Following Setpoint | Inverter | inverter034_follwing | Following Setpoint | 339 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_AutoStart On | Inverter | inverter035_MODBUS.HR0501_restartEn | AutoStart On | 340 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Comm Fail | Inverter | inverter035_commsFail | Comm Fail | 341 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Faulted | Inverter | inverter035_fault | Faulted | 342 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Locked Out | Inverter | inverter035_lockout | Locked Out | 343 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Master Control Enabled | Inverter | inverter035_masterControl | Master Control Enabled | 344 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Offline | Inverter | inverter035_offline | Offline | 345 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Ramp Up Enabled | Inverter | inverter035_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 346 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Ramp Down Enabled | Inverter | inverter035_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 347 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Real Power Curtailment Flag | Inverter | inverter035_curtailed | Real Power Curtailment Flag | 348 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Following Setpoint | Inverter | inverter035_follwing | Following Setpoint | 349 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_AutoStart On | Inverter | inverter036_MODBUS.HR0501_restartEn | AutoStart On | 350 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Comm Fail | Inverter | inverter036_commsFail | Comm Fail | 351 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Faulted | Inverter | inverter036_fault | Faulted | 352 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Locked Out | Inverter | inverter036_lockout | Locked Out | 353 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Master Control Enabled | Inverter | inverter036_masterControl | Master Control Enabled | 354 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Offline | Inverter | inverter036_offline | Offline | 355 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Ramp Up Enabled | Inverter | inverter036_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 356 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Ramp Down Enabled | Inverter | inverter036_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 357 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Real Power Curtailment Flag | Inverter | inverter036_curtailed | Real Power Curtailment Flag | 358 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Following Setpoint | Inverter | inverter036_follwing | Following Setpoint | 359 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_AutoStart On | Inverter | inverter037_MODBUS.HR0501_restartEn | AutoStart On | 360 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Comm Fail | Inverter | inverter037_commsFail | Comm Fail | 361 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Faulted | Inverter | inverter037_fault | Faulted | 362 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Locked Out | Inverter | inverter037_lockout | Locked Out | 363 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Master Control Enabled | Inverter | inverter037_masterControl | Master Control Enabled | 364 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Offline | Inverter | inverter037_offline | Offline | 365 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Ramp Up Enabled | Inverter | inverter037_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 366 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Ramp Down Enabled | Inverter | inverter037_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 367 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Real Power Curtailment Flag | Inverter | inverter037_curtailed | Real Power Curtailment Flag | 368 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Following Setpoint | Inverter | inverter037_follwing | Following Setpoint | 369 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_AutoStart On | Inverter | inverter038_MODBUS.HR0501_restartEn | AutoStart On | 370 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Comm Fail | Inverter | inverter038_commsFail | Comm Fail | 371 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Faulted | Inverter | inverter038_fault | Faulted | 372 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Locked Out | Inverter | inverter038_lockout | Locked Out | 373 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Master Control Enabled | Inverter | inverter038_masterControl | Master Control Enabled | 374 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Offline | Inverter | inverter038_offline | Offline | 375 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Ramp Up Enabled | Inverter | inverter038_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 376 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Ramp Down Enabled | Inverter | inverter038_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 377 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Real Power Curtailment Flag | Inverter | inverter038_curtailed | Real Power Curtailment Flag | 378 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Following Setpoint | Inverter | inverter038_follwing | Following Setpoint | 379 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_AutoStart On | Inverter | inverter039_MODBUS.HR0501_restartEn | AutoStart On | 380 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Comm Fail | Inverter | inverter039_commsFail | Comm Fail | 381 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Faulted | Inverter | inverter039_fault | Faulted | 382 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Locked Out | Inverter | inverter039_lockout | Locked Out | 383 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Master Control Enabled | Inverter | inverter039_masterControl | Master Control Enabled | 384 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Offline | Inverter | inverter039_offline | Offline | 385 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Ramp Up Enabled | Inverter | inverter039_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 386 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Ramp Down Enabled | Inverter | inverter039_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 387 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Real Power Curtailment Flag | Inverter | inverter039_curtailed | Real Power Curtailment Flag | 388 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Following Setpoint | Inverter | inverter039_follwing | Following Setpoint | 389 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_AutoStart On | Inverter | inverter040_MODBUS.HR0501_restartEn | AutoStart On | 390 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Comm Fail | Inverter | inverter040_commsFail | Comm Fail | 391 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Faulted | Inverter | inverter040_fault | Faulted | 392 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Locked Out | Inverter | inverter040_lockout | Locked Out | 393 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Master Control Enabled | Inverter | inverter040_masterControl | Master Control Enabled | 394 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Offline | Inverter | inverter040_offline | Offline | 395 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Ramp Up Enabled | Inverter | inverter040_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 396 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Ramp Down Enabled | Inverter | inverter040_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 397 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Real Power Curtailment Flag | Inverter | inverter040_curtailed | Real Power Curtailment Flag | 398 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Following Setpoint | Inverter | inverter040_follwing | Following Setpoint | 399 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_AutoStart On | Inverter | inverter041_MODBUS.HR0501_restartEn | AutoStart On | 400 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Comm Fail | Inverter | inverter041_commsFail | Comm Fail | 401 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Faulted | Inverter | inverter041_fault | Faulted | 402 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Locked Out | Inverter | inverter041_lockout | Locked Out | 403 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Master Control Enabled | Inverter | inverter041_masterControl | Master Control Enabled | 404 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Offline | Inverter | inverter041_offline | Offline | 405 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Ramp Up Enabled | Inverter | inverter041_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 406 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Ramp Down Enabled | Inverter | inverter041_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 407 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Real Power Curtailment Flag | Inverter | inverter041_curtailed | Real Power Curtailment Flag | 408 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Following Setpoint | Inverter | inverter041_follwing | Following Setpoint | 409 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_AutoStart On | Inverter | inverter042_MODBUS.HR0501_restartEn | AutoStart On | 410 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Comm Fail | Inverter | inverter042_commsFail | Comm Fail | 411 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Faulted | Inverter | inverter042_fault | Faulted | 412 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Locked Out | Inverter | inverter042_lockout | Locked Out | 413 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Master Control Enabled | Inverter | inverter042_masterControl | Master Control Enabled | 414 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Offline | Inverter | inverter042_offline | Offline | 415 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Ramp Up Enabled | Inverter | inverter042_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 416 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Ramp Down Enabled | Inverter | inverter042_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 417 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Real Power Curtailment Flag | Inverter | inverter042_curtailed | Real Power Curtailment Flag | 418 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Following Setpoint | Inverter | inverter042_follwing | Following Setpoint | 419 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_AutoStart On | Inverter | inverter043_MODBUS.HR0501_restartEn | AutoStart On | 420 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Comm Fail | Inverter | inverter043_commsFail | Comm Fail | 421 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Faulted | Inverter | inverter043_fault | Faulted | 422 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Locked Out | Inverter | inverter043_lockout | Locked Out | 423 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Master Control Enabled | Inverter | inverter043_masterControl | Master Control Enabled | 424 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Offline | Inverter | inverter043_offline | Offline | 425 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Ramp Up Enabled | Inverter | inverter043_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 426 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Ramp Down Enabled | Inverter | inverter043_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 427 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Real Power Curtailment Flag | Inverter | inverter043_curtailed | Real Power Curtailment Flag | 428 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Following Setpoint | Inverter | inverter043_follwing | Following Setpoint | 429 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_AutoStart On | Inverter | inverter044_MODBUS.HR0501_restartEn | AutoStart On | 430 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Comm Fail | Inverter | inverter044_commsFail | Comm Fail | 431 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Faulted | Inverter | inverter044_fault | Faulted | 432 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Locked Out | Inverter | inverter044_lockout | Locked Out | 433 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Master Control Enabled | Inverter | inverter044_masterControl | Master Control Enabled | 434 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Offline | Inverter | inverter044_offline | Offline | 435 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Ramp Up Enabled | Inverter | inverter044_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 436 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Ramp Down Enabled | Inverter | inverter044_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 437 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Real Power Curtailment Flag | Inverter | inverter044_curtailed | Real Power Curtailment Flag | 438 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Following Setpoint | Inverter | inverter044_follwing | Following Setpoint | 439 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_AutoStart On | Inverter | inverter045_MODBUS.HR0501_restartEn | AutoStart On | 440 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Comm Fail | Inverter | inverter045_commsFail | Comm Fail | 441 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Faulted | Inverter | inverter045_fault | Faulted | 442 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Locked Out | Inverter | inverter045_lockout | Locked Out | 443 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Master Control Enabled | Inverter | inverter045_masterControl | Master Control Enabled | 444 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Offline | Inverter | inverter045_offline | Offline | 445 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Ramp Up Enabled | Inverter | inverter045_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 446 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Ramp Down Enabled | Inverter | inverter045_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 447 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Real Power Curtailment Flag | Inverter | inverter045_curtailed | Real Power Curtailment Flag | 448 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Following Setpoint | Inverter | inverter045_follwing | Following Setpoint | 449 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_AutoStart On | Inverter | inverter046_MODBUS.HR0501_restartEn | AutoStart On | 450 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Comm Fail | Inverter | inverter046_commsFail | Comm Fail | 451 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Faulted | Inverter | inverter046_fault | Faulted | 452 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Locked Out | Inverter | inverter046_lockout | Locked Out | 453 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Master Control Enabled | Inverter | inverter046_masterControl | Master Control Enabled | 454 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Offline | Inverter | inverter046_offline | Offline | 455 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Ramp Up Enabled | Inverter | inverter046_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 456 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Ramp Down Enabled | Inverter | inverter046_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 457 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Real Power Curtailment Flag | Inverter | inverter046_curtailed | Real Power Curtailment Flag | 458 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Following Setpoint | Inverter | inverter046_follwing | Following Setpoint | 459 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_AutoStart On | Inverter | inverter047_MODBUS.HR0501_restartEn | AutoStart On | 460 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Comm Fail | Inverter | inverter047_commsFail | Comm Fail | 461 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_DC Monitor Offline | Inverter |  | DC Monitor Offline |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Faulted | Inverter | inverter047_fault | Faulted | 462 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Locked Out | Inverter | inverter047_lockout | Locked Out | 463 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Master Control Enabled | Inverter | inverter047_masterControl | Master Control Enabled | 464 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Offline | Inverter | inverter047_offline | Offline | 465 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Ramp Up Enabled | Inverter | inverter047_MODBUS.HR0281_riseGradient_pEn | Ramp Up Enabled | 466 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Ramp Down Enabled | Inverter | inverter047_MODBUS.HR0285_dropGradient_pEn | Ramp Down Enabled | 467 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Real Power Curtailment Flag | Inverter | inverter047_curtailed | Real Power Curtailment Flag | 468 | 0=False, 1=TRUE | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Surge MOV Failed | Inverter |  | Surge MOV Failed |  | 0=False, 1=TRUE | Requested-Not Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Following Setpoint | Inverter | inverter047_follwing | Following Setpoint | 469 | 0=False, 1=TRUE | Requested-Available
Counters
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | ROLLOVER VALUE
Analog Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability
Digital Outputs | Applicable to GMS Connection ports only
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | 0/1 State | Availability
SUB1 | INV001 | Daggett 3_SUB1_INV001_Start | Inverter | Inverter001_start | Start | 0 | LatchOff/LatchOn | Requested-Available
SUB1 | INV001 | Daggett 3_SUB1_INV001_Stop | Inverter | Inverter001_stop | Stop | 1 | LatchOff/LatchOn | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Start | Inverter | Inverter002_start | Start | 2 | LatchOff/LatchOn | Requested-Available
SUB1 | INV002 | Daggett 3_SUB1_INV002_Stop | Inverter | Inverter002_stop | Stop | 3 | LatchOff/LatchOn | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Start | Inverter | Inverter003_start | Start | 4 | LatchOff/LatchOn | Requested-Available
SUB1 | INV003 | Daggett 3_SUB1_INV003_Stop | Inverter | Inverter003_stop | Stop | 5 | LatchOff/LatchOn | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Start | Inverter | Inverter004_start | Start | 6 | LatchOff/LatchOn | Requested-Available
SUB1 | INV004 | Daggett 3_SUB1_INV004_Stop | Inverter | Inverter004_stop | Stop | 7 | LatchOff/LatchOn | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Start | Inverter | Inverter005_start | Start | 8 | LatchOff/LatchOn | Requested-Available
SUB1 | INV005 | Daggett 3_SUB1_INV005_Stop | Inverter | Inverter005_stop | Stop | 9 | LatchOff/LatchOn | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Start | Inverter | Inverter006_start | Start | 10 | LatchOff/LatchOn | Requested-Available
SUB1 | INV006 | Daggett 3_SUB1_INV006_Stop | Inverter | Inverter006_stop | Stop | 11 | LatchOff/LatchOn | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Start | Inverter | Inverter007_start | Start | 12 | LatchOff/LatchOn | Requested-Available
SUB1 | INV007 | Daggett 3_SUB1_INV007_Stop | Inverter | Inverter007_stop | Stop | 13 | LatchOff/LatchOn | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Start | Inverter | Inverter008_start | Start | 14 | LatchOff/LatchOn | Requested-Available
SUB1 | INV008 | Daggett 3_SUB1_INV008_Stop | Inverter | Inverter008_stop | Stop | 15 | LatchOff/LatchOn | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Start | Inverter | Inverter009_start | Start | 16 | LatchOff/LatchOn | Requested-Available
SUB1 | INV009 | Daggett 3_SUB1_INV009_Stop | Inverter | Inverter009_stop | Stop | 17 | LatchOff/LatchOn | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Start | Inverter | Inverter010_start | Start | 18 | LatchOff/LatchOn | Requested-Available
SUB1 | INV010 | Daggett 3_SUB1_INV010_Stop | Inverter | Inverter010_stop | Stop | 19 | LatchOff/LatchOn | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Start | Inverter | inverter011_start | Start | 20 | LatchOff/LatchOn | Requested-Available
SUB1 | INV011 | Daggett 3_SUB1_INV011_Stop | Inverter | inverter011_stop | Stop | 21 | LatchOff/LatchOn | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Start | Inverter | inverter012_start | Start | 22 | LatchOff/LatchOn | Requested-Available
SUB1 | INV012 | Daggett 3_SUB1_INV012_Stop | Inverter | inverter012_stop | Stop | 23 | LatchOff/LatchOn | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Start | Inverter | inverter013_start | Start | 24 | LatchOff/LatchOn | Requested-Available
SUB1 | INV013 | Daggett 3_SUB1_INV013_Stop | Inverter | inverter013_stop | Stop | 25 | LatchOff/LatchOn | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Start | Inverter | inverter014_start | Start | 26 | LatchOff/LatchOn | Requested-Available
SUB1 | INV014 | Daggett 3_SUB1_INV014_Stop | Inverter | inverter014_stop | Stop | 27 | LatchOff/LatchOn | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Start | Inverter | inverter015_start | Start | 28 | LatchOff/LatchOn | Requested-Available
SUB1 | INV015 | Daggett 3_SUB1_INV015_Stop | Inverter | inverter015_stop | Stop | 29 | LatchOff/LatchOn | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Start | Inverter | inverter016_start | Start | 30 | LatchOff/LatchOn | Requested-Available
SUB1 | INV016 | Daggett 3_SUB1_INV016_Stop | Inverter | inverter016_stop | Stop | 31 | LatchOff/LatchOn | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Start | Inverter | inverter017_start | Start | 32 | LatchOff/LatchOn | Requested-Available
SUB1 | INV017 | Daggett 3_SUB1_INV017_Stop | Inverter | inverter017_stop | Stop | 33 | LatchOff/LatchOn | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Start | Inverter | inverter018_start | Start | 34 | LatchOff/LatchOn | Requested-Available
SUB1 | INV018 | Daggett 3_SUB1_INV018_Stop | Inverter | inverter018_stop | Stop | 35 | LatchOff/LatchOn | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Start | Inverter | inverter019_start | Start | 36 | LatchOff/LatchOn | Requested-Available
SUB1 | INV019 | Daggett 3_SUB1_INV019_Stop | Inverter | inverter019_stop | Stop | 37 | LatchOff/LatchOn | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Start | Inverter | inverter020_start | Start | 38 | LatchOff/LatchOn | Requested-Available
SUB1 | INV020 | Daggett 3_SUB1_INV020_Stop | Inverter | inverter020_stop | Stop | 39 | LatchOff/LatchOn | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Start | Inverter | inverter021_start | Start | 40 | LatchOff/LatchOn | Requested-Available
SUB1 | INV021 | Daggett 3_SUB1_INV021_Stop | Inverter | inverter021_stop | Stop | 41 | LatchOff/LatchOn | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Start | Inverter | inverter022_start | Start | 42 | LatchOff/LatchOn | Requested-Available
SUB1 | INV022 | Daggett 3_SUB1_INV022_Stop | Inverter | inverter022_stop | Stop | 43 | LatchOff/LatchOn | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Start | Inverter | inverter023_start | Start | 44 | LatchOff/LatchOn | Requested-Available
SUB1 | INV023 | Daggett 3_SUB1_INV023_Stop | Inverter | inverter023_stop | Stop | 45 | LatchOff/LatchOn | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Start | Inverter | inverter024_start | Start | 46 | LatchOff/LatchOn | Requested-Available
SUB1 | INV024 | Daggett 3_SUB1_INV024_Stop | Inverter | inverter024_stop | Stop | 47 | LatchOff/LatchOn | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Start | Inverter | inverter025_start | Start | 48 | LatchOff/LatchOn | Requested-Available
SUB1 | INV025 | Daggett 3_SUB1_INV025_Stop | Inverter | inverter025_stop | Stop | 49 | LatchOff/LatchOn | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Start | Inverter | inverter026_start | Start | 50 | LatchOff/LatchOn | Requested-Available
SUB1 | INV026 | Daggett 3_SUB1_INV026_Stop | Inverter | inverter026_stop | Stop | 51 | LatchOff/LatchOn | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Start | Inverter | inverter027_start | Start | 52 | LatchOff/LatchOn | Requested-Available
SUB1 | INV027 | Daggett 3_SUB1_INV027_Stop | Inverter | inverter027_stop | Stop | 53 | LatchOff/LatchOn | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Start | Inverter | inverter028_start | Start | 54 | LatchOff/LatchOn | Requested-Available
SUB1 | INV028 | Daggett 3_SUB1_INV028_Stop | Inverter | inverter028_stop | Stop | 55 | LatchOff/LatchOn | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Start | Inverter | inverter029_start | Start | 56 | LatchOff/LatchOn | Requested-Available
SUB1 | INV029 | Daggett 3_SUB1_INV029_Stop | Inverter | inverter029_stop | Stop | 57 | LatchOff/LatchOn | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Start | Inverter | inverter030_start | Start | 58 | LatchOff/LatchOn | Requested-Available
SUB1 | INV030 | Daggett 3_SUB1_INV030_Stop | Inverter | inverter030_stop | Stop | 59 | LatchOff/LatchOn | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Start | Inverter | inverter031_start | Start | 60 | LatchOff/LatchOn | Requested-Available
SUB1 | INV031 | Daggett 3_SUB1_INV031_Stop | Inverter | inverter031_stop | Stop | 61 | LatchOff/LatchOn | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Start | Inverter | inverter032_start | Start | 62 | LatchOff/LatchOn | Requested-Available
SUB1 | INV032 | Daggett 3_SUB1_INV032_Stop | Inverter | inverter032_stop | Stop | 63 | LatchOff/LatchOn | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Start | Inverter | inverter033_start | Start | 64 | LatchOff/LatchOn | Requested-Available
SUB1 | INV033 | Daggett 3_SUB1_INV033_Stop | Inverter | inverter033_stop | Stop | 65 | LatchOff/LatchOn | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Start | Inverter | inverter034_start | Start | 66 | LatchOff/LatchOn | Requested-Available
SUB1 | INV034 | Daggett 3_SUB1_INV034_Stop | Inverter | inverter034_stop | Stop | 67 | LatchOff/LatchOn | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Start | Inverter | inverter035_start | Start | 68 | LatchOff/LatchOn | Requested-Available
SUB1 | INV035 | Daggett 3_SUB1_INV035_Stop | Inverter | inverter035_stop | Stop | 69 | LatchOff/LatchOn | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Start | Inverter | inverter036_start | Start | 70 | LatchOff/LatchOn | Requested-Available
SUB1 | INV036 | Daggett 3_SUB1_INV036_Stop | Inverter | inverter036_stop | Stop | 71 | LatchOff/LatchOn | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Start | Inverter | inverter037_start | Start | 72 | LatchOff/LatchOn | Requested-Available
SUB1 | INV037 | Daggett 3_SUB1_INV037_Stop | Inverter | inverter037_stop | Stop | 73 | LatchOff/LatchOn | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Start | Inverter | inverter038_start | Start | 74 | LatchOff/LatchOn | Requested-Available
SUB1 | INV038 | Daggett 3_SUB1_INV038_Stop | Inverter | inverter038_stop | Stop | 75 | LatchOff/LatchOn | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Start | Inverter | inverter039_start | Start | 76 | LatchOff/LatchOn | Requested-Available
SUB1 | INV039 | Daggett 3_SUB1_INV039_Stop | Inverter | inverter039_stop | Stop | 77 | LatchOff/LatchOn | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Start | Inverter | inverter040_start | Start | 78 | LatchOff/LatchOn | Requested-Available
SUB1 | INV040 | Daggett 3_SUB1_INV040_Stop | Inverter | inverter040_stop | Stop | 79 | LatchOff/LatchOn | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Start | Inverter | inverter041_start | Start | 80 | LatchOff/LatchOn | Requested-Available
SUB1 | INV041 | Daggett 3_SUB1_INV041_Stop | Inverter | inverter041_stop | Stop | 81 | LatchOff/LatchOn | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Start | Inverter | inverter042_start | Start | 82 | LatchOff/LatchOn | Requested-Available
SUB1 | INV042 | Daggett 3_SUB1_INV042_Stop | Inverter | inverter042_stop | Stop | 83 | LatchOff/LatchOn | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Start | Inverter | inverter043_start | Start | 84 | LatchOff/LatchOn | Requested-Available
SUB1 | INV043 | Daggett 3_SUB1_INV043_Stop | Inverter | inverter043_stop | Stop | 85 | LatchOff/LatchOn | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Start | Inverter | inverter044_start | Start | 86 | LatchOff/LatchOn | Requested-Available
SUB1 | INV044 | Daggett 3_SUB1_INV044_Stop | Inverter | inverter044_stop | Stop | 87 | LatchOff/LatchOn | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Start | Inverter | inverter045_start | Start | 88 | LatchOff/LatchOn | Requested-Available
SUB1 | INV045 | Daggett 3_SUB1_INV045_Stop | Inverter | inverter045_stop | Stop | 89 | LatchOff/LatchOn | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Start | Inverter | inverter046_start | Start | 90 | LatchOff/LatchOn | Requested-Available
SUB1 | INV046 | Daggett 3_SUB1_INV046_Stop | Inverter | inverter046_stop | Stop | 91 | LatchOff/LatchOn | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Start | Inverter | inverter047_start | Start | 92 | LatchOff/LatchOn | Requested-Available
SUB1 | INV047 | Daggett 3_SUB1_INV047_Stop | Inverter | inverter047_stop | Stop | 93 | LatchOff/LatchOn | Requested-Available

## DNP3.0 Server#3 (INV48-95)
PI DNP Connection Details: |  |  | GMS DNP Connection Details:
DNP Server | 10.75.32.2 |  | DNP Server | 10.75.32.2
DNP Server Port# | 20003 |  | DNP Server Port# | 20014 (PROD); 20015 (QAS)
PI DNP Client 1 address | 10 |  | DNP Client 1 address | 10
RTAC DNP Server address | 2 |  | RTAC DNP Server address | 1
| Data Type | DNP Event Class | Event Obj/Var | Static Obj/Var | Control Obj/Var
Analogs Inputs | Single Precision Floating Point | 2 | 32/5 | 30/5
Digitals | Status with Flags | 1 | 2/2 | 1/2
Accumulators | 32-Bit with Flag | 0 | 22/5 | 20/1
Binary Outputs | Status With Flags | 0 |  |  | 10/2
Analogs Outputs | 16 bit with Flag | 0 |  |  | 41/2
Availability
Requested-Available | Point requested per Attachment 3 and available. Point Name follows defined naming convention.
Requested-Not Available | Point requested per Attachment 3 but not available. Clearyway will review each of these points to determine if not having them is acceptable
Requested-Not Applicable | Point requested per Attachment 3 but not applicable, i.e. no wind turbines at a solar site
Not Requested-Available | Point is not requested but is available. Contractor will fill in a Point Name following naming convention standards. Owner will review and approve the PI Point Name.
Analog Inputs | Event Deadband of 0.01 for all points except 0.001 for Frequency and Power Factor
Substation | DeviceID | Point Name | Device Type | Native RTAC Point Name | Description | DNP Index | Units | Availability | EGU MIN | EGU MAX | INTERNAL SCALING
SUB1 | INV048 | Daggett 3_SUB1_INV048_A Phase Current | Inverter | inverter048_MODBUS.HR1004_i1_A | A Phase Current | 0 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_B Phase Current | Inverter | inverter048_MODBUS.HR1005_i2_A | B Phase Current | 1 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_C Phase Current | Inverter | inverter048_MODBUS.HR1006_i3_A | C Phase Current | 2 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Bus Voltage | Inverter | inverter048_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV048 | Daggett 3_SUB1_INV048_Apparent Power | Inverter | inverter048_MODBUS.HR1010_s3_VA | Apparent Power | 4 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 1 | Inverter | Inverter048_MODBUS.HR5805_du1_idc_A | Current DC Input# | 5 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC Input 1 | Inverter | Inverter048_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 6 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 2 | Inverter | Inverter048_MODBUS.HR5811_du2_idc_A | Current DC Input# | 7 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 2 | Inverter | Inverter048_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 8 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 3 | Inverter | Inverter048_MODBUS.HR5817_du3_idc_A | Current DC Input# | 9 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 3 | Inverter | Inverter048_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 10 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 4 | Inverter | Inverter048_MODBUS.HR5823_du4_idc_A | Current DC Input# | 11 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 4 | Inverter | Inverter048_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 12 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 5 | Inverter | Inverter048_MODBUS.HR5829_du5_idc_A | Current DC Input# | 13 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 5 | Inverter | Inverter048_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 14 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 6 | Inverter | Inverter048_MODBUS.HR5835_du6_idc_A | Current DC Input# | 15 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 6 | Inverter | Inverter048_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 16 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 7 | Inverter | Inverter048_MODBUS.HR5841_du7_idc_A | Current DC Input# | 17 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 7 | Inverter | Inverter048_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 18 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 8 | Inverter | Inverter048_MODBUS.HR5847_du8_idc_A | Current DC Input# | 19 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 8 | Inverter | Inverter048_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 20 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 9 | Inverter | Inverter048_MODBUS.HR5853_du9_idc_A | Current DC Input# | 21 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 9 | Inverter | Inverter048_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 22 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 10 | Inverter | Inverter048_MODBUS.HR5859_du10_idc_A | Current DC Input# | 23 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 10 | Inverter | Inverter048_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 24 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 11 | Inverter | Inverter048_MODBUS.HR5865_du11_idc_A | Current DC Input# | 25 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 11 | Inverter | Inverter048_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 26 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 12 | Inverter | Inverter048_MODBUS.HR5871_du12_idc_A | Current DC Input# | 27 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 12 | Inverter | Inverter048_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 28 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 13 | Inverter | Inverter048_MODBUS.HR5877_du13_idc_A | Current DC Input# | 29 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 13 | Inverter | Inverter048_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 30 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 14 | Inverter | Inverter048_MODBUS.HR5883_du14_idc_A | Current DC Input# | 31 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 14 | Inverter | Inverter048_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 32 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 15 | Inverter | Inverter048_MODBUS.HR5889_du15_idc_A | Current DC Input# | 33 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 15 | Inverter | Inverter048_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 34 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 16 | Inverter | Inverter048_MODBUS.HR5895_du16_idc_A | Current DC Input# | 35 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 16 | Inverter | Inverter048_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 36 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 17 | Inverter | Inverter048_MODBUS.HR5901_du17_idc_A | Current DC Input# | 37 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 17 | Inverter | Inverter048_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 38 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 18 | Inverter | Inverter048_MODBUS.HR5907_du18_idc_A | Current DC Input# | 39 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 18 | Inverter | Inverter048_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 40 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 19 | Inverter | Inverter048_MODBUS.HR5913_du19_idc_A | Current DC Input# | 41 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 19 | Inverter | Inverter048_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 42 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current DC Input 20 | Inverter | Inverter048_MODBUS.HR5919_du20_idc_A | Current DC Input# | 43 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC input 20 | Inverter | Inverter048_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 44 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current-AC | Inverter | inverter048_MODBUS.HR1007_i3Avg_A | Current-AC | 45 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Current-DC | Inverter | inverter048_MODBUS.HR1062_idcInput_A | Current-DC | 46 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Daily Energy Delivered | Inverter | inverter048_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 47 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power Set Point | Inverter | inverter048_MODBUS.HR0553_pRef | Real Power Set Point | 48 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Reactive Power Set Point | Inverter | inverter048_MODBUS.HR0558_qRef | Reactive Power Set Point | 49 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Frequency | Inverter | inverter048_MODBUS.HR1012_f3_Hz | Frequency | 50 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV048 | Daggett 3_SUB1_INV048_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Insulation Resistance | Inverter | inverter048_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 51 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Number of DU Channels | Inverter | inverter048_MODBUS.HR0653_duChannels | Number of DU Channels | 52 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Number of Running Modules | Inverter | inverter048_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 53 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Operating State | Inverter | inverter048_MODBUS.HR1123_currentStatus | Operating State | 54 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Power Factor | Inverter | inverter048_MODBUS.HR1011_pf3 | Power Factor | 55 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV048 | Daggett 3_SUB1_INV048_Ramp Down | Inverter | inverter048_MODBUS.HR0286_dropGradient_p | Ramp Down | 56 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Ramp Up | Inverter | inverter048_MODBUS.HR0282_riseGradient_p | Ramp Up | 57 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power Delivered | Inverter | inverter048_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 58 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Reactive Power Delivered | Inverter | inverter048_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 59 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power | 60 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Reactive Power | Inverter | inverter048_MODBUS.HR1009_q3_kvar | Reactive Power | 61 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Reactive Power Mode | Inverter | inverter048_MODBUS.HR0552_qControlMode | Reactive Power Mode | 62 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Reactive Power Set Point Percent | Inverter | inverter048_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 63 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power AC Percent | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power AC Percent | 64 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power-AC | Inverter | inverter048_MODBUS.HR1008_p3_kW | Real Power-AC | 65 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Real Power-DC | Inverter | inverter048_MODBUS.HR1061_pdcInput_W | Real Power-DC | 66 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Air Intake | Inverter | inverter048_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 67 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Cabinet | Inverter | inverter048_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 68 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-IGBT | Inverter | inverter048_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 69 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Temperature-Module | Inverter | inverter048_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 70 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage A-B | Inverter | inverter048_MODBUS.HR1008_vRS_V | Voltage A-B | 71 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage B-C | Inverter | inverter048_MODBUS.HR1002_vST_V | Voltage B-C | 72 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage C-A | Inverter | inverter048_MODBUS.HR1003_vTR_V | Voltage C-A | 73 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV048 | Daggett 3_SUB1_INV048_Voltage DC | Inverter | inverter048_MODBUS.HR1051_vdcBus_V | Voltage DC | 74 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV048 | Daggett 3_SUB1_INV048_Fault Code 1 | Inverter | Inverter048_MODBUS.HRxxxx_currentFault | Fault Code 1 | 75 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Warning | Inverter | Inverter048_MODBUS.HRxxxx_currentWarning | Warning | 76 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Internal Input Status | Inverter | Inverter048_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 77 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Internal Output Status | Inverter | Inverter048_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 78 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Module Fault Code | Inverter | Inverter048_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 79 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Internal Humidity | Inverter | Inverter048_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 80 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Humidity | Inverter | Inverter048_MODBUS.HRxxxx_humidity | Humidity | 81 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_Comms Fault Time | Inverter | Inverter048_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 82 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Status | Inverter | Inverter048_MODBUS.HRxxxx_M1_status | Module Status | 83 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 IR | Inverter | Inverter048_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 84 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 IS | Inverter | Inverter048_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 85 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 IT | Inverter | Inverter048_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 86 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 87 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 88 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 89 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 90 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 P | Inverter | Inverter048_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 91 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Q | Inverter | Inverter048_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 92 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 93 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 94 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 95 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 96 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M1 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 97 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Status | Inverter | Inverter048_MODBUS.HRxxxx_M2_status | Module Status | 98 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 IR | Inverter | Inverter048_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 99 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 IS | Inverter | Inverter048_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 IT | Inverter | Inverter048_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 103 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 104 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 P | Inverter | Inverter048_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 106 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Q | Inverter | Inverter048_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 107 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 108 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 109 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 110 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 111 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M2 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Status | Inverter | Inverter048_MODBUS.HRxxxx_M3_status | Module Status | 113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 IR | Inverter | Inverter048_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 114 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 IS | Inverter | Inverter048_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 115 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 IT | Inverter | Inverter048_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 116 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 118 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 119 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 120 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 P | Inverter | Inverter048_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 121 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Q | Inverter | Inverter048_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 122 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 123 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 124 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 125 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 126 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M3 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 127 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Status | Inverter | Inverter048_MODBUS.HRxxxx_M4_status | Module Status | 128 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 IR | Inverter | Inverter048_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 129 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 IS | Inverter | Inverter048_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 130 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 IT | Inverter | Inverter048_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 132 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 133 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 134 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 135 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 P | Inverter | Inverter048_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 136 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Q | Inverter | Inverter048_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 137 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 138 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 139 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 140 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 141 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M4 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 142 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Status | Inverter | Inverter048_MODBUS.HRxxxx_M5_status | Module Status | 143 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 IR | Inverter | Inverter048_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 144 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 IS | Inverter | Inverter048_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 145 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 IT | Inverter | Inverter048_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 146 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 148 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 149 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 150 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 P | Inverter | Inverter048_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 151 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Q | Inverter | Inverter048_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 152 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 153 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 154 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 155 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 156 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M5 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 157 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Status | Inverter | Inverter048_MODBUS.HRxxxx_M6_status | Module Status | 158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 IR | Inverter | Inverter048_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 159 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 IS | Inverter | Inverter048_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 160 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 IT | Inverter | Inverter048_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 IDC | Inverter | Inverter048_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 VDCP | Inverter | Inverter048_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 163 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 VDCN | Inverter | Inverter048_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 164 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 VDC | Inverter | Inverter048_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 P | Inverter | Inverter048_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 166 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Q | Inverter | Inverter048_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 167 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Ambient Temp | Inverter | Inverter048_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 168 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Max IGBT Temp | Inverter | Inverter048_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 169 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 IO Status | Inverter | Inverter048_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 170 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Hardware Version | Inverter | Inverter048_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV048 | Daggett 3_SUB1_INV048_M6 Software Version | Inverter | Inverter048_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_A Phase Current | Inverter | inverter049_MODBUS.HR1004_i1_A | A Phase Current | 173 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_B Phase Current | Inverter | inverter049_MODBUS.HR1005_i2_A | B Phase Current | 174 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_C Phase Current | Inverter | inverter049_MODBUS.HR1006_i3_A | C Phase Current | 175 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Bus Voltage | Inverter | inverter049_MODBUS.HR1051_vdcBus_V | Bus Voltage | 176 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV049 | Daggett 3_SUB1_INV049_Apparent Power | Inverter | inverter049_MODBUS.HR1010_s3_VA | Apparent Power | 177 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 1 | Inverter | Inverter049_MODBUS.HR5805_du1_idc_A | Current DC Input# | 178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC Input 1 | Inverter | Inverter049_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 179 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 2 | Inverter | Inverter049_MODBUS.HR5811_du2_idc_A | Current DC Input# | 180 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 2 | Inverter | Inverter049_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 181 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 3 | Inverter | Inverter049_MODBUS.HR5817_du3_idc_A | Current DC Input# | 182 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 3 | Inverter | Inverter049_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 183 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 4 | Inverter | Inverter049_MODBUS.HR5823_du4_idc_A | Current DC Input# | 184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 4 | Inverter | Inverter049_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 185 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 5 | Inverter | Inverter049_MODBUS.HR5829_du5_idc_A | Current DC Input# | 186 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 5 | Inverter | Inverter049_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 187 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 6 | Inverter | Inverter049_MODBUS.HR5835_du6_idc_A | Current DC Input# | 188 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 6 | Inverter | Inverter049_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 189 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 7 | Inverter | Inverter049_MODBUS.HR5841_du7_idc_A | Current DC Input# | 190 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 7 | Inverter | Inverter049_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 191 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 8 | Inverter | Inverter049_MODBUS.HR5847_du8_idc_A | Current DC Input# | 192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 8 | Inverter | Inverter049_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 193 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 9 | Inverter | Inverter049_MODBUS.HR5853_du9_idc_A | Current DC Input# | 194 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 9 | Inverter | Inverter049_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 195 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 10 | Inverter | Inverter049_MODBUS.HR5859_du10_idc_A | Current DC Input# | 196 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 10 | Inverter | Inverter049_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 197 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 11 | Inverter | Inverter049_MODBUS.HR5865_du11_idc_A | Current DC Input# | 198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 11 | Inverter | Inverter049_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 199 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 12 | Inverter | Inverter049_MODBUS.HR5871_du12_idc_A | Current DC Input# | 200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 12 | Inverter | Inverter049_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 201 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 13 | Inverter | Inverter049_MODBUS.HR5877_du13_idc_A | Current DC Input# | 202 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 13 | Inverter | Inverter049_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 203 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 14 | Inverter | Inverter049_MODBUS.HR5883_du14_idc_A | Current DC Input# | 204 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 14 | Inverter | Inverter049_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 205 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 15 | Inverter | Inverter049_MODBUS.HR5889_du15_idc_A | Current DC Input# | 206 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 15 | Inverter | Inverter049_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 207 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 16 | Inverter | Inverter049_MODBUS.HR5895_du16_idc_A | Current DC Input# | 208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 16 | Inverter | Inverter049_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 209 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 17 | Inverter | Inverter049_MODBUS.HR5901_du17_idc_A | Current DC Input# | 210 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 17 | Inverter | Inverter049_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 211 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 18 | Inverter | Inverter049_MODBUS.HR5907_du18_idc_A | Current DC Input# | 212 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 18 | Inverter | Inverter049_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 213 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 19 | Inverter | Inverter049_MODBUS.HR5913_du19_idc_A | Current DC Input# | 214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 19 | Inverter | Inverter049_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 215 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current DC Input 20 | Inverter | Inverter049_MODBUS.HR5919_du20_idc_A | Current DC Input# | 216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC input 20 | Inverter | Inverter049_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 217 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current-AC | Inverter | inverter049_MODBUS.HR1007_i3Avg_A | Current-AC | 218 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Current-DC | Inverter | inverter049_MODBUS.HR1062_idcInput_A | Current-DC | 219 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Daily Energy Delivered | Inverter | inverter049_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 220 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power Set Point | Inverter | inverter049_MODBUS.HR0553_pRef | Real Power Set Point | 221 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Reactive Power Set Point | Inverter | inverter049_MODBUS.HR0558_qRef | Reactive Power Set Point | 222 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Frequency | Inverter | inverter049_MODBUS.HR1012_f3_Hz | Frequency | 223 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV049 | Daggett 3_SUB1_INV049_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Insulation Resistance | Inverter | inverter049_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 224 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Number of DU Channels | Inverter | inverter049_MODBUS.HR0653_duChannels | Number of DU Channels | 225 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Number of Running Modules | Inverter | inverter049_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 226 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Operating State | Inverter | inverter049_MODBUS.HR1123_currentStatus | Operating State | 227 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Power Factor | Inverter | inverter049_MODBUS.HR1011_pf3 | Power Factor | 228 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV049 | Daggett 3_SUB1_INV049_Ramp Down | Inverter | inverter049_MODBUS.HR0286_dropGradient_p | Ramp Down | 229 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Ramp Up | Inverter | inverter049_MODBUS.HR0282_riseGradient_p | Ramp Up | 230 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power Delivered | Inverter | inverter049_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 231 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Reactive Power Delivered | Inverter | inverter049_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 232 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power | 233 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Reactive Power | Inverter | inverter049_MODBUS.HR1009_q3_kvar | Reactive Power | 234 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Reactive Power Mode | Inverter | inverter049_MODBUS.HR0552_qControlMode | Reactive Power Mode | 235 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Reactive Power Set Point Percent | Inverter | inverter049_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 236 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power AC Percent | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power AC Percent | 237 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power-AC | Inverter | inverter049_MODBUS.HR1008_p3_kW | Real Power-AC | 238 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Real Power-DC | Inverter | inverter049_MODBUS.HR1061_pdcInput_W | Real Power-DC | 239 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Air Intake | Inverter | inverter049_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 240 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Cabinet | Inverter | inverter049_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 241 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-IGBT | Inverter | inverter049_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 242 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Temperature-Module | Inverter | inverter049_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 243 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage A-B | Inverter | inverter049_MODBUS.HR1009_vRS_V | Voltage A-B | 244 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage B-C | Inverter | inverter049_MODBUS.HR1002_vST_V | Voltage B-C | 245 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage C-A | Inverter | inverter049_MODBUS.HR1003_vTR_V | Voltage C-A | 246 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV049 | Daggett 3_SUB1_INV049_Voltage DC | Inverter | inverter049_MODBUS.HR1051_vdcBus_V | Voltage DC | 247 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV049 | Daggett 3_SUB1_INV049_Fault Code 1 | Inverter | Inverter049_MODBUS.HRxxxx_currentFault | Fault Code 1 | 248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Warning | Inverter | Inverter049_MODBUS.HRxxxx_currentWarning | Warning | 249 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Internal Input Status | Inverter | Inverter049_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 250 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Internal Output Status | Inverter | Inverter049_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 251 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Module Fault Code | Inverter | Inverter049_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 252 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Internal Humidity | Inverter | Inverter049_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 253 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Humidity | Inverter | Inverter049_MODBUS.HRxxxx_humidity | Humidity | 254 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_Comms Fault Time | Inverter | Inverter049_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 255 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Status | Inverter | Inverter049_MODBUS.HRxxxx_M1_status | Module Status | 256 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 IR | Inverter | Inverter049_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 257 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 IS | Inverter | Inverter049_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 IT | Inverter | Inverter049_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 261 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 262 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 263 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 P | Inverter | Inverter049_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 264 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Q | Inverter | Inverter049_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 265 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 266 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 267 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 268 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M1 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 270 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Status | Inverter | Inverter049_MODBUS.HRxxxx_M2_status | Module Status | 271 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 IR | Inverter | Inverter049_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 272 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 IS | Inverter | Inverter049_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 IT | Inverter | Inverter049_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 276 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 277 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 P | Inverter | Inverter049_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 279 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Q | Inverter | Inverter049_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 280 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 281 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 282 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 283 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 284 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M2 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Status | Inverter | Inverter049_MODBUS.HRxxxx_M3_status | Module Status | 286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 IR | Inverter | Inverter049_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 287 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 IS | Inverter | Inverter049_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 288 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 IT | Inverter | Inverter049_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 289 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 291 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 292 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 293 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 P | Inverter | Inverter049_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 294 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Q | Inverter | Inverter049_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 295 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 296 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 297 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 298 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 299 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M3 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 300 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Status | Inverter | Inverter049_MODBUS.HRxxxx_M4_status | Module Status | 301 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 IR | Inverter | Inverter049_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 302 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 IS | Inverter | Inverter049_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 303 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 IT | Inverter | Inverter049_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 305 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 306 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 307 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 308 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 P | Inverter | Inverter049_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 309 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Q | Inverter | Inverter049_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 310 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 311 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 312 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 313 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 314 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M4 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 315 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Status | Inverter | Inverter049_MODBUS.HRxxxx_M5_status | Module Status | 316 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 IR | Inverter | Inverter049_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 317 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 IS | Inverter | Inverter049_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 318 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 IT | Inverter | Inverter049_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 319 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 321 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 322 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 323 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 P | Inverter | Inverter049_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 324 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Q | Inverter | Inverter049_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 325 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 326 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 327 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 328 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 329 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M5 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 330 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Status | Inverter | Inverter049_MODBUS.HRxxxx_M6_status | Module Status | 331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 IR | Inverter | Inverter049_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 332 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 IS | Inverter | Inverter049_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 333 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 IT | Inverter | Inverter049_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 IDC | Inverter | Inverter049_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 VDCP | Inverter | Inverter049_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 336 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 VDCN | Inverter | Inverter049_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 337 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 VDC | Inverter | Inverter049_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 P | Inverter | Inverter049_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 339 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Q | Inverter | Inverter049_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 340 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Ambient Temp | Inverter | Inverter049_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 341 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Max IGBT Temp | Inverter | Inverter049_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 342 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 IO Status | Inverter | Inverter049_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 343 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Hardware Version | Inverter | Inverter049_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV049 | Daggett 3_SUB1_INV049_M6 Software Version | Inverter | Inverter049_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_A Phase Current | Inverter | Inverter050_MODBUS.HR1004_i1_A | A Phase Current | 346 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_B Phase Current | Inverter | Inverter050_MODBUS.HR1005_i2_A | B Phase Current | 347 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_C Phase Current | Inverter | Inverter050_MODBUS.HR1006_i3_A | C Phase Current | 348 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Bus Voltage | Inverter | Inverter050_MODBUS.HR1051_vdcBus_V | Bus Voltage | 349 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV050 | Daggett 3_SUB1_INV050_Apparent Power | Inverter | Inverter050_MODBUS.HR1010_s3_VA | Apparent Power | 350 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 1 | Inverter | Inverter050_MODBUS.HR5805_du1_idc_A | Current DC Input# | 351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC Input 1 | Inverter | Inverter050_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 352 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 2 | Inverter | Inverter050_MODBUS.HR5811_du2_idc_A | Current DC Input# | 353 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 2 | Inverter | Inverter050_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 354 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 3 | Inverter | Inverter050_MODBUS.HR5817_du3_idc_A | Current DC Input# | 355 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 3 | Inverter | Inverter050_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 356 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 4 | Inverter | Inverter050_MODBUS.HR5823_du4_idc_A | Current DC Input# | 357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 4 | Inverter | Inverter050_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 358 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 5 | Inverter | Inverter050_MODBUS.HR5829_du5_idc_A | Current DC Input# | 359 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 5 | Inverter | Inverter050_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 360 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 6 | Inverter | Inverter050_MODBUS.HR5835_du6_idc_A | Current DC Input# | 361 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 6 | Inverter | Inverter050_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 362 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 7 | Inverter | Inverter050_MODBUS.HR5841_du7_idc_A | Current DC Input# | 363 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 7 | Inverter | Inverter050_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 364 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 8 | Inverter | Inverter050_MODBUS.HR5847_du8_idc_A | Current DC Input# | 365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 8 | Inverter | Inverter050_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 366 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 9 | Inverter | Inverter050_MODBUS.HR5853_du9_idc_A | Current DC Input# | 367 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 9 | Inverter | Inverter050_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 368 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 10 | Inverter | Inverter050_MODBUS.HR5859_du10_idc_A | Current DC Input# | 369 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 10 | Inverter | Inverter050_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 370 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 11 | Inverter | Inverter050_MODBUS.HR5865_du11_idc_A | Current DC Input# | 371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 11 | Inverter | Inverter050_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 372 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 12 | Inverter | Inverter050_MODBUS.HR5871_du12_idc_A | Current DC Input# | 373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 12 | Inverter | Inverter050_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 374 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 13 | Inverter | Inverter050_MODBUS.HR5877_du13_idc_A | Current DC Input# | 375 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 13 | Inverter | Inverter050_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 376 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 14 | Inverter | Inverter050_MODBUS.HR5883_du14_idc_A | Current DC Input# | 377 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 14 | Inverter | Inverter050_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 378 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 15 | Inverter | Inverter050_MODBUS.HR5889_du15_idc_A | Current DC Input# | 379 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 15 | Inverter | Inverter050_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 380 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 16 | Inverter | Inverter050_MODBUS.HR5895_du16_idc_A | Current DC Input# | 381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 16 | Inverter | Inverter050_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 382 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 17 | Inverter | Inverter050_MODBUS.HR5901_du17_idc_A | Current DC Input# | 383 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 17 | Inverter | Inverter050_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 384 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 18 | Inverter | Inverter050_MODBUS.HR5907_du18_idc_A | Current DC Input# | 385 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 18 | Inverter | Inverter050_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 386 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 19 | Inverter | Inverter050_MODBUS.HR5913_du19_idc_A | Current DC Input# | 387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 19 | Inverter | Inverter050_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 388 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current DC Input 20 | Inverter | Inverter050_MODBUS.HR5919_du20_idc_A | Current DC Input# | 389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC input 20 | Inverter | Inverter050_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 390 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current-AC | Inverter | Inverter050_MODBUS.HR1007_i3Avg_A | Current-AC | 391 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Current-DC | Inverter | Inverter050_MODBUS.HR1062_idcInput_A | Current-DC | 392 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Daily Energy Delivered | Inverter | Inverter050_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 393 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power Set Point | Inverter | Inverter050_MODBUS.HR0553_pRef | Real Power Set Point | 394 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Reactive Power Set Point | Inverter | Inverter050_MODBUS.HR0558_qRef | Reactive Power Set Point | 395 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Frequency | Inverter | Inverter050_MODBUS.HR1012_f3_Hz | Frequency | 396 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV050 | Daggett 3_SUB1_INV050_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Insulation Resistance | Inverter | Inverter050_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 397 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Number of DU Channels | Inverter | Inverter050_MODBUS.HR0653_duChannels | Number of DU Channels | 398 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Number of Running Modules | Inverter | Inverter050_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 399 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Operating State | Inverter | Inverter050_MODBUS.HR1123_currentStatus | Operating State | 400 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Power Factor | Inverter | Inverter050_MODBUS.HR1011_pf3 | Power Factor | 401 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV050 | Daggett 3_SUB1_INV050_Ramp Down | Inverter | Inverter050_MODBUS.HR0286_dropGradient_p | Ramp Down | 402 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Ramp Up | Inverter | Inverter050_MODBUS.HR0282_riseGradient_p | Ramp Up | 403 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power Delivered | Inverter | Inverter050_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 404 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Reactive Power Delivered | Inverter | Inverter050_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 405 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power | 406 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Reactive Power | Inverter | Inverter050_MODBUS.HR1009_q3_kvar | Reactive Power | 407 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Reactive Power Mode | Inverter | Inverter050_MODBUS.HR0552_qControlMode | Reactive Power Mode | 408 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Reactive Power Set Point Percent | Inverter | Inverter050_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 409 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power AC Percent | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power AC Percent | 410 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power-AC | Inverter | Inverter050_MODBUS.HR1008_p3_kW | Real Power-AC | 411 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Real Power-DC | Inverter | Inverter050_MODBUS.HR1061_pdcInput_W | Real Power-DC | 412 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Air Intake | Inverter | Inverter050_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 413 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Cabinet | Inverter | Inverter050_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 414 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-IGBT | Inverter | Inverter050_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 415 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Temperature-Module | Inverter | Inverter050_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 416 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage A-B | Inverter | Inverter050_MODBUS.HR1010_vRS_V | Voltage A-B | 417 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage B-C | Inverter | Inverter050_MODBUS.HR1002_vST_V | Voltage B-C | 418 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage C-A | Inverter | Inverter050_MODBUS.HR1003_vTR_V | Voltage C-A | 419 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV050 | Daggett 3_SUB1_INV050_Voltage DC | Inverter | Inverter050_MODBUS.HR1051_vdcBus_V | Voltage DC | 420 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV050 | Daggett 3_SUB1_INV050_Fault Code 1 | Inverter | Inverter050_MODBUS.HRxxxx_currentFault | Fault Code 1 | 421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Warning | Inverter | Inverter050_MODBUS.HRxxxx_currentWarning | Warning | 422 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Internal Input Status | Inverter | Inverter050_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 423 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Internal Output Status | Inverter | Inverter050_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 424 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Module Fault Code | Inverter | Inverter050_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 425 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Internal Humidity | Inverter | Inverter050_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 426 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Humidity | Inverter | Inverter050_MODBUS.HRxxxx_humidity | Humidity | 427 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_Comms Fault Time | Inverter | Inverter050_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 428 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Status | Inverter | Inverter050_MODBUS.HRxxxx_M1_status | Module Status | 429 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 IR | Inverter | Inverter050_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 430 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 IS | Inverter | Inverter050_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 IT | Inverter | Inverter050_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 434 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 435 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 436 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 P | Inverter | Inverter050_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 437 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Q | Inverter | Inverter050_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 438 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 439 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 440 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 441 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M1 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 443 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Status | Inverter | Inverter050_MODBUS.HRxxxx_M2_status | Module Status | 444 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 IR | Inverter | Inverter050_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 445 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 IS | Inverter | Inverter050_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 IT | Inverter | Inverter050_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 449 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 450 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 P | Inverter | Inverter050_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 452 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Q | Inverter | Inverter050_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 453 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 454 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 455 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 456 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 457 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M2 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Status | Inverter | Inverter050_MODBUS.HRxxxx_M3_status | Module Status | 459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 IR | Inverter | Inverter050_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 460 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 IS | Inverter | Inverter050_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 461 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 IT | Inverter | Inverter050_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 462 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 464 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 465 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 466 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 P | Inverter | Inverter050_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 467 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Q | Inverter | Inverter050_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 468 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 469 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 470 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 471 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 472 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M3 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 473 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Status | Inverter | Inverter050_MODBUS.HRxxxx_M4_status | Module Status | 474 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 IR | Inverter | Inverter050_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 475 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 IS | Inverter | Inverter050_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 476 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 IT | Inverter | Inverter050_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 478 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 479 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 480 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 481 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 P | Inverter | Inverter050_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 482 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Q | Inverter | Inverter050_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 483 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 484 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 485 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 486 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 487 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M4 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 488 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Status | Inverter | Inverter050_MODBUS.HRxxxx_M5_status | Module Status | 489 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 IR | Inverter | Inverter050_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 490 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 IS | Inverter | Inverter050_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 491 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 IT | Inverter | Inverter050_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 492 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 494 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 495 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 496 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 P | Inverter | Inverter050_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 497 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Q | Inverter | Inverter050_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 498 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 499 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 500 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 501 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 502 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M5 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 503 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Status | Inverter | Inverter050_MODBUS.HRxxxx_M6_status | Module Status | 504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 IR | Inverter | Inverter050_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 505 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 IS | Inverter | Inverter050_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 506 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 IT | Inverter | Inverter050_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 IDC | Inverter | Inverter050_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 VDCP | Inverter | Inverter050_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 509 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 VDCN | Inverter | Inverter050_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 510 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 VDC | Inverter | Inverter050_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 P | Inverter | Inverter050_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 512 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Q | Inverter | Inverter050_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 513 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Ambient Temp | Inverter | Inverter050_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 514 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Max IGBT Temp | Inverter | Inverter050_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 515 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 IO Status | Inverter | Inverter050_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 516 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Hardware Version | Inverter | Inverter050_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV050 | Daggett 3_SUB1_INV050_M6 Software Version | Inverter | Inverter050_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_A Phase Current | Inverter | Inverter051_MODBUS.HR1004_i1_A | A Phase Current | 519 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_B Phase Current | Inverter | Inverter051_MODBUS.HR1005_i2_A | B Phase Current | 520 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_C Phase Current | Inverter | Inverter051_MODBUS.HR1006_i3_A | C Phase Current | 521 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Bus Voltage | Inverter | Inverter051_MODBUS.HR1051_vdcBus_V | Bus Voltage | 522 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV051 | Daggett 3_SUB1_INV051_Apparent Power | Inverter | Inverter051_MODBUS.HR1010_s3_VA | Apparent Power | 523 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 1 | Inverter | Inverter051_MODBUS.HR5805_du1_idc_A | Current DC Input# | 524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC Input 1 | Inverter | Inverter051_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 525 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 2 | Inverter | Inverter051_MODBUS.HR5811_du2_idc_A | Current DC Input# | 526 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 2 | Inverter | Inverter051_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 527 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 3 | Inverter | Inverter051_MODBUS.HR5817_du3_idc_A | Current DC Input# | 528 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 3 | Inverter | Inverter051_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 529 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 4 | Inverter | Inverter051_MODBUS.HR5823_du4_idc_A | Current DC Input# | 530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 4 | Inverter | Inverter051_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 531 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 5 | Inverter | Inverter051_MODBUS.HR5829_du5_idc_A | Current DC Input# | 532 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 5 | Inverter | Inverter051_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 533 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 6 | Inverter | Inverter051_MODBUS.HR5835_du6_idc_A | Current DC Input# | 534 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 6 | Inverter | Inverter051_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 535 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 7 | Inverter | Inverter051_MODBUS.HR5841_du7_idc_A | Current DC Input# | 536 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 7 | Inverter | Inverter051_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 537 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 8 | Inverter | Inverter051_MODBUS.HR5847_du8_idc_A | Current DC Input# | 538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 8 | Inverter | Inverter051_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 539 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 9 | Inverter | Inverter051_MODBUS.HR5853_du9_idc_A | Current DC Input# | 540 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 9 | Inverter | Inverter051_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 541 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 10 | Inverter | Inverter051_MODBUS.HR5859_du10_idc_A | Current DC Input# | 542 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 10 | Inverter | Inverter051_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 543 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 11 | Inverter | Inverter051_MODBUS.HR5865_du11_idc_A | Current DC Input# | 544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 11 | Inverter | Inverter051_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 545 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 12 | Inverter | Inverter051_MODBUS.HR5871_du12_idc_A | Current DC Input# | 546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 12 | Inverter | Inverter051_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 547 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 13 | Inverter | Inverter051_MODBUS.HR5877_du13_idc_A | Current DC Input# | 548 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 13 | Inverter | Inverter051_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 549 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 14 | Inverter | Inverter051_MODBUS.HR5883_du14_idc_A | Current DC Input# | 550 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 14 | Inverter | Inverter051_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 551 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 15 | Inverter | Inverter051_MODBUS.HR5889_du15_idc_A | Current DC Input# | 552 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 15 | Inverter | Inverter051_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 553 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 16 | Inverter | Inverter051_MODBUS.HR5895_du16_idc_A | Current DC Input# | 554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 16 | Inverter | Inverter051_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 555 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 17 | Inverter | Inverter051_MODBUS.HR5901_du17_idc_A | Current DC Input# | 556 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 17 | Inverter | Inverter051_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 557 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 18 | Inverter | Inverter051_MODBUS.HR5907_du18_idc_A | Current DC Input# | 558 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 18 | Inverter | Inverter051_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 559 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 19 | Inverter | Inverter051_MODBUS.HR5913_du19_idc_A | Current DC Input# | 560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 19 | Inverter | Inverter051_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 561 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current DC Input 20 | Inverter | Inverter051_MODBUS.HR5919_du20_idc_A | Current DC Input# | 562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC input 20 | Inverter | Inverter051_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 563 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current-AC | Inverter | Inverter051_MODBUS.HR1007_i3Avg_A | Current-AC | 564 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Current-DC | Inverter | Inverter051_MODBUS.HR1062_idcInput_A | Current-DC | 565 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Daily Energy Delivered | Inverter | Inverter051_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 566 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power Set Point | Inverter | Inverter051_MODBUS.HR0553_pRef | Real Power Set Point | 567 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Reactive Power Set Point | Inverter | Inverter051_MODBUS.HR0558_qRef | Reactive Power Set Point | 568 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Frequency | Inverter | Inverter051_MODBUS.HR1012_f3_Hz | Frequency | 569 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV051 | Daggett 3_SUB1_INV051_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Insulation Resistance | Inverter | Inverter051_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 570 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Number of DU Channels | Inverter | Inverter051_MODBUS.HR0653_duChannels | Number of DU Channels | 571 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Number of Running Modules | Inverter | Inverter051_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 572 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Operating State | Inverter | Inverter051_MODBUS.HR1123_currentStatus | Operating State | 573 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Power Factor | Inverter | Inverter051_MODBUS.HR1011_pf3 | Power Factor | 574 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV051 | Daggett 3_SUB1_INV051_Ramp Down | Inverter | Inverter051_MODBUS.HR0286_dropGradient_p | Ramp Down | 575 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Ramp Up | Inverter | Inverter051_MODBUS.HR0282_riseGradient_p | Ramp Up | 576 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power Delivered | Inverter | Inverter051_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 577 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Reactive Power Delivered | Inverter | Inverter051_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 578 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power | 579 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Reactive Power | Inverter | Inverter051_MODBUS.HR1009_q3_kvar | Reactive Power | 580 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Reactive Power Mode | Inverter | Inverter051_MODBUS.HR0552_qControlMode | Reactive Power Mode | 581 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Reactive Power Set Point Percent | Inverter | Inverter051_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 582 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power AC Percent | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power AC Percent | 583 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power-AC | Inverter | Inverter051_MODBUS.HR1008_p3_kW | Real Power-AC | 584 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Real Power-DC | Inverter | Inverter051_MODBUS.HR1061_pdcInput_W | Real Power-DC | 585 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Air Intake | Inverter | Inverter051_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 586 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Cabinet | Inverter | Inverter051_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 587 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-IGBT | Inverter | Inverter051_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 588 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Temperature-Module | Inverter | Inverter051_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 589 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage A-B | Inverter | Inverter051_MODBUS.HR1001_vRS_V | Voltage A-B | 590 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage B-C | Inverter | Inverter051_MODBUS.HR1002_vST_V | Voltage B-C | 591 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage C-A | Inverter | Inverter051_MODBUS.HR1003_vTR_V | Voltage C-A | 592 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV051 | Daggett 3_SUB1_INV051_Voltage DC | Inverter | Inverter051_MODBUS.HR1051_vdcBus_V | Voltage DC | 593 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV051 | Daggett 3_SUB1_INV051_Fault Code 1 | Inverter | Inverter051_MODBUS.HRxxxx_currentFault | Fault Code 1 | 594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Warning | Inverter | Inverter051_MODBUS.HRxxxx_currentWarning | Warning | 595 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Internal Input Status | Inverter | Inverter051_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 596 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Internal Output Status | Inverter | Inverter051_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 597 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Module Fault Code | Inverter | Inverter051_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 598 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Internal Humidity | Inverter | Inverter051_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 599 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Humidity | Inverter | Inverter051_MODBUS.HRxxxx_humidity | Humidity | 600 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_Comms Fault Time | Inverter | Inverter051_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 601 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Status | Inverter | Inverter051_MODBUS.HRxxxx_M1_status | Module Status | 602 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 IR | Inverter | Inverter051_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 603 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 IS | Inverter | Inverter051_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 IT | Inverter | Inverter051_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 607 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 608 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 609 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 P | Inverter | Inverter051_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 610 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Q | Inverter | Inverter051_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 611 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 612 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 613 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 614 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M1 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 616 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Status | Inverter | Inverter051_MODBUS.HRxxxx_M2_status | Module Status | 617 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 IR | Inverter | Inverter051_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 618 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 IS | Inverter | Inverter051_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 IT | Inverter | Inverter051_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 622 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 623 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 P | Inverter | Inverter051_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 625 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Q | Inverter | Inverter051_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 626 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 627 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 628 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 629 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 630 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M2 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Status | Inverter | Inverter051_MODBUS.HRxxxx_M3_status | Module Status | 632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 IR | Inverter | Inverter051_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 633 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 IS | Inverter | Inverter051_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 634 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 IT | Inverter | Inverter051_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 635 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 637 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 638 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 639 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 P | Inverter | Inverter051_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 640 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Q | Inverter | Inverter051_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 641 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 642 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 643 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 644 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 645 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M3 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 646 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Status | Inverter | Inverter051_MODBUS.HRxxxx_M4_status | Module Status | 647 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 IR | Inverter | Inverter051_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 648 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 IS | Inverter | Inverter051_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 649 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 IT | Inverter | Inverter051_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 651 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 652 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 653 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 654 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 P | Inverter | Inverter051_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 655 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Q | Inverter | Inverter051_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 656 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 657 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 658 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 659 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 660 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M4 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 661 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Status | Inverter | Inverter051_MODBUS.HRxxxx_M5_status | Module Status | 662 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 IR | Inverter | Inverter051_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 663 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 IS | Inverter | Inverter051_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 664 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 IT | Inverter | Inverter051_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 665 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 667 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 668 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 669 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 P | Inverter | Inverter051_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 670 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Q | Inverter | Inverter051_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 671 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 672 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 673 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 674 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 675 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M5 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 676 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Status | Inverter | Inverter051_MODBUS.HRxxxx_M6_status | Module Status | 677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 IR | Inverter | Inverter051_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 678 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 IS | Inverter | Inverter051_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 679 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 IT | Inverter | Inverter051_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 IDC | Inverter | Inverter051_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 VDCP | Inverter | Inverter051_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 682 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 VDCN | Inverter | Inverter051_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 683 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 VDC | Inverter | Inverter051_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 P | Inverter | Inverter051_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 685 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Q | Inverter | Inverter051_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 686 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Ambient Temp | Inverter | Inverter051_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 687 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Max IGBT Temp | Inverter | Inverter051_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 688 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 IO Status | Inverter | Inverter051_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 689 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Hardware Version | Inverter | Inverter051_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV051 | Daggett 3_SUB1_INV051_M6 Software Version | Inverter | Inverter051_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_A Phase Current | Inverter | Inverter052_MODBUS.HR1004_i1_A | A Phase Current | 692 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_B Phase Current | Inverter | Inverter052_MODBUS.HR1005_i2_A | B Phase Current | 693 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_C Phase Current | Inverter | Inverter052_MODBUS.HR1006_i3_A | C Phase Current | 694 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Bus Voltage | Inverter | Inverter052_MODBUS.HR1051_vdcBus_V | Bus Voltage | 695 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV052 | Daggett 3_SUB1_INV052_Apparent Power | Inverter | Inverter052_MODBUS.HR1010_s3_VA | Apparent Power | 696 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 1 | Inverter | Inverter052_MODBUS.HR5805_du1_idc_A | Current DC Input# | 697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC Input 1 | Inverter | Inverter052_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 698 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 2 | Inverter | Inverter052_MODBUS.HR5811_du2_idc_A | Current DC Input# | 699 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 2 | Inverter | Inverter052_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 700 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 3 | Inverter | Inverter052_MODBUS.HR5817_du3_idc_A | Current DC Input# | 701 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 3 | Inverter | Inverter052_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 702 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 4 | Inverter | Inverter052_MODBUS.HR5823_du4_idc_A | Current DC Input# | 703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 4 | Inverter | Inverter052_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 704 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 5 | Inverter | Inverter052_MODBUS.HR5829_du5_idc_A | Current DC Input# | 705 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 5 | Inverter | Inverter052_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 706 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 6 | Inverter | Inverter052_MODBUS.HR5835_du6_idc_A | Current DC Input# | 707 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 6 | Inverter | Inverter052_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 708 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 7 | Inverter | Inverter052_MODBUS.HR5841_du7_idc_A | Current DC Input# | 709 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 7 | Inverter | Inverter052_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 710 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 8 | Inverter | Inverter052_MODBUS.HR5847_du8_idc_A | Current DC Input# | 711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 8 | Inverter | Inverter052_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 712 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 9 | Inverter | Inverter052_MODBUS.HR5853_du9_idc_A | Current DC Input# | 713 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 9 | Inverter | Inverter052_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 714 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 10 | Inverter | Inverter052_MODBUS.HR5859_du10_idc_A | Current DC Input# | 715 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 10 | Inverter | Inverter052_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 716 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 11 | Inverter | Inverter052_MODBUS.HR5865_du11_idc_A | Current DC Input# | 717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 11 | Inverter | Inverter052_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 718 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 12 | Inverter | Inverter052_MODBUS.HR5871_du12_idc_A | Current DC Input# | 719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 12 | Inverter | Inverter052_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 720 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 13 | Inverter | Inverter052_MODBUS.HR5877_du13_idc_A | Current DC Input# | 721 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 13 | Inverter | Inverter052_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 722 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 14 | Inverter | Inverter052_MODBUS.HR5883_du14_idc_A | Current DC Input# | 723 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 14 | Inverter | Inverter052_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 724 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 15 | Inverter | Inverter052_MODBUS.HR5889_du15_idc_A | Current DC Input# | 725 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 15 | Inverter | Inverter052_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 726 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 16 | Inverter | Inverter052_MODBUS.HR5895_du16_idc_A | Current DC Input# | 727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 16 | Inverter | Inverter052_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 728 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 17 | Inverter | Inverter052_MODBUS.HR5901_du17_idc_A | Current DC Input# | 729 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 17 | Inverter | Inverter052_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 730 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 18 | Inverter | Inverter052_MODBUS.HR5907_du18_idc_A | Current DC Input# | 731 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 18 | Inverter | Inverter052_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 732 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 19 | Inverter | Inverter052_MODBUS.HR5913_du19_idc_A | Current DC Input# | 733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 19 | Inverter | Inverter052_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 734 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current DC Input 20 | Inverter | Inverter052_MODBUS.HR5919_du20_idc_A | Current DC Input# | 735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC input 20 | Inverter | Inverter052_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 736 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current-AC | Inverter | Inverter052_MODBUS.HR1007_i3Avg_A | Current-AC | 737 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Current-DC | Inverter | Inverter052_MODBUS.HR1062_idcInput_A | Current-DC | 738 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Daily Energy Delivered | Inverter | Inverter052_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 739 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power Set Point | Inverter | Inverter052_MODBUS.HR0553_pRef | Real Power Set Point | 740 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Reactive Power Set Point | Inverter | Inverter052_MODBUS.HR0558_qRef | Reactive Power Set Point | 741 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Frequency | Inverter | Inverter052_MODBUS.HR1012_f3_Hz | Frequency | 742 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV052 | Daggett 3_SUB1_INV052_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Insulation Resistance | Inverter | Inverter052_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 743 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Number of DU Channels | Inverter | Inverter052_MODBUS.HR0653_duChannels | Number of DU Channels | 744 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Number of Running Modules | Inverter | Inverter052_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 745 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Operating State | Inverter | Inverter052_MODBUS.HR1123_currentStatus | Operating State | 746 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Power Factor | Inverter | Inverter052_MODBUS.HR1011_pf3 | Power Factor | 747 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV052 | Daggett 3_SUB1_INV052_Ramp Down | Inverter | Inverter052_MODBUS.HR0286_dropGradient_p | Ramp Down | 748 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Ramp Up | Inverter | Inverter052_MODBUS.HR0282_riseGradient_p | Ramp Up | 749 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power Delivered | Inverter | Inverter052_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 750 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Reactive Power Delivered | Inverter | Inverter052_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 751 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power | 752 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Reactive Power | Inverter | Inverter052_MODBUS.HR1009_q3_kvar | Reactive Power | 753 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Reactive Power Mode | Inverter | Inverter052_MODBUS.HR0552_qControlMode | Reactive Power Mode | 754 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Reactive Power Set Point Percent | Inverter | Inverter052_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 755 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power AC Percent | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power AC Percent | 756 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power-AC | Inverter | Inverter052_MODBUS.HR1008_p3_kW | Real Power-AC | 757 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Real Power-DC | Inverter | Inverter052_MODBUS.HR1061_pdcInput_W | Real Power-DC | 758 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Air Intake | Inverter | Inverter052_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 759 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Cabinet | Inverter | Inverter052_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 760 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-IGBT | Inverter | Inverter052_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 761 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Temperature-Module | Inverter | Inverter052_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 762 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage A-B | Inverter | Inverter052_MODBUS.HR1002_vRS_V | Voltage A-B | 763 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage B-C | Inverter | Inverter052_MODBUS.HR1002_vST_V | Voltage B-C | 764 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage C-A | Inverter | Inverter052_MODBUS.HR1003_vTR_V | Voltage C-A | 765 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV052 | Daggett 3_SUB1_INV052_Voltage DC | Inverter | Inverter052_MODBUS.HR1051_vdcBus_V | Voltage DC | 766 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV052 | Daggett 3_SUB1_INV052_Fault Code 1 | Inverter | Inverter052_MODBUS.HRxxxx_currentFault | Fault Code 1 | 767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Warning | Inverter | Inverter052_MODBUS.HRxxxx_currentWarning | Warning | 768 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Internal Input Status | Inverter | Inverter052_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 769 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Internal Output Status | Inverter | Inverter052_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 770 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Module Fault Code | Inverter | Inverter052_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 771 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Internal Humidity | Inverter | Inverter052_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 772 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Humidity | Inverter | Inverter052_MODBUS.HRxxxx_humidity | Humidity | 773 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_Comms Fault Time | Inverter | Inverter052_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 774 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Status | Inverter | Inverter052_MODBUS.HRxxxx_M1_status | Module Status | 775 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 IR | Inverter | Inverter052_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 776 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 IS | Inverter | Inverter052_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 IT | Inverter | Inverter052_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 780 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 781 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 782 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 P | Inverter | Inverter052_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 783 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Q | Inverter | Inverter052_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 784 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 785 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 786 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 787 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M1 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 789 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Status | Inverter | Inverter052_MODBUS.HRxxxx_M2_status | Module Status | 790 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 IR | Inverter | Inverter052_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 791 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 IS | Inverter | Inverter052_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 IT | Inverter | Inverter052_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 795 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 796 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 P | Inverter | Inverter052_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 798 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Q | Inverter | Inverter052_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 799 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 800 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 801 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 802 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 803 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M2 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Status | Inverter | Inverter052_MODBUS.HRxxxx_M3_status | Module Status | 805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 IR | Inverter | Inverter052_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 806 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 IS | Inverter | Inverter052_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 807 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 IT | Inverter | Inverter052_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 808 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 810 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 811 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 812 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 P | Inverter | Inverter052_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 813 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Q | Inverter | Inverter052_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 814 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 815 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 816 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 817 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 818 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M3 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 819 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Status | Inverter | Inverter052_MODBUS.HRxxxx_M4_status | Module Status | 820 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 IR | Inverter | Inverter052_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 821 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 IS | Inverter | Inverter052_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 822 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 IT | Inverter | Inverter052_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 824 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 825 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 826 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 827 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 P | Inverter | Inverter052_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 828 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Q | Inverter | Inverter052_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 829 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 830 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 831 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 832 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 833 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M4 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 834 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Status | Inverter | Inverter052_MODBUS.HRxxxx_M5_status | Module Status | 835 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 IR | Inverter | Inverter052_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 836 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 IS | Inverter | Inverter052_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 837 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 IT | Inverter | Inverter052_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 838 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 840 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 841 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 842 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 P | Inverter | Inverter052_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 843 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Q | Inverter | Inverter052_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 844 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 845 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 846 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 847 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 848 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M5 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 849 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Status | Inverter | Inverter052_MODBUS.HRxxxx_M6_status | Module Status | 850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 IR | Inverter | Inverter052_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 851 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 IS | Inverter | Inverter052_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 852 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 IT | Inverter | Inverter052_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 IDC | Inverter | Inverter052_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 VDCP | Inverter | Inverter052_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 855 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 VDCN | Inverter | Inverter052_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 856 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 VDC | Inverter | Inverter052_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 P | Inverter | Inverter052_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 858 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Q | Inverter | Inverter052_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 859 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Ambient Temp | Inverter | Inverter052_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 860 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Max IGBT Temp | Inverter | Inverter052_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 861 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 IO Status | Inverter | Inverter052_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 862 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Hardware Version | Inverter | Inverter052_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV052 | Daggett 3_SUB1_INV052_M6 Software Version | Inverter | Inverter052_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_A Phase Current | Inverter | Inverter053_MODBUS.HR1004_i1_A | A Phase Current | 865 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_B Phase Current | Inverter | Inverter053_MODBUS.HR1005_i2_A | B Phase Current | 866 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_C Phase Current | Inverter | Inverter053_MODBUS.HR1006_i3_A | C Phase Current | 867 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Bus Voltage | Inverter | Inverter053_MODBUS.HR1051_vdcBus_V | Bus Voltage | 868 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV053 | Daggett 3_SUB1_INV053_Apparent Power | Inverter | Inverter053_MODBUS.HR1010_s3_VA | Apparent Power | 869 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 1 | Inverter | Inverter053_MODBUS.HR5805_du1_idc_A | Current DC Input# | 870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC Input 1 | Inverter | Inverter053_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 871 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 2 | Inverter | Inverter053_MODBUS.HR5811_du2_idc_A | Current DC Input# | 872 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 2 | Inverter | Inverter053_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 873 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 3 | Inverter | Inverter053_MODBUS.HR5817_du3_idc_A | Current DC Input# | 874 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 3 | Inverter | Inverter053_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 875 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 4 | Inverter | Inverter053_MODBUS.HR5823_du4_idc_A | Current DC Input# | 876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 4 | Inverter | Inverter053_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 877 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 5 | Inverter | Inverter053_MODBUS.HR5829_du5_idc_A | Current DC Input# | 878 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 5 | Inverter | Inverter053_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 879 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 6 | Inverter | Inverter053_MODBUS.HR5835_du6_idc_A | Current DC Input# | 880 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 6 | Inverter | Inverter053_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 881 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 7 | Inverter | Inverter053_MODBUS.HR5841_du7_idc_A | Current DC Input# | 882 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 7 | Inverter | Inverter053_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 883 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 8 | Inverter | Inverter053_MODBUS.HR5847_du8_idc_A | Current DC Input# | 884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 8 | Inverter | Inverter053_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 885 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 9 | Inverter | Inverter053_MODBUS.HR5853_du9_idc_A | Current DC Input# | 886 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 9 | Inverter | Inverter053_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 887 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 10 | Inverter | Inverter053_MODBUS.HR5859_du10_idc_A | Current DC Input# | 888 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 10 | Inverter | Inverter053_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 889 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 11 | Inverter | Inverter053_MODBUS.HR5865_du11_idc_A | Current DC Input# | 890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 11 | Inverter | Inverter053_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 891 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 12 | Inverter | Inverter053_MODBUS.HR5871_du12_idc_A | Current DC Input# | 892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 12 | Inverter | Inverter053_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 893 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 13 | Inverter | Inverter053_MODBUS.HR5877_du13_idc_A | Current DC Input# | 894 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 13 | Inverter | Inverter053_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 895 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 14 | Inverter | Inverter053_MODBUS.HR5883_du14_idc_A | Current DC Input# | 896 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 14 | Inverter | Inverter053_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 897 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 15 | Inverter | Inverter053_MODBUS.HR5889_du15_idc_A | Current DC Input# | 898 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 15 | Inverter | Inverter053_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 899 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 16 | Inverter | Inverter053_MODBUS.HR5895_du16_idc_A | Current DC Input# | 900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 16 | Inverter | Inverter053_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 901 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 17 | Inverter | Inverter053_MODBUS.HR5901_du17_idc_A | Current DC Input# | 902 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 17 | Inverter | Inverter053_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 903 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 18 | Inverter | Inverter053_MODBUS.HR5907_du18_idc_A | Current DC Input# | 904 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 18 | Inverter | Inverter053_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 905 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 19 | Inverter | Inverter053_MODBUS.HR5913_du19_idc_A | Current DC Input# | 906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 19 | Inverter | Inverter053_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 907 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current DC Input 20 | Inverter | Inverter053_MODBUS.HR5919_du20_idc_A | Current DC Input# | 908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC input 20 | Inverter | Inverter053_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 909 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current-AC | Inverter | Inverter053_MODBUS.HR1007_i3Avg_A | Current-AC | 910 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Current-DC | Inverter | Inverter053_MODBUS.HR1062_idcInput_A | Current-DC | 911 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Daily Energy Delivered | Inverter | Inverter053_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 912 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power Set Point | Inverter | Inverter053_MODBUS.HR0553_pRef | Real Power Set Point | 913 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Reactive Power Set Point | Inverter | Inverter053_MODBUS.HR0558_qRef | Reactive Power Set Point | 914 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Frequency | Inverter | Inverter053_MODBUS.HR1012_f3_Hz | Frequency | 915 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV053 | Daggett 3_SUB1_INV053_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Insulation Resistance | Inverter | Inverter053_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 916 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Number of DU Channels | Inverter | Inverter053_MODBUS.HR0653_duChannels | Number of DU Channels | 917 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Number of Running Modules | Inverter | Inverter053_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 918 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Operating State | Inverter | Inverter053_MODBUS.HR1123_currentStatus | Operating State | 919 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Power Factor | Inverter | Inverter053_MODBUS.HR1011_pf3 | Power Factor | 920 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV053 | Daggett 3_SUB1_INV053_Ramp Down | Inverter | Inverter053_MODBUS.HR0286_dropGradient_p | Ramp Down | 921 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Ramp Up | Inverter | Inverter053_MODBUS.HR0282_riseGradient_p | Ramp Up | 922 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power Delivered | Inverter | Inverter053_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 923 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Reactive Power Delivered | Inverter | Inverter053_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 924 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power | 925 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Reactive Power | Inverter | Inverter053_MODBUS.HR1009_q3_kvar | Reactive Power | 926 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Reactive Power Mode | Inverter | Inverter053_MODBUS.HR0552_qControlMode | Reactive Power Mode | 927 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Reactive Power Set Point Percent | Inverter | Inverter053_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 928 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power AC Percent | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power AC Percent | 929 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power-AC | Inverter | Inverter053_MODBUS.HR1008_p3_kW | Real Power-AC | 930 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Real Power-DC | Inverter | Inverter053_MODBUS.HR1061_pdcInput_W | Real Power-DC | 931 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Air Intake | Inverter | Inverter053_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 932 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Cabinet | Inverter | Inverter053_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 933 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-IGBT | Inverter | Inverter053_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 934 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Temperature-Module | Inverter | Inverter053_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 935 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage A-B | Inverter | Inverter053_MODBUS.HR1003_vRS_V | Voltage A-B | 936 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage B-C | Inverter | Inverter053_MODBUS.HR1002_vST_V | Voltage B-C | 937 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage C-A | Inverter | Inverter053_MODBUS.HR1003_vTR_V | Voltage C-A | 938 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV053 | Daggett 3_SUB1_INV053_Voltage DC | Inverter | Inverter053_MODBUS.HR1051_vdcBus_V | Voltage DC | 939 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV053 | Daggett 3_SUB1_INV053_Fault Code 1 | Inverter | Inverter053_MODBUS.HRxxxx_currentFault | Fault Code 1 | 940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Warning | Inverter | Inverter053_MODBUS.HRxxxx_currentWarning | Warning | 941 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Internal Input Status | Inverter | Inverter053_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 942 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Internal Output Status | Inverter | Inverter053_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 943 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Module Fault Code | Inverter | Inverter053_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 944 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Internal Humidity | Inverter | Inverter053_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 945 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Humidity | Inverter | Inverter053_MODBUS.HRxxxx_humidity | Humidity | 946 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_Comms Fault Time | Inverter | Inverter053_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 947 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Status | Inverter | Inverter053_MODBUS.HRxxxx_M1_status | Module Status | 948 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 IR | Inverter | Inverter053_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 949 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 IS | Inverter | Inverter053_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 IT | Inverter | Inverter053_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 953 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 954 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 955 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 P | Inverter | Inverter053_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 956 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Q | Inverter | Inverter053_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 957 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 958 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 959 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 960 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M1 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 962 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Status | Inverter | Inverter053_MODBUS.HRxxxx_M2_status | Module Status | 963 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 IR | Inverter | Inverter053_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 964 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 IS | Inverter | Inverter053_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 IT | Inverter | Inverter053_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 968 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 969 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 P | Inverter | Inverter053_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 971 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Q | Inverter | Inverter053_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 972 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 973 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 974 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 975 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 976 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M2 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Status | Inverter | Inverter053_MODBUS.HRxxxx_M3_status | Module Status | 978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 IR | Inverter | Inverter053_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 979 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 IS | Inverter | Inverter053_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 980 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 IT | Inverter | Inverter053_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 981 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 983 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 984 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 985 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 P | Inverter | Inverter053_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 986 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Q | Inverter | Inverter053_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 987 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 988 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 989 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 990 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 991 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M3 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 992 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Status | Inverter | Inverter053_MODBUS.HRxxxx_M4_status | Module Status | 993 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 IR | Inverter | Inverter053_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 994 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 IS | Inverter | Inverter053_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 995 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 IT | Inverter | Inverter053_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 997 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 998 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 999 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1000 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 P | Inverter | Inverter053_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1001 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Q | Inverter | Inverter053_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1002 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1003 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1004 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1005 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1006 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M4 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1007 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Status | Inverter | Inverter053_MODBUS.HRxxxx_M5_status | Module Status | 1008 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 IR | Inverter | Inverter053_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1009 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 IS | Inverter | Inverter053_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1010 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 IT | Inverter | Inverter053_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1011 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1013 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1014 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1015 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 P | Inverter | Inverter053_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1016 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Q | Inverter | Inverter053_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1017 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1018 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1019 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1020 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1021 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M5 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1022 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Status | Inverter | Inverter053_MODBUS.HRxxxx_M6_status | Module Status | 1023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 IR | Inverter | Inverter053_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1024 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 IS | Inverter | Inverter053_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1025 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 IT | Inverter | Inverter053_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 IDC | Inverter | Inverter053_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 VDCP | Inverter | Inverter053_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1028 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 VDCN | Inverter | Inverter053_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1029 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 VDC | Inverter | Inverter053_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 P | Inverter | Inverter053_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1031 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Q | Inverter | Inverter053_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1032 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Ambient Temp | Inverter | Inverter053_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1033 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Max IGBT Temp | Inverter | Inverter053_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1034 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 IO Status | Inverter | Inverter053_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1035 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Hardware Version | Inverter | Inverter053_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV053 | Daggett 3_SUB1_INV053_M6 Software Version | Inverter | Inverter053_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_A Phase Current | Inverter | Inverter054_MODBUS.HR1004_i1_A | A Phase Current | 1038 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_B Phase Current | Inverter | Inverter054_MODBUS.HR1005_i2_A | B Phase Current | 1039 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_C Phase Current | Inverter | Inverter054_MODBUS.HR1006_i3_A | C Phase Current | 1040 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Bus Voltage | Inverter | Inverter054_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1041 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV054 | Daggett 3_SUB1_INV054_Apparent Power | Inverter | Inverter054_MODBUS.HR1010_s3_VA | Apparent Power | 1042 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 1 | Inverter | Inverter054_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC Input 1 | Inverter | Inverter054_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1044 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 2 | Inverter | Inverter054_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1045 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 2 | Inverter | Inverter054_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1046 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 3 | Inverter | Inverter054_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1047 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 3 | Inverter | Inverter054_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1048 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 4 | Inverter | Inverter054_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 4 | Inverter | Inverter054_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1050 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 5 | Inverter | Inverter054_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1051 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 5 | Inverter | Inverter054_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1052 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 6 | Inverter | Inverter054_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1053 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 6 | Inverter | Inverter054_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1054 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 7 | Inverter | Inverter054_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1055 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 7 | Inverter | Inverter054_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1056 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 8 | Inverter | Inverter054_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 8 | Inverter | Inverter054_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1058 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 9 | Inverter | Inverter054_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1059 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 9 | Inverter | Inverter054_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1060 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 10 | Inverter | Inverter054_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1061 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 10 | Inverter | Inverter054_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1062 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 11 | Inverter | Inverter054_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 11 | Inverter | Inverter054_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1064 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 12 | Inverter | Inverter054_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 12 | Inverter | Inverter054_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1066 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 13 | Inverter | Inverter054_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1067 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 13 | Inverter | Inverter054_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1068 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 14 | Inverter | Inverter054_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1069 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 14 | Inverter | Inverter054_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1070 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 15 | Inverter | Inverter054_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1071 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 15 | Inverter | Inverter054_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1072 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 16 | Inverter | Inverter054_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 16 | Inverter | Inverter054_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1074 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 17 | Inverter | Inverter054_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1075 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 17 | Inverter | Inverter054_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1076 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 18 | Inverter | Inverter054_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1077 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 18 | Inverter | Inverter054_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1078 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 19 | Inverter | Inverter054_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 19 | Inverter | Inverter054_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1080 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current DC Input 20 | Inverter | Inverter054_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC input 20 | Inverter | Inverter054_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1082 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current-AC | Inverter | Inverter054_MODBUS.HR1007_i3Avg_A | Current-AC | 1083 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Current-DC | Inverter | Inverter054_MODBUS.HR1062_idcInput_A | Current-DC | 1084 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Daily Energy Delivered | Inverter | Inverter054_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1085 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power Set Point | Inverter | Inverter054_MODBUS.HR0553_pRef | Real Power Set Point | 1086 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Reactive Power Set Point | Inverter | Inverter054_MODBUS.HR0558_qRef | Reactive Power Set Point | 1087 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Frequency | Inverter | Inverter054_MODBUS.HR1012_f3_Hz | Frequency | 1088 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV054 | Daggett 3_SUB1_INV054_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Insulation Resistance | Inverter | Inverter054_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1089 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Number of DU Channels | Inverter | Inverter054_MODBUS.HR0653_duChannels | Number of DU Channels | 1090 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Number of Running Modules | Inverter | Inverter054_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1091 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Operating State | Inverter | Inverter054_MODBUS.HR1123_currentStatus | Operating State | 1092 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Power Factor | Inverter | Inverter054_MODBUS.HR1011_pf3 | Power Factor | 1093 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV054 | Daggett 3_SUB1_INV054_Ramp Down | Inverter | Inverter054_MODBUS.HR0286_dropGradient_p | Ramp Down | 1094 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Ramp Up | Inverter | Inverter054_MODBUS.HR0282_riseGradient_p | Ramp Up | 1095 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power Delivered | Inverter | Inverter054_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1096 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Reactive Power Delivered | Inverter | Inverter054_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1097 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power | 1098 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Reactive Power | Inverter | Inverter054_MODBUS.HR1009_q3_kvar | Reactive Power | 1099 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Reactive Power Mode | Inverter | Inverter054_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1100 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Reactive Power Set Point Percent | Inverter | Inverter054_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1101 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power AC Percent | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1102 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power-AC | Inverter | Inverter054_MODBUS.HR1008_p3_kW | Real Power-AC | 1103 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Real Power-DC | Inverter | Inverter054_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1104 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Air Intake | Inverter | Inverter054_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1105 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Cabinet | Inverter | Inverter054_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1106 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-IGBT | Inverter | Inverter054_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1107 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Temperature-Module | Inverter | Inverter054_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1108 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage A-B | Inverter | Inverter054_MODBUS.HR1004_vRS_V | Voltage A-B | 1109 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage B-C | Inverter | Inverter054_MODBUS.HR1002_vST_V | Voltage B-C | 1110 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage C-A | Inverter | Inverter054_MODBUS.HR1003_vTR_V | Voltage C-A | 1111 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV054 | Daggett 3_SUB1_INV054_Voltage DC | Inverter | Inverter054_MODBUS.HR1051_vdcBus_V | Voltage DC | 1112 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV054 | Daggett 3_SUB1_INV054_Fault Code 1 | Inverter | Inverter054_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Warning | Inverter | Inverter054_MODBUS.HRxxxx_currentWarning | Warning | 1114 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Internal Input Status | Inverter | Inverter054_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1115 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Internal Output Status | Inverter | Inverter054_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1116 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Module Fault Code | Inverter | Inverter054_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1117 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Internal Humidity | Inverter | Inverter054_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1118 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Humidity | Inverter | Inverter054_MODBUS.HRxxxx_humidity | Humidity | 1119 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_Comms Fault Time | Inverter | Inverter054_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1120 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Status | Inverter | Inverter054_MODBUS.HRxxxx_M1_status | Module Status | 1121 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 IR | Inverter | Inverter054_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1122 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 IS | Inverter | Inverter054_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 IT | Inverter | Inverter054_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1126 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1127 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1128 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 P | Inverter | Inverter054_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1129 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Q | Inverter | Inverter054_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1130 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1131 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1132 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1133 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M1 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1135 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Status | Inverter | Inverter054_MODBUS.HRxxxx_M2_status | Module Status | 1136 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 IR | Inverter | Inverter054_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1137 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 IS | Inverter | Inverter054_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1138 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 IT | Inverter | Inverter054_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1141 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1142 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 P | Inverter | Inverter054_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1144 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Q | Inverter | Inverter054_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1145 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1146 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1147 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1148 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1149 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M2 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Status | Inverter | Inverter054_MODBUS.HRxxxx_M3_status | Module Status | 1151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 IR | Inverter | Inverter054_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1152 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 IS | Inverter | Inverter054_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1153 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 IT | Inverter | Inverter054_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1154 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1156 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1157 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1158 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 P | Inverter | Inverter054_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1159 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Q | Inverter | Inverter054_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1160 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1161 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1162 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1163 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1164 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M3 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1165 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Status | Inverter | Inverter054_MODBUS.HRxxxx_M4_status | Module Status | 1166 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 IR | Inverter | Inverter054_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1167 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 IS | Inverter | Inverter054_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1168 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 IT | Inverter | Inverter054_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1170 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1171 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1172 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1173 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 P | Inverter | Inverter054_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1174 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Q | Inverter | Inverter054_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1175 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1176 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1177 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1178 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1179 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M4 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1180 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Status | Inverter | Inverter054_MODBUS.HRxxxx_M5_status | Module Status | 1181 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 IR | Inverter | Inverter054_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1182 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 IS | Inverter | Inverter054_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1183 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 IT | Inverter | Inverter054_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1184 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1186 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1187 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1188 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 P | Inverter | Inverter054_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1189 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Q | Inverter | Inverter054_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1190 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1191 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1192 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1193 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1194 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M5 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1195 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Status | Inverter | Inverter054_MODBUS.HRxxxx_M6_status | Module Status | 1196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 IR | Inverter | Inverter054_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1197 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 IS | Inverter | Inverter054_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 IT | Inverter | Inverter054_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 IDC | Inverter | Inverter054_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 VDCP | Inverter | Inverter054_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1201 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 VDCN | Inverter | Inverter054_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1202 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 VDC | Inverter | Inverter054_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 P | Inverter | Inverter054_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1204 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Q | Inverter | Inverter054_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1205 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Ambient Temp | Inverter | Inverter054_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1206 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Max IGBT Temp | Inverter | Inverter054_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1207 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 IO Status | Inverter | Inverter054_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1208 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Hardware Version | Inverter | Inverter054_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1209 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV054 | Daggett 3_SUB1_INV054_M6 Software Version | Inverter | Inverter054_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_A Phase Current | Inverter | Inverter055_MODBUS.HR1004_i1_A | A Phase Current | 1211 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_B Phase Current | Inverter | Inverter055_MODBUS.HR1005_i2_A | B Phase Current | 1212 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_C Phase Current | Inverter | Inverter055_MODBUS.HR1006_i3_A | C Phase Current | 1213 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Bus Voltage | Inverter | Inverter055_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1214 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV055 | Daggett 3_SUB1_INV055_Apparent Power | Inverter | Inverter055_MODBUS.HR1010_s3_VA | Apparent Power | 1215 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 1 | Inverter | Inverter055_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC Input 1 | Inverter | Inverter055_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1217 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 2 | Inverter | Inverter055_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1218 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 2 | Inverter | Inverter055_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1219 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 3 | Inverter | Inverter055_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1220 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 3 | Inverter | Inverter055_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1221 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 4 | Inverter | Inverter055_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 4 | Inverter | Inverter055_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1223 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 5 | Inverter | Inverter055_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1224 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 5 | Inverter | Inverter055_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1225 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 6 | Inverter | Inverter055_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1226 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 6 | Inverter | Inverter055_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1227 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 7 | Inverter | Inverter055_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1228 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 7 | Inverter | Inverter055_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1229 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 8 | Inverter | Inverter055_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1230 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 8 | Inverter | Inverter055_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1231 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 9 | Inverter | Inverter055_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1232 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 9 | Inverter | Inverter055_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1233 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 10 | Inverter | Inverter055_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1234 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 10 | Inverter | Inverter055_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1235 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 11 | Inverter | Inverter055_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 11 | Inverter | Inverter055_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1237 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 12 | Inverter | Inverter055_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 12 | Inverter | Inverter055_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1239 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 13 | Inverter | Inverter055_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1240 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 13 | Inverter | Inverter055_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1241 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 14 | Inverter | Inverter055_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1242 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 14 | Inverter | Inverter055_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1243 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 15 | Inverter | Inverter055_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1244 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 15 | Inverter | Inverter055_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1245 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 16 | Inverter | Inverter055_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1246 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 16 | Inverter | Inverter055_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1247 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 17 | Inverter | Inverter055_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1248 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 17 | Inverter | Inverter055_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1249 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 18 | Inverter | Inverter055_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1250 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 18 | Inverter | Inverter055_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1251 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 19 | Inverter | Inverter055_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1252 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 19 | Inverter | Inverter055_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1253 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current DC Input 20 | Inverter | Inverter055_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC input 20 | Inverter | Inverter055_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1255 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current-AC | Inverter | Inverter055_MODBUS.HR1007_i3Avg_A | Current-AC | 1256 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Current-DC | Inverter | Inverter055_MODBUS.HR1062_idcInput_A | Current-DC | 1257 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Daily Energy Delivered | Inverter | Inverter055_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1258 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power Set Point | Inverter | Inverter055_MODBUS.HR0553_pRef | Real Power Set Point | 1259 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Reactive Power Set Point | Inverter | Inverter055_MODBUS.HR0558_qRef | Reactive Power Set Point | 1260 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Frequency | Inverter | Inverter055_MODBUS.HR1012_f3_Hz | Frequency | 1261 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV055 | Daggett 3_SUB1_INV055_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Insulation Resistance | Inverter | Inverter055_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1262 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Number of DU Channels | Inverter | Inverter055_MODBUS.HR0653_duChannels | Number of DU Channels | 1263 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Number of Running Modules | Inverter | Inverter055_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1264 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Operating State | Inverter | Inverter055_MODBUS.HR1123_currentStatus | Operating State | 1265 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Power Factor | Inverter | Inverter055_MODBUS.HR1011_pf3 | Power Factor | 1266 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV055 | Daggett 3_SUB1_INV055_Ramp Down | Inverter | Inverter055_MODBUS.HR0286_dropGradient_p | Ramp Down | 1267 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Ramp Up | Inverter | Inverter055_MODBUS.HR0282_riseGradient_p | Ramp Up | 1268 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power Delivered | Inverter | Inverter055_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1269 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Reactive Power Delivered | Inverter | Inverter055_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1270 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power | 1271 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Reactive Power | Inverter | Inverter055_MODBUS.HR1009_q3_kvar | Reactive Power | 1272 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Reactive Power Mode | Inverter | Inverter055_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1273 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Reactive Power Set Point Percent | Inverter | Inverter055_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1274 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power AC Percent | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1275 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power-AC | Inverter | Inverter055_MODBUS.HR1008_p3_kW | Real Power-AC | 1276 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Real Power-DC | Inverter | Inverter055_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1277 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Air Intake | Inverter | Inverter055_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1278 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Cabinet | Inverter | Inverter055_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1279 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-IGBT | Inverter | Inverter055_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1280 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Temperature-Module | Inverter | Inverter055_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1281 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage A-B | Inverter | Inverter055_MODBUS.HR1005_vRS_V | Voltage A-B | 1282 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage B-C | Inverter | Inverter055_MODBUS.HR1002_vST_V | Voltage B-C | 1283 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage C-A | Inverter | Inverter055_MODBUS.HR1003_vTR_V | Voltage C-A | 1284 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV055 | Daggett 3_SUB1_INV055_Voltage DC | Inverter | Inverter055_MODBUS.HR1051_vdcBus_V | Voltage DC | 1285 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV055 | Daggett 3_SUB1_INV055_Fault Code 1 | Inverter | Inverter055_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Warning | Inverter | Inverter055_MODBUS.HRxxxx_currentWarning | Warning | 1287 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Internal Input Status | Inverter | Inverter055_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1288 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Internal Output Status | Inverter | Inverter055_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1289 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Module Fault Code | Inverter | Inverter055_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1290 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Internal Humidity | Inverter | Inverter055_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1291 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Humidity | Inverter | Inverter055_MODBUS.HRxxxx_humidity | Humidity | 1292 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_Comms Fault Time | Inverter | Inverter055_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1293 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Status | Inverter | Inverter055_MODBUS.HRxxxx_M1_status | Module Status | 1294 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 IR | Inverter | Inverter055_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1295 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 IS | Inverter | Inverter055_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 IT | Inverter | Inverter055_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1297 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1299 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1300 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1301 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 P | Inverter | Inverter055_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1302 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Q | Inverter | Inverter055_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1303 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1304 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1305 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1306 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1307 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M1 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1308 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Status | Inverter | Inverter055_MODBUS.HRxxxx_M2_status | Module Status | 1309 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 IR | Inverter | Inverter055_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1310 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 IS | Inverter | Inverter055_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1311 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 IT | Inverter | Inverter055_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1313 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1314 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1315 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1316 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 P | Inverter | Inverter055_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1317 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Q | Inverter | Inverter055_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1318 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1319 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1320 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1321 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1322 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M2 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1323 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Status | Inverter | Inverter055_MODBUS.HRxxxx_M3_status | Module Status | 1324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 IR | Inverter | Inverter055_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1325 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 IS | Inverter | Inverter055_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1326 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 IT | Inverter | Inverter055_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1327 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1329 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1330 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1331 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 P | Inverter | Inverter055_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1332 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Q | Inverter | Inverter055_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1333 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1334 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1335 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1336 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1337 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M3 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1338 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Status | Inverter | Inverter055_MODBUS.HRxxxx_M4_status | Module Status | 1339 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 IR | Inverter | Inverter055_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1340 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 IS | Inverter | Inverter055_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1341 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 IT | Inverter | Inverter055_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1342 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1343 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1344 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1345 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1346 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 P | Inverter | Inverter055_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1347 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Q | Inverter | Inverter055_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1348 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1349 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1350 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1351 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1352 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M4 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1353 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Status | Inverter | Inverter055_MODBUS.HRxxxx_M5_status | Module Status | 1354 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 IR | Inverter | Inverter055_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1355 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 IS | Inverter | Inverter055_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1356 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 IT | Inverter | Inverter055_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1357 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1358 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1359 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1360 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1361 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 P | Inverter | Inverter055_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1362 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Q | Inverter | Inverter055_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1363 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1364 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1365 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1366 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1367 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M5 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1368 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Status | Inverter | Inverter055_MODBUS.HRxxxx_M6_status | Module Status | 1369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 IR | Inverter | Inverter055_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1370 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 IS | Inverter | Inverter055_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 IT | Inverter | Inverter055_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 IDC | Inverter | Inverter055_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 VDCP | Inverter | Inverter055_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1374 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 VDCN | Inverter | Inverter055_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1375 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 VDC | Inverter | Inverter055_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 P | Inverter | Inverter055_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1377 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Q | Inverter | Inverter055_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1378 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Ambient Temp | Inverter | Inverter055_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1379 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Max IGBT Temp | Inverter | Inverter055_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1380 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 IO Status | Inverter | Inverter055_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1381 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Hardware Version | Inverter | Inverter055_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1382 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV055 | Daggett 3_SUB1_INV055_M6 Software Version | Inverter | Inverter055_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_A Phase Current | Inverter | Inverter056_MODBUS.HR1004_i1_A | A Phase Current | 1384 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_B Phase Current | Inverter | Inverter056_MODBUS.HR1005_i2_A | B Phase Current | 1385 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_C Phase Current | Inverter | Inverter056_MODBUS.HR1006_i3_A | C Phase Current | 1386 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Bus Voltage | Inverter | Inverter056_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1387 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV056 | Daggett 3_SUB1_INV056_Apparent Power | Inverter | Inverter056_MODBUS.HR1010_s3_VA | Apparent Power | 1388 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 1 | Inverter | Inverter056_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC Input 1 | Inverter | Inverter056_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1390 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 2 | Inverter | Inverter056_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1391 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 2 | Inverter | Inverter056_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1392 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 3 | Inverter | Inverter056_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1393 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 3 | Inverter | Inverter056_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1394 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 4 | Inverter | Inverter056_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 4 | Inverter | Inverter056_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1396 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 5 | Inverter | Inverter056_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1397 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 5 | Inverter | Inverter056_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1398 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 6 | Inverter | Inverter056_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1399 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 6 | Inverter | Inverter056_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1400 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 7 | Inverter | Inverter056_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1401 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 7 | Inverter | Inverter056_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1402 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 8 | Inverter | Inverter056_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1403 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 8 | Inverter | Inverter056_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1404 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 9 | Inverter | Inverter056_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1405 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 9 | Inverter | Inverter056_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1406 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 10 | Inverter | Inverter056_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1407 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 10 | Inverter | Inverter056_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1408 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 11 | Inverter | Inverter056_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 11 | Inverter | Inverter056_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1410 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 12 | Inverter | Inverter056_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 12 | Inverter | Inverter056_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1412 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 13 | Inverter | Inverter056_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1413 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 13 | Inverter | Inverter056_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1414 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 14 | Inverter | Inverter056_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1415 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 14 | Inverter | Inverter056_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1416 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 15 | Inverter | Inverter056_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1417 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 15 | Inverter | Inverter056_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1418 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 16 | Inverter | Inverter056_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1419 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 16 | Inverter | Inverter056_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1420 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 17 | Inverter | Inverter056_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1421 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 17 | Inverter | Inverter056_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1422 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 18 | Inverter | Inverter056_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1423 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 18 | Inverter | Inverter056_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1424 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 19 | Inverter | Inverter056_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1425 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 19 | Inverter | Inverter056_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1426 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current DC Input 20 | Inverter | Inverter056_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC input 20 | Inverter | Inverter056_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1428 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current-AC | Inverter | Inverter056_MODBUS.HR1007_i3Avg_A | Current-AC | 1429 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Current-DC | Inverter | Inverter056_MODBUS.HR1062_idcInput_A | Current-DC | 1430 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Daily Energy Delivered | Inverter | Inverter056_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1431 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power Set Point | Inverter | Inverter056_MODBUS.HR0553_pRef | Real Power Set Point | 1432 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Reactive Power Set Point | Inverter | Inverter056_MODBUS.HR0558_qRef | Reactive Power Set Point | 1433 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Frequency | Inverter | Inverter056_MODBUS.HR1012_f3_Hz | Frequency | 1434 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV056 | Daggett 3_SUB1_INV056_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Insulation Resistance | Inverter | Inverter056_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1435 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Number of DU Channels | Inverter | Inverter056_MODBUS.HR0653_duChannels | Number of DU Channels | 1436 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Number of Running Modules | Inverter | Inverter056_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1437 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Operating State | Inverter | Inverter056_MODBUS.HR1123_currentStatus | Operating State | 1438 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Power Factor | Inverter | Inverter056_MODBUS.HR1011_pf3 | Power Factor | 1439 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV056 | Daggett 3_SUB1_INV056_Ramp Down | Inverter | Inverter056_MODBUS.HR0286_dropGradient_p | Ramp Down | 1440 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Ramp Up | Inverter | Inverter056_MODBUS.HR0282_riseGradient_p | Ramp Up | 1441 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power Delivered | Inverter | Inverter056_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1442 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Reactive Power Delivered | Inverter | Inverter056_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1443 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power | 1444 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Reactive Power | Inverter | Inverter056_MODBUS.HR1009_q3_kvar | Reactive Power | 1445 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Reactive Power Mode | Inverter | Inverter056_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1446 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Reactive Power Set Point Percent | Inverter | Inverter056_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1447 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power AC Percent | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1448 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power-AC | Inverter | Inverter056_MODBUS.HR1008_p3_kW | Real Power-AC | 1449 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Real Power-DC | Inverter | Inverter056_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1450 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Air Intake | Inverter | Inverter056_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1451 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Cabinet | Inverter | Inverter056_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1452 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-IGBT | Inverter | Inverter056_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1453 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Temperature-Module | Inverter | Inverter056_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1454 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage A-B | Inverter | Inverter056_MODBUS.HR1006_vRS_V | Voltage A-B | 1455 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage B-C | Inverter | Inverter056_MODBUS.HR1002_vST_V | Voltage B-C | 1456 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage C-A | Inverter | Inverter056_MODBUS.HR1003_vTR_V | Voltage C-A | 1457 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV056 | Daggett 3_SUB1_INV056_Voltage DC | Inverter | Inverter056_MODBUS.HR1051_vdcBus_V | Voltage DC | 1458 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV056 | Daggett 3_SUB1_INV056_Fault Code 1 | Inverter | Inverter056_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Warning | Inverter | Inverter056_MODBUS.HRxxxx_currentWarning | Warning | 1460 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Internal Input Status | Inverter | Inverter056_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1461 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Internal Output Status | Inverter | Inverter056_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1462 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Module Fault Code | Inverter | Inverter056_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1463 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Internal Humidity | Inverter | Inverter056_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1464 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Humidity | Inverter | Inverter056_MODBUS.HRxxxx_humidity | Humidity | 1465 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_Comms Fault Time | Inverter | Inverter056_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1466 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Status | Inverter | Inverter056_MODBUS.HRxxxx_M1_status | Module Status | 1467 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 IR | Inverter | Inverter056_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1468 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 IS | Inverter | Inverter056_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 IT | Inverter | Inverter056_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1470 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1472 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1473 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1474 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 P | Inverter | Inverter056_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1475 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Q | Inverter | Inverter056_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1476 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1477 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1478 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1479 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1480 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M1 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1481 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Status | Inverter | Inverter056_MODBUS.HRxxxx_M2_status | Module Status | 1482 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 IR | Inverter | Inverter056_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1483 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 IS | Inverter | Inverter056_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1484 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 IT | Inverter | Inverter056_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1486 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1487 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1488 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1489 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 P | Inverter | Inverter056_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1490 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Q | Inverter | Inverter056_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1491 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1492 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1493 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1494 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1495 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M2 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1496 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Status | Inverter | Inverter056_MODBUS.HRxxxx_M3_status | Module Status | 1497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 IR | Inverter | Inverter056_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1498 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 IS | Inverter | Inverter056_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1499 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 IT | Inverter | Inverter056_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1500 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1502 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1503 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1504 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 P | Inverter | Inverter056_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1505 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Q | Inverter | Inverter056_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1506 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1507 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1508 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1509 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1510 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M3 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1511 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Status | Inverter | Inverter056_MODBUS.HRxxxx_M4_status | Module Status | 1512 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 IR | Inverter | Inverter056_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1513 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 IS | Inverter | Inverter056_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1514 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 IT | Inverter | Inverter056_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1515 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1516 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1517 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1518 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1519 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 P | Inverter | Inverter056_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1520 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Q | Inverter | Inverter056_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1521 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1522 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1523 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1524 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1525 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M4 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1526 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Status | Inverter | Inverter056_MODBUS.HRxxxx_M5_status | Module Status | 1527 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 IR | Inverter | Inverter056_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1528 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 IS | Inverter | Inverter056_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1529 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 IT | Inverter | Inverter056_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1530 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1531 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1532 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1533 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1534 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 P | Inverter | Inverter056_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1535 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Q | Inverter | Inverter056_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1536 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1537 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1538 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1539 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1540 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M5 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1541 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Status | Inverter | Inverter056_MODBUS.HRxxxx_M6_status | Module Status | 1542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 IR | Inverter | Inverter056_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1543 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 IS | Inverter | Inverter056_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 IT | Inverter | Inverter056_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 IDC | Inverter | Inverter056_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 VDCP | Inverter | Inverter056_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1547 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 VDCN | Inverter | Inverter056_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1548 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 VDC | Inverter | Inverter056_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 P | Inverter | Inverter056_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1550 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Q | Inverter | Inverter056_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1551 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Ambient Temp | Inverter | Inverter056_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1552 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Max IGBT Temp | Inverter | Inverter056_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1553 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 IO Status | Inverter | Inverter056_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1554 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Hardware Version | Inverter | Inverter056_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1555 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV056 | Daggett 3_SUB1_INV056_M6 Software Version | Inverter | Inverter056_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_A Phase Current | Inverter | Inverter057_MODBUS.HR1004_i1_A | A Phase Current | 1557 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_B Phase Current | Inverter | Inverter057_MODBUS.HR1005_i2_A | B Phase Current | 1558 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_C Phase Current | Inverter | Inverter057_MODBUS.HR1006_i3_A | C Phase Current | 1559 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Bus Voltage | Inverter | Inverter057_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1560 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV057 | Daggett 3_SUB1_INV057_Apparent Power | Inverter | Inverter057_MODBUS.HR1010_s3_VA | Apparent Power | 1561 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 1 | Inverter | Inverter057_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC Input 1 | Inverter | Inverter057_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1563 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 2 | Inverter | Inverter057_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1564 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 2 | Inverter | Inverter057_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1565 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 3 | Inverter | Inverter057_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1566 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 3 | Inverter | Inverter057_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1567 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 4 | Inverter | Inverter057_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 4 | Inverter | Inverter057_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1569 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 5 | Inverter | Inverter057_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1570 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 5 | Inverter | Inverter057_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1571 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 6 | Inverter | Inverter057_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1572 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 6 | Inverter | Inverter057_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1573 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 7 | Inverter | Inverter057_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1574 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 7 | Inverter | Inverter057_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1575 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 8 | Inverter | Inverter057_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1576 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 8 | Inverter | Inverter057_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1577 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 9 | Inverter | Inverter057_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1578 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 9 | Inverter | Inverter057_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1579 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 10 | Inverter | Inverter057_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1580 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 10 | Inverter | Inverter057_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1581 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 11 | Inverter | Inverter057_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 11 | Inverter | Inverter057_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1583 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 12 | Inverter | Inverter057_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 12 | Inverter | Inverter057_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1585 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 13 | Inverter | Inverter057_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1586 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 13 | Inverter | Inverter057_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1587 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 14 | Inverter | Inverter057_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1588 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 14 | Inverter | Inverter057_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1589 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 15 | Inverter | Inverter057_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1590 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 15 | Inverter | Inverter057_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1591 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 16 | Inverter | Inverter057_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1592 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 16 | Inverter | Inverter057_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1593 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 17 | Inverter | Inverter057_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1594 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 17 | Inverter | Inverter057_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1595 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 18 | Inverter | Inverter057_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1596 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 18 | Inverter | Inverter057_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1597 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 19 | Inverter | Inverter057_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1598 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 19 | Inverter | Inverter057_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1599 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current DC Input 20 | Inverter | Inverter057_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC input 20 | Inverter | Inverter057_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1601 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current-AC | Inverter | Inverter057_MODBUS.HR1007_i3Avg_A | Current-AC | 1602 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Current-DC | Inverter | Inverter057_MODBUS.HR1062_idcInput_A | Current-DC | 1603 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Daily Energy Delivered | Inverter | Inverter057_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1604 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power Set Point | Inverter | Inverter057_MODBUS.HR0553_pRef | Real Power Set Point | 1605 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Reactive Power Set Point | Inverter | Inverter057_MODBUS.HR0558_qRef | Reactive Power Set Point | 1606 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Frequency | Inverter | Inverter057_MODBUS.HR1012_f3_Hz | Frequency | 1607 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV057 | Daggett 3_SUB1_INV057_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Insulation Resistance | Inverter | Inverter057_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1608 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Number of DU Channels | Inverter | Inverter057_MODBUS.HR0653_duChannels | Number of DU Channels | 1609 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Number of Running Modules | Inverter | Inverter057_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1610 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Operating State | Inverter | Inverter057_MODBUS.HR1123_currentStatus | Operating State | 1611 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Power Factor | Inverter | Inverter057_MODBUS.HR1011_pf3 | Power Factor | 1612 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV057 | Daggett 3_SUB1_INV057_Ramp Down | Inverter | Inverter057_MODBUS.HR0286_dropGradient_p | Ramp Down | 1613 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Ramp Up | Inverter | Inverter057_MODBUS.HR0282_riseGradient_p | Ramp Up | 1614 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power Delivered | Inverter | Inverter057_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1615 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Reactive Power Delivered | Inverter | Inverter057_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1616 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power | 1617 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Reactive Power | Inverter | Inverter057_MODBUS.HR1009_q3_kvar | Reactive Power | 1618 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Reactive Power Mode | Inverter | Inverter057_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1619 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Reactive Power Set Point Percent | Inverter | Inverter057_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1620 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power AC Percent | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1621 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power-AC | Inverter | Inverter057_MODBUS.HR1008_p3_kW | Real Power-AC | 1622 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Real Power-DC | Inverter | Inverter057_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1623 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Air Intake | Inverter | Inverter057_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1624 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Cabinet | Inverter | Inverter057_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1625 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-IGBT | Inverter | Inverter057_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1626 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Temperature-Module | Inverter | Inverter057_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1627 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage A-B | Inverter | Inverter057_MODBUS.HR1007_vRS_V | Voltage A-B | 1628 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage B-C | Inverter | Inverter057_MODBUS.HR1002_vST_V | Voltage B-C | 1629 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage C-A | Inverter | Inverter057_MODBUS.HR1003_vTR_V | Voltage C-A | 1630 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV057 | Daggett 3_SUB1_INV057_Voltage DC | Inverter | Inverter057_MODBUS.HR1051_vdcBus_V | Voltage DC | 1631 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV057 | Daggett 3_SUB1_INV057_Fault Code 1 | Inverter | Inverter057_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Warning | Inverter | Inverter057_MODBUS.HRxxxx_currentWarning | Warning | 1633 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Internal Input Status | Inverter | Inverter057_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1634 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Internal Output Status | Inverter | Inverter057_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1635 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Module Fault Code | Inverter | Inverter057_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1636 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Internal Humidity | Inverter | Inverter057_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1637 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Humidity | Inverter | Inverter057_MODBUS.HRxxxx_humidity | Humidity | 1638 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_Comms Fault Time | Inverter | Inverter057_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1639 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Status | Inverter | Inverter057_MODBUS.HRxxxx_M1_status | Module Status | 1640 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 IR | Inverter | Inverter057_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1641 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 IS | Inverter | Inverter057_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 IT | Inverter | Inverter057_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1643 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1645 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1646 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1647 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 P | Inverter | Inverter057_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1648 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Q | Inverter | Inverter057_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1649 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1650 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1651 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1652 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1653 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M1 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1654 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Status | Inverter | Inverter057_MODBUS.HRxxxx_M2_status | Module Status | 1655 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 IR | Inverter | Inverter057_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1656 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 IS | Inverter | Inverter057_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1657 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 IT | Inverter | Inverter057_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1659 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1660 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1661 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1662 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 P | Inverter | Inverter057_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1663 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Q | Inverter | Inverter057_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1664 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1665 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1666 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1667 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1668 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M2 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1669 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Status | Inverter | Inverter057_MODBUS.HRxxxx_M3_status | Module Status | 1670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 IR | Inverter | Inverter057_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1671 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 IS | Inverter | Inverter057_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1672 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 IT | Inverter | Inverter057_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1673 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1675 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1676 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1677 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 P | Inverter | Inverter057_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1678 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Q | Inverter | Inverter057_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1679 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1680 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1681 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1682 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1683 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M3 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1684 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Status | Inverter | Inverter057_MODBUS.HRxxxx_M4_status | Module Status | 1685 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 IR | Inverter | Inverter057_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1686 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 IS | Inverter | Inverter057_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1687 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 IT | Inverter | Inverter057_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1688 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1689 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1690 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1691 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1692 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 P | Inverter | Inverter057_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1693 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Q | Inverter | Inverter057_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1694 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1695 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1696 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1697 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1698 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M4 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1699 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Status | Inverter | Inverter057_MODBUS.HRxxxx_M5_status | Module Status | 1700 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 IR | Inverter | Inverter057_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1701 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 IS | Inverter | Inverter057_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1702 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 IT | Inverter | Inverter057_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1703 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1704 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1705 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1706 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1707 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 P | Inverter | Inverter057_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1708 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Q | Inverter | Inverter057_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1709 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1710 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1711 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1712 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1713 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M5 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1714 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Status | Inverter | Inverter057_MODBUS.HRxxxx_M6_status | Module Status | 1715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 IR | Inverter | Inverter057_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1716 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 IS | Inverter | Inverter057_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 IT | Inverter | Inverter057_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 IDC | Inverter | Inverter057_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 VDCP | Inverter | Inverter057_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1720 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 VDCN | Inverter | Inverter057_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1721 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 VDC | Inverter | Inverter057_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 P | Inverter | Inverter057_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1723 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Q | Inverter | Inverter057_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1724 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Ambient Temp | Inverter | Inverter057_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1725 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Max IGBT Temp | Inverter | Inverter057_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1726 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 IO Status | Inverter | Inverter057_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1727 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Hardware Version | Inverter | Inverter057_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1728 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV057 | Daggett 3_SUB1_INV057_M6 Software Version | Inverter | Inverter057_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_A Phase Current | Inverter | Inverter058_MODBUS.HR1004_i1_A | A Phase Current | 1730 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_B Phase Current | Inverter | Inverter058_MODBUS.HR1005_i2_A | B Phase Current | 1731 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_C Phase Current | Inverter | Inverter058_MODBUS.HR1006_i3_A | C Phase Current | 1732 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Bus Voltage | Inverter | Inverter058_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1733 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV058 | Daggett 3_SUB1_INV058_Apparent Power | Inverter | Inverter058_MODBUS.HR1010_s3_VA | Apparent Power | 1734 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 1 | Inverter | Inverter058_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC Input 1 | Inverter | Inverter058_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1736 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 2 | Inverter | Inverter058_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1737 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 2 | Inverter | Inverter058_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1738 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 3 | Inverter | Inverter058_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1739 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 3 | Inverter | Inverter058_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1740 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 4 | Inverter | Inverter058_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 4 | Inverter | Inverter058_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1742 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 5 | Inverter | Inverter058_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1743 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 5 | Inverter | Inverter058_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1744 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 6 | Inverter | Inverter058_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1745 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 6 | Inverter | Inverter058_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1746 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 7 | Inverter | Inverter058_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1747 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 7 | Inverter | Inverter058_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1748 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 8 | Inverter | Inverter058_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1749 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 8 | Inverter | Inverter058_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1750 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 9 | Inverter | Inverter058_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1751 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 9 | Inverter | Inverter058_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1752 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 10 | Inverter | Inverter058_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1753 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 10 | Inverter | Inverter058_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1754 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 11 | Inverter | Inverter058_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 11 | Inverter | Inverter058_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1756 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 12 | Inverter | Inverter058_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 12 | Inverter | Inverter058_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1758 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 13 | Inverter | Inverter058_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1759 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 13 | Inverter | Inverter058_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1760 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 14 | Inverter | Inverter058_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1761 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 14 | Inverter | Inverter058_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1762 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 15 | Inverter | Inverter058_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1763 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 15 | Inverter | Inverter058_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1764 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 16 | Inverter | Inverter058_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1765 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 16 | Inverter | Inverter058_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1766 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 17 | Inverter | Inverter058_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1767 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 17 | Inverter | Inverter058_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1768 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 18 | Inverter | Inverter058_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1769 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 18 | Inverter | Inverter058_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1770 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 19 | Inverter | Inverter058_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1771 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 19 | Inverter | Inverter058_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1772 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current DC Input 20 | Inverter | Inverter058_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC input 20 | Inverter | Inverter058_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1774 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current-AC | Inverter | Inverter058_MODBUS.HR1007_i3Avg_A | Current-AC | 1775 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Current-DC | Inverter | Inverter058_MODBUS.HR1062_idcInput_A | Current-DC | 1776 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Daily Energy Delivered | Inverter | Inverter058_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1777 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power Set Point | Inverter | Inverter058_MODBUS.HR0553_pRef | Real Power Set Point | 1778 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Reactive Power Set Point | Inverter | Inverter058_MODBUS.HR0558_qRef | Reactive Power Set Point | 1779 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Frequency | Inverter | Inverter058_MODBUS.HR1012_f3_Hz | Frequency | 1780 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV058 | Daggett 3_SUB1_INV058_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Insulation Resistance | Inverter | Inverter058_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1781 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Number of DU Channels | Inverter | Inverter058_MODBUS.HR0653_duChannels | Number of DU Channels | 1782 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Number of Running Modules | Inverter | Inverter058_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1783 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Operating State | Inverter | Inverter058_MODBUS.HR1123_currentStatus | Operating State | 1784 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Power Factor | Inverter | Inverter058_MODBUS.HR1011_pf3 | Power Factor | 1785 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV058 | Daggett 3_SUB1_INV058_Ramp Down | Inverter | Inverter058_MODBUS.HR0286_dropGradient_p | Ramp Down | 1786 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Ramp Up | Inverter | Inverter058_MODBUS.HR0282_riseGradient_p | Ramp Up | 1787 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power Delivered | Inverter | Inverter058_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1788 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Reactive Power Delivered | Inverter | Inverter058_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1789 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power | 1790 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Reactive Power | Inverter | Inverter058_MODBUS.HR1009_q3_kvar | Reactive Power | 1791 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Reactive Power Mode | Inverter | Inverter058_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1792 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Reactive Power Set Point Percent | Inverter | Inverter058_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1793 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power AC Percent | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1794 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power-AC | Inverter | Inverter058_MODBUS.HR1008_p3_kW | Real Power-AC | 1795 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Real Power-DC | Inverter | Inverter058_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1796 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Air Intake | Inverter | Inverter058_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1797 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Cabinet | Inverter | Inverter058_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1798 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-IGBT | Inverter | Inverter058_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1799 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Temperature-Module | Inverter | Inverter058_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1800 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage A-B | Inverter | Inverter058_MODBUS.HR1008_vRS_V | Voltage A-B | 1801 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage B-C | Inverter | Inverter058_MODBUS.HR1002_vST_V | Voltage B-C | 1802 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage C-A | Inverter | Inverter058_MODBUS.HR1003_vTR_V | Voltage C-A | 1803 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV058 | Daggett 3_SUB1_INV058_Voltage DC | Inverter | Inverter058_MODBUS.HR1051_vdcBus_V | Voltage DC | 1804 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV058 | Daggett 3_SUB1_INV058_Fault Code 1 | Inverter | Inverter058_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Warning | Inverter | Inverter058_MODBUS.HRxxxx_currentWarning | Warning | 1806 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Internal Input Status | Inverter | Inverter058_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1807 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Internal Output Status | Inverter | Inverter058_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1808 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Module Fault Code | Inverter | Inverter058_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1809 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Internal Humidity | Inverter | Inverter058_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1810 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Humidity | Inverter | Inverter058_MODBUS.HRxxxx_humidity | Humidity | 1811 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_Comms Fault Time | Inverter | Inverter058_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1812 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Status | Inverter | Inverter058_MODBUS.HRxxxx_M1_status | Module Status | 1813 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 IR | Inverter | Inverter058_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1814 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 IS | Inverter | Inverter058_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 IT | Inverter | Inverter058_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1816 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1818 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1819 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1820 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 P | Inverter | Inverter058_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1821 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Q | Inverter | Inverter058_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1822 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1823 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1824 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1825 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1826 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M1 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 1827 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Status | Inverter | Inverter058_MODBUS.HRxxxx_M2_status | Module Status | 1828 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 IR | Inverter | Inverter058_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 1829 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 IS | Inverter | Inverter058_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 1830 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 IT | Inverter | Inverter058_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 1831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 1832 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 1833 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 1834 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 1835 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 P | Inverter | Inverter058_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 1836 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Q | Inverter | Inverter058_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 1837 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 1838 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 1839 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 1840 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 1841 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M2 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 1842 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Status | Inverter | Inverter058_MODBUS.HRxxxx_M3_status | Module Status | 1843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 IR | Inverter | Inverter058_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 1844 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 IS | Inverter | Inverter058_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 1845 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 IT | Inverter | Inverter058_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 1846 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 1847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 1848 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 1849 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 1850 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 P | Inverter | Inverter058_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 1851 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Q | Inverter | Inverter058_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 1852 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 1853 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 1854 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 1855 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 1856 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M3 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 1857 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Status | Inverter | Inverter058_MODBUS.HRxxxx_M4_status | Module Status | 1858 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 IR | Inverter | Inverter058_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 1859 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 IS | Inverter | Inverter058_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 1860 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 IT | Inverter | Inverter058_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 1861 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 1862 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 1863 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 1864 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 1865 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 P | Inverter | Inverter058_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 1866 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Q | Inverter | Inverter058_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 1867 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 1868 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 1869 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 1870 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 1871 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M4 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 1872 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Status | Inverter | Inverter058_MODBUS.HRxxxx_M5_status | Module Status | 1873 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 IR | Inverter | Inverter058_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 1874 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 IS | Inverter | Inverter058_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 1875 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 IT | Inverter | Inverter058_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 1876 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 1877 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 1878 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 1879 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 1880 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 P | Inverter | Inverter058_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 1881 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Q | Inverter | Inverter058_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 1882 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 1883 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 1884 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 1885 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 1886 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M5 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 1887 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Status | Inverter | Inverter058_MODBUS.HRxxxx_M6_status | Module Status | 1888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 IR | Inverter | Inverter058_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 1889 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 IS | Inverter | Inverter058_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 1890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 IT | Inverter | Inverter058_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 1891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 IDC | Inverter | Inverter058_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 1892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 VDCP | Inverter | Inverter058_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 1893 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 VDCN | Inverter | Inverter058_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 1894 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 VDC | Inverter | Inverter058_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 1895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 P | Inverter | Inverter058_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 1896 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Q | Inverter | Inverter058_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 1897 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Ambient Temp | Inverter | Inverter058_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 1898 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Max IGBT Temp | Inverter | Inverter058_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 1899 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 IO Status | Inverter | Inverter058_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 1900 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Hardware Version | Inverter | Inverter058_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 1901 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV058 | Daggett 3_SUB1_INV058_M6 Software Version | Inverter | Inverter058_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 1902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_A Phase Current | Inverter | Inverter059_MODBUS.HR1004_i1_A | A Phase Current | 1903 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_B Phase Current | Inverter | Inverter059_MODBUS.HR1005_i2_A | B Phase Current | 1904 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_C Phase Current | Inverter | Inverter059_MODBUS.HR1006_i3_A | C Phase Current | 1905 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Bus Voltage | Inverter | Inverter059_MODBUS.HR1051_vdcBus_V | Bus Voltage | 1906 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV059 | Daggett 3_SUB1_INV059_Apparent Power | Inverter | Inverter059_MODBUS.HR1010_s3_VA | Apparent Power | 1907 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 1 | Inverter | Inverter059_MODBUS.HR5805_du1_idc_A | Current DC Input# | 1908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC Input 1 | Inverter | Inverter059_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 1909 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 2 | Inverter | Inverter059_MODBUS.HR5811_du2_idc_A | Current DC Input# | 1910 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 2 | Inverter | Inverter059_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 1911 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 3 | Inverter | Inverter059_MODBUS.HR5817_du3_idc_A | Current DC Input# | 1912 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 3 | Inverter | Inverter059_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 1913 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 4 | Inverter | Inverter059_MODBUS.HR5823_du4_idc_A | Current DC Input# | 1914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 4 | Inverter | Inverter059_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 1915 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 5 | Inverter | Inverter059_MODBUS.HR5829_du5_idc_A | Current DC Input# | 1916 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 5 | Inverter | Inverter059_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 1917 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 6 | Inverter | Inverter059_MODBUS.HR5835_du6_idc_A | Current DC Input# | 1918 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 6 | Inverter | Inverter059_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 1919 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 7 | Inverter | Inverter059_MODBUS.HR5841_du7_idc_A | Current DC Input# | 1920 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 7 | Inverter | Inverter059_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 1921 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 8 | Inverter | Inverter059_MODBUS.HR5847_du8_idc_A | Current DC Input# | 1922 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 8 | Inverter | Inverter059_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 1923 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 9 | Inverter | Inverter059_MODBUS.HR5853_du9_idc_A | Current DC Input# | 1924 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 9 | Inverter | Inverter059_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 1925 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 10 | Inverter | Inverter059_MODBUS.HR5859_du10_idc_A | Current DC Input# | 1926 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 10 | Inverter | Inverter059_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 1927 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 11 | Inverter | Inverter059_MODBUS.HR5865_du11_idc_A | Current DC Input# | 1928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 11 | Inverter | Inverter059_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 1929 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 12 | Inverter | Inverter059_MODBUS.HR5871_du12_idc_A | Current DC Input# | 1930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 12 | Inverter | Inverter059_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 1931 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 13 | Inverter | Inverter059_MODBUS.HR5877_du13_idc_A | Current DC Input# | 1932 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 13 | Inverter | Inverter059_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 1933 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 14 | Inverter | Inverter059_MODBUS.HR5883_du14_idc_A | Current DC Input# | 1934 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 14 | Inverter | Inverter059_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 1935 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 15 | Inverter | Inverter059_MODBUS.HR5889_du15_idc_A | Current DC Input# | 1936 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 15 | Inverter | Inverter059_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 1937 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 16 | Inverter | Inverter059_MODBUS.HR5895_du16_idc_A | Current DC Input# | 1938 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 16 | Inverter | Inverter059_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 1939 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 17 | Inverter | Inverter059_MODBUS.HR5901_du17_idc_A | Current DC Input# | 1940 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 17 | Inverter | Inverter059_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 1941 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 18 | Inverter | Inverter059_MODBUS.HR5907_du18_idc_A | Current DC Input# | 1942 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 18 | Inverter | Inverter059_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 1943 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 19 | Inverter | Inverter059_MODBUS.HR5913_du19_idc_A | Current DC Input# | 1944 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 19 | Inverter | Inverter059_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 1945 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current DC Input 20 | Inverter | Inverter059_MODBUS.HR5919_du20_idc_A | Current DC Input# | 1946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC input 20 | Inverter | Inverter059_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 1947 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current-AC | Inverter | Inverter059_MODBUS.HR1007_i3Avg_A | Current-AC | 1948 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Current-DC | Inverter | Inverter059_MODBUS.HR1062_idcInput_A | Current-DC | 1949 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Daily Energy Delivered | Inverter | Inverter059_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 1950 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power Set Point | Inverter | Inverter059_MODBUS.HR0553_pRef | Real Power Set Point | 1951 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Reactive Power Set Point | Inverter | Inverter059_MODBUS.HR0558_qRef | Reactive Power Set Point | 1952 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Frequency | Inverter | Inverter059_MODBUS.HR1012_f3_Hz | Frequency | 1953 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV059 | Daggett 3_SUB1_INV059_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Insulation Resistance | Inverter | Inverter059_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 1954 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Number of DU Channels | Inverter | Inverter059_MODBUS.HR0653_duChannels | Number of DU Channels | 1955 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Number of Running Modules | Inverter | Inverter059_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 1956 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Operating State | Inverter | Inverter059_MODBUS.HR1123_currentStatus | Operating State | 1957 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Power Factor | Inverter | Inverter059_MODBUS.HR1011_pf3 | Power Factor | 1958 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV059 | Daggett 3_SUB1_INV059_Ramp Down | Inverter | Inverter059_MODBUS.HR0286_dropGradient_p | Ramp Down | 1959 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Ramp Up | Inverter | Inverter059_MODBUS.HR0282_riseGradient_p | Ramp Up | 1960 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power Delivered | Inverter | Inverter059_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 1961 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Reactive Power Delivered | Inverter | Inverter059_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 1962 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power | 1963 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Reactive Power | Inverter | Inverter059_MODBUS.HR1009_q3_kvar | Reactive Power | 1964 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Reactive Power Mode | Inverter | Inverter059_MODBUS.HR0552_qControlMode | Reactive Power Mode | 1965 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Reactive Power Set Point Percent | Inverter | Inverter059_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 1966 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power AC Percent | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power AC Percent | 1967 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power-AC | Inverter | Inverter059_MODBUS.HR1008_p3_kW | Real Power-AC | 1968 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Real Power-DC | Inverter | Inverter059_MODBUS.HR1061_pdcInput_W | Real Power-DC | 1969 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Air Intake | Inverter | Inverter059_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 1970 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Cabinet | Inverter | Inverter059_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 1971 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-IGBT | Inverter | Inverter059_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 1972 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Temperature-Module | Inverter | Inverter059_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 1973 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage A-B | Inverter | Inverter059_MODBUS.HR1009_vRS_V | Voltage A-B | 1974 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage B-C | Inverter | Inverter059_MODBUS.HR1002_vST_V | Voltage B-C | 1975 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage C-A | Inverter | Inverter059_MODBUS.HR1003_vTR_V | Voltage C-A | 1976 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV059 | Daggett 3_SUB1_INV059_Voltage DC | Inverter | Inverter059_MODBUS.HR1051_vdcBus_V | Voltage DC | 1977 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV059 | Daggett 3_SUB1_INV059_Fault Code 1 | Inverter | Inverter059_MODBUS.HRxxxx_currentFault | Fault Code 1 | 1978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Warning | Inverter | Inverter059_MODBUS.HRxxxx_currentWarning | Warning | 1979 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Internal Input Status | Inverter | Inverter059_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 1980 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Internal Output Status | Inverter | Inverter059_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 1981 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Module Fault Code | Inverter | Inverter059_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 1982 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Internal Humidity | Inverter | Inverter059_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 1983 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Humidity | Inverter | Inverter059_MODBUS.HRxxxx_humidity | Humidity | 1984 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_Comms Fault Time | Inverter | Inverter059_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 1985 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Status | Inverter | Inverter059_MODBUS.HRxxxx_M1_status | Module Status | 1986 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 IR | Inverter | Inverter059_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 1987 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 IS | Inverter | Inverter059_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 1988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 IT | Inverter | Inverter059_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 1989 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 1990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 1991 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 1992 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 1993 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 P | Inverter | Inverter059_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 1994 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Q | Inverter | Inverter059_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 1995 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 1996 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 1997 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 1998 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 1999 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M1 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2000 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Status | Inverter | Inverter059_MODBUS.HRxxxx_M2_status | Module Status | 2001 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 IR | Inverter | Inverter059_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2002 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 IS | Inverter | Inverter059_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2003 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 IT | Inverter | Inverter059_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2005 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2006 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2007 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2008 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 P | Inverter | Inverter059_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2009 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Q | Inverter | Inverter059_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2010 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2011 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2012 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2013 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2014 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M2 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2015 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Status | Inverter | Inverter059_MODBUS.HRxxxx_M3_status | Module Status | 2016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 IR | Inverter | Inverter059_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2017 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 IS | Inverter | Inverter059_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2018 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 IT | Inverter | Inverter059_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2019 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2021 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2022 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2023 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 P | Inverter | Inverter059_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2024 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Q | Inverter | Inverter059_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2025 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2026 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2027 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2028 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2029 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M3 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2030 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Status | Inverter | Inverter059_MODBUS.HRxxxx_M4_status | Module Status | 2031 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 IR | Inverter | Inverter059_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2032 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 IS | Inverter | Inverter059_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2033 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 IT | Inverter | Inverter059_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2034 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2035 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2036 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2037 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2038 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 P | Inverter | Inverter059_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2039 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Q | Inverter | Inverter059_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2040 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2041 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2042 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2043 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2044 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M4 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2045 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Status | Inverter | Inverter059_MODBUS.HRxxxx_M5_status | Module Status | 2046 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 IR | Inverter | Inverter059_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2047 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 IS | Inverter | Inverter059_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2048 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 IT | Inverter | Inverter059_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2049 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2050 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2051 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2052 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2053 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 P | Inverter | Inverter059_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2054 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Q | Inverter | Inverter059_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2055 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2056 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2057 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2058 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2059 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M5 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2060 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Status | Inverter | Inverter059_MODBUS.HRxxxx_M6_status | Module Status | 2061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 IR | Inverter | Inverter059_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2062 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 IS | Inverter | Inverter059_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 IT | Inverter | Inverter059_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 IDC | Inverter | Inverter059_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 VDCP | Inverter | Inverter059_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2066 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 VDCN | Inverter | Inverter059_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2067 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 VDC | Inverter | Inverter059_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 P | Inverter | Inverter059_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2069 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Q | Inverter | Inverter059_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2070 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Ambient Temp | Inverter | Inverter059_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2071 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Max IGBT Temp | Inverter | Inverter059_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2072 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 IO Status | Inverter | Inverter059_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2073 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Hardware Version | Inverter | Inverter059_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2074 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV059 | Daggett 3_SUB1_INV059_M6 Software Version | Inverter | Inverter059_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_A Phase Current | Inverter | Inverter060_MODBUS.HR1004_i1_A | A Phase Current | 2076 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_B Phase Current | Inverter | Inverter060_MODBUS.HR1005_i2_A | B Phase Current | 2077 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_C Phase Current | Inverter | Inverter060_MODBUS.HR1006_i3_A | C Phase Current | 2078 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Bus Voltage | Inverter | Inverter060_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2079 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV060 | Daggett 3_SUB1_INV060_Apparent Power | Inverter | Inverter060_MODBUS.HR1010_s3_VA | Apparent Power | 2080 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 1 | Inverter | Inverter060_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC Input 1 | Inverter | Inverter060_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2082 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 2 | Inverter | Inverter060_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2083 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 2 | Inverter | Inverter060_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2084 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 3 | Inverter | Inverter060_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2085 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 3 | Inverter | Inverter060_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2086 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 4 | Inverter | Inverter060_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 4 | Inverter | Inverter060_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2088 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 5 | Inverter | Inverter060_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2089 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 5 | Inverter | Inverter060_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2090 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 6 | Inverter | Inverter060_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2091 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 6 | Inverter | Inverter060_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2092 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 7 | Inverter | Inverter060_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2093 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 7 | Inverter | Inverter060_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2094 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 8 | Inverter | Inverter060_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2095 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 8 | Inverter | Inverter060_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2096 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 9 | Inverter | Inverter060_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2097 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 9 | Inverter | Inverter060_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2098 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 10 | Inverter | Inverter060_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2099 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 10 | Inverter | Inverter060_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2100 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 11 | Inverter | Inverter060_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 11 | Inverter | Inverter060_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2102 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 12 | Inverter | Inverter060_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 12 | Inverter | Inverter060_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2104 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 13 | Inverter | Inverter060_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2105 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 13 | Inverter | Inverter060_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2106 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 14 | Inverter | Inverter060_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2107 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 14 | Inverter | Inverter060_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2108 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 15 | Inverter | Inverter060_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2109 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 15 | Inverter | Inverter060_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2110 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 16 | Inverter | Inverter060_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2111 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 16 | Inverter | Inverter060_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2112 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 17 | Inverter | Inverter060_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2113 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 17 | Inverter | Inverter060_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2114 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 18 | Inverter | Inverter060_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2115 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 18 | Inverter | Inverter060_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2116 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 19 | Inverter | Inverter060_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2117 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 19 | Inverter | Inverter060_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2118 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current DC Input 20 | Inverter | Inverter060_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC input 20 | Inverter | Inverter060_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2120 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current-AC | Inverter | Inverter060_MODBUS.HR1007_i3Avg_A | Current-AC | 2121 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Current-DC | Inverter | Inverter060_MODBUS.HR1062_idcInput_A | Current-DC | 2122 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Daily Energy Delivered | Inverter | Inverter060_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2123 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power Set Point | Inverter | Inverter060_MODBUS.HR0553_pRef | Real Power Set Point | 2124 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Reactive Power Set Point | Inverter | Inverter060_MODBUS.HR0558_qRef | Reactive Power Set Point | 2125 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Frequency | Inverter | Inverter060_MODBUS.HR1012_f3_Hz | Frequency | 2126 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV060 | Daggett 3_SUB1_INV060_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Insulation Resistance | Inverter | Inverter060_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2127 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Number of DU Channels | Inverter | Inverter060_MODBUS.HR0653_duChannels | Number of DU Channels | 2128 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Number of Running Modules | Inverter | Inverter060_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2129 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Operating State | Inverter | Inverter060_MODBUS.HR1123_currentStatus | Operating State | 2130 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Power Factor | Inverter | Inverter060_MODBUS.HR1011_pf3 | Power Factor | 2131 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV060 | Daggett 3_SUB1_INV060_Ramp Down | Inverter | Inverter060_MODBUS.HR0286_dropGradient_p | Ramp Down | 2132 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Ramp Up | Inverter | Inverter060_MODBUS.HR0282_riseGradient_p | Ramp Up | 2133 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power Delivered | Inverter | Inverter060_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2134 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Reactive Power Delivered | Inverter | Inverter060_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2135 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power | 2136 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Reactive Power | Inverter | Inverter060_MODBUS.HR1009_q3_kvar | Reactive Power | 2137 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Reactive Power Mode | Inverter | Inverter060_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2138 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Reactive Power Set Point Percent | Inverter | Inverter060_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2139 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power AC Percent | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2140 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power-AC | Inverter | Inverter060_MODBUS.HR1008_p3_kW | Real Power-AC | 2141 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Real Power-DC | Inverter | Inverter060_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2142 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Air Intake | Inverter | Inverter060_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2143 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Cabinet | Inverter | Inverter060_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2144 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-IGBT | Inverter | Inverter060_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2145 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Temperature-Module | Inverter | Inverter060_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2146 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage A-B | Inverter | Inverter060_MODBUS.HR1010_vRS_V | Voltage A-B | 2147 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage B-C | Inverter | Inverter060_MODBUS.HR1002_vST_V | Voltage B-C | 2148 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage C-A | Inverter | Inverter060_MODBUS.HR1003_vTR_V | Voltage C-A | 2149 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV060 | Daggett 3_SUB1_INV060_Voltage DC | Inverter | Inverter060_MODBUS.HR1051_vdcBus_V | Voltage DC | 2150 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV060 | Daggett 3_SUB1_INV060_Fault Code 1 | Inverter | Inverter060_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Warning | Inverter | Inverter060_MODBUS.HRxxxx_currentWarning | Warning | 2152 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Internal Input Status | Inverter | Inverter060_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2153 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Internal Output Status | Inverter | Inverter060_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2154 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Module Fault Code | Inverter | Inverter060_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2155 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Internal Humidity | Inverter | Inverter060_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2156 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Humidity | Inverter | Inverter060_MODBUS.HRxxxx_humidity | Humidity | 2157 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_Comms Fault Time | Inverter | Inverter060_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2158 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Status | Inverter | Inverter060_MODBUS.HRxxxx_M1_status | Module Status | 2159 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 IR | Inverter | Inverter060_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2160 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 IS | Inverter | Inverter060_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 IT | Inverter | Inverter060_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2162 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2164 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2165 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2166 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 P | Inverter | Inverter060_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2167 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Q | Inverter | Inverter060_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2168 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2169 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2170 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2171 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2172 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M1 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2173 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Status | Inverter | Inverter060_MODBUS.HRxxxx_M2_status | Module Status | 2174 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 IR | Inverter | Inverter060_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2175 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 IS | Inverter | Inverter060_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2176 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 IT | Inverter | Inverter060_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2178 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2179 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2180 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2181 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 P | Inverter | Inverter060_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2182 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Q | Inverter | Inverter060_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2183 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2184 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2185 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2186 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2187 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M2 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2188 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Status | Inverter | Inverter060_MODBUS.HRxxxx_M3_status | Module Status | 2189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 IR | Inverter | Inverter060_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2190 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 IS | Inverter | Inverter060_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2191 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 IT | Inverter | Inverter060_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2192 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2194 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2195 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2196 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 P | Inverter | Inverter060_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2197 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Q | Inverter | Inverter060_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2198 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2199 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2200 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2201 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2202 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M3 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2203 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Status | Inverter | Inverter060_MODBUS.HRxxxx_M4_status | Module Status | 2204 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 IR | Inverter | Inverter060_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2205 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 IS | Inverter | Inverter060_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2206 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 IT | Inverter | Inverter060_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2207 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2208 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2209 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2210 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2211 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 P | Inverter | Inverter060_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2212 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Q | Inverter | Inverter060_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2213 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2214 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2215 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2216 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2217 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M4 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2218 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Status | Inverter | Inverter060_MODBUS.HRxxxx_M5_status | Module Status | 2219 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 IR | Inverter | Inverter060_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2220 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 IS | Inverter | Inverter060_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2221 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 IT | Inverter | Inverter060_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2222 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2223 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2224 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2225 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2226 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 P | Inverter | Inverter060_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2227 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Q | Inverter | Inverter060_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2228 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2229 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2230 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2231 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2232 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M5 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2233 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Status | Inverter | Inverter060_MODBUS.HRxxxx_M6_status | Module Status | 2234 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 IR | Inverter | Inverter060_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2235 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 IS | Inverter | Inverter060_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2236 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 IT | Inverter | Inverter060_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2237 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 IDC | Inverter | Inverter060_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2238 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 VDCP | Inverter | Inverter060_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2239 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 VDCN | Inverter | Inverter060_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2240 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 VDC | Inverter | Inverter060_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2241 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 P | Inverter | Inverter060_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2242 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Q | Inverter | Inverter060_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2243 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Ambient Temp | Inverter | Inverter060_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2244 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Max IGBT Temp | Inverter | Inverter060_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2245 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 IO Status | Inverter | Inverter060_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2246 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Hardware Version | Inverter | Inverter060_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2247 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV060 | Daggett 3_SUB1_INV060_M6 Software Version | Inverter | Inverter060_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2248 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_A Phase Current | Inverter | Inverter061_MODBUS.HR1004_i1_A | A Phase Current | 2249 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_B Phase Current | Inverter | Inverter061_MODBUS.HR1005_i2_A | B Phase Current | 2250 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_C Phase Current | Inverter | Inverter061_MODBUS.HR1006_i3_A | C Phase Current | 2251 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Bus Voltage | Inverter | Inverter061_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2252 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV061 | Daggett 3_SUB1_INV061_Apparent Power | Inverter | Inverter061_MODBUS.HR1010_s3_VA | Apparent Power | 2253 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 1 | Inverter | Inverter061_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2254 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC Input 1 | Inverter | Inverter061_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2255 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 2 | Inverter | Inverter061_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2256 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 2 | Inverter | Inverter061_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2257 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 3 | Inverter | Inverter061_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 3 | Inverter | Inverter061_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2259 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 4 | Inverter | Inverter061_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 4 | Inverter | Inverter061_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2261 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 5 | Inverter | Inverter061_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2262 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 5 | Inverter | Inverter061_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2263 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 6 | Inverter | Inverter061_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2264 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 6 | Inverter | Inverter061_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2265 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 7 | Inverter | Inverter061_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2266 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 7 | Inverter | Inverter061_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2267 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 8 | Inverter | Inverter061_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2268 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 8 | Inverter | Inverter061_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2269 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 9 | Inverter | Inverter061_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2270 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 9 | Inverter | Inverter061_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2271 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 10 | Inverter | Inverter061_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2272 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 10 | Inverter | Inverter061_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2273 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 11 | Inverter | Inverter061_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 11 | Inverter | Inverter061_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2275 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 12 | Inverter | Inverter061_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 12 | Inverter | Inverter061_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2277 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 13 | Inverter | Inverter061_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2278 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 13 | Inverter | Inverter061_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2279 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 14 | Inverter | Inverter061_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2280 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 14 | Inverter | Inverter061_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2281 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 15 | Inverter | Inverter061_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2282 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 15 | Inverter | Inverter061_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2283 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 16 | Inverter | Inverter061_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2284 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 16 | Inverter | Inverter061_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2285 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 17 | Inverter | Inverter061_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2286 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 17 | Inverter | Inverter061_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2287 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 18 | Inverter | Inverter061_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2288 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 18 | Inverter | Inverter061_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2289 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 19 | Inverter | Inverter061_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2290 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 19 | Inverter | Inverter061_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2291 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current DC Input 20 | Inverter | Inverter061_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC input 20 | Inverter | Inverter061_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2293 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current-AC | Inverter | Inverter061_MODBUS.HR1007_i3Avg_A | Current-AC | 2294 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Current-DC | Inverter | Inverter061_MODBUS.HR1062_idcInput_A | Current-DC | 2295 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Daily Energy Delivered | Inverter | Inverter061_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2296 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power Set Point | Inverter | Inverter061_MODBUS.HR0553_pRef | Real Power Set Point | 2297 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Reactive Power Set Point | Inverter | Inverter061_MODBUS.HR0558_qRef | Reactive Power Set Point | 2298 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Frequency | Inverter | Inverter061_MODBUS.HR1012_f3_Hz | Frequency | 2299 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV061 | Daggett 3_SUB1_INV061_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Insulation Resistance | Inverter | Inverter061_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2300 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Number of DU Channels | Inverter | Inverter061_MODBUS.HR0653_duChannels | Number of DU Channels | 2301 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Number of Running Modules | Inverter | Inverter061_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2302 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Operating State | Inverter | Inverter061_MODBUS.HR1123_currentStatus | Operating State | 2303 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Power Factor | Inverter | Inverter061_MODBUS.HR1011_pf3 | Power Factor | 2304 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV061 | Daggett 3_SUB1_INV061_Ramp Down | Inverter | Inverter061_MODBUS.HR0286_dropGradient_p | Ramp Down | 2305 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Ramp Up | Inverter | Inverter061_MODBUS.HR0282_riseGradient_p | Ramp Up | 2306 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power Delivered | Inverter | Inverter061_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2307 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Reactive Power Delivered | Inverter | Inverter061_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2308 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power | 2309 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Reactive Power | Inverter | Inverter061_MODBUS.HR1009_q3_kvar | Reactive Power | 2310 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Reactive Power Mode | Inverter | Inverter061_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2311 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Reactive Power Set Point Percent | Inverter | Inverter061_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2312 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power AC Percent | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2313 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power-AC | Inverter | Inverter061_MODBUS.HR1008_p3_kW | Real Power-AC | 2314 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Real Power-DC | Inverter | Inverter061_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2315 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Air Intake | Inverter | Inverter061_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2316 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Cabinet | Inverter | Inverter061_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2317 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-IGBT | Inverter | Inverter061_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2318 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Temperature-Module | Inverter | Inverter061_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2319 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage A-B | Inverter | Inverter061_MODBUS.HR1001_vRS_V | Voltage A-B | 2320 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage B-C | Inverter | Inverter061_MODBUS.HR1002_vST_V | Voltage B-C | 2321 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage C-A | Inverter | Inverter061_MODBUS.HR1003_vTR_V | Voltage C-A | 2322 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV061 | Daggett 3_SUB1_INV061_Voltage DC | Inverter | Inverter061_MODBUS.HR1051_vdcBus_V | Voltage DC | 2323 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV061 | Daggett 3_SUB1_INV061_Fault Code 1 | Inverter | Inverter061_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2324 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Warning | Inverter | Inverter061_MODBUS.HRxxxx_currentWarning | Warning | 2325 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Internal Input Status | Inverter | Inverter061_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2326 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Internal Output Status | Inverter | Inverter061_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2327 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Module Fault Code | Inverter | Inverter061_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2328 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Internal Humidity | Inverter | Inverter061_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2329 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Humidity | Inverter | Inverter061_MODBUS.HRxxxx_humidity | Humidity | 2330 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_Comms Fault Time | Inverter | Inverter061_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2331 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Status | Inverter | Inverter061_MODBUS.HRxxxx_M1_status | Module Status | 2332 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 IR | Inverter | Inverter061_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2333 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 IS | Inverter | Inverter061_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2334 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 IT | Inverter | Inverter061_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2335 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2336 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2337 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2338 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2339 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 P | Inverter | Inverter061_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2340 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Q | Inverter | Inverter061_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2341 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2342 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2343 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2344 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2345 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M1 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2346 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Status | Inverter | Inverter061_MODBUS.HRxxxx_M2_status | Module Status | 2347 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 IR | Inverter | Inverter061_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2348 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 IS | Inverter | Inverter061_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2349 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 IT | Inverter | Inverter061_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2350 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2351 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2352 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2353 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2354 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 P | Inverter | Inverter061_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2355 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Q | Inverter | Inverter061_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2356 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2357 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2358 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2359 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2360 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M2 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2361 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Status | Inverter | Inverter061_MODBUS.HRxxxx_M3_status | Module Status | 2362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 IR | Inverter | Inverter061_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2363 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 IS | Inverter | Inverter061_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2364 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 IT | Inverter | Inverter061_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2365 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2366 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2367 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2368 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2369 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 P | Inverter | Inverter061_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2370 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Q | Inverter | Inverter061_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2371 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2372 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2373 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2374 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2375 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M3 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2376 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Status | Inverter | Inverter061_MODBUS.HRxxxx_M4_status | Module Status | 2377 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 IR | Inverter | Inverter061_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2378 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 IS | Inverter | Inverter061_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2379 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 IT | Inverter | Inverter061_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2380 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2381 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2382 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2383 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2384 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 P | Inverter | Inverter061_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2385 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Q | Inverter | Inverter061_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2386 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2387 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2388 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2389 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2390 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M4 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2391 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Status | Inverter | Inverter061_MODBUS.HRxxxx_M5_status | Module Status | 2392 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 IR | Inverter | Inverter061_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2393 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 IS | Inverter | Inverter061_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2394 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 IT | Inverter | Inverter061_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2395 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2396 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2397 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2398 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2399 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 P | Inverter | Inverter061_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2400 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Q | Inverter | Inverter061_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2401 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2402 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2403 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2404 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2405 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M5 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2406 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Status | Inverter | Inverter061_MODBUS.HRxxxx_M6_status | Module Status | 2407 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 IR | Inverter | Inverter061_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2408 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 IS | Inverter | Inverter061_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2409 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 IT | Inverter | Inverter061_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2410 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 IDC | Inverter | Inverter061_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2411 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 VDCP | Inverter | Inverter061_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2412 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 VDCN | Inverter | Inverter061_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2413 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 VDC | Inverter | Inverter061_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2414 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 P | Inverter | Inverter061_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2415 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Q | Inverter | Inverter061_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2416 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Ambient Temp | Inverter | Inverter061_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2417 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Max IGBT Temp | Inverter | Inverter061_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2418 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 IO Status | Inverter | Inverter061_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2419 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Hardware Version | Inverter | Inverter061_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2420 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV061 | Daggett 3_SUB1_INV061_M6 Software Version | Inverter | Inverter061_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2421 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_A Phase Current | Inverter | Inverter062_MODBUS.HR1004_i1_A | A Phase Current | 2422 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_B Phase Current | Inverter | Inverter062_MODBUS.HR1005_i2_A | B Phase Current | 2423 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_C Phase Current | Inverter | Inverter062_MODBUS.HR1006_i3_A | C Phase Current | 2424 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Bus Voltage | Inverter | Inverter062_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2425 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV062 | Daggett 3_SUB1_INV062_Apparent Power | Inverter | Inverter062_MODBUS.HR1010_s3_VA | Apparent Power | 2426 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 1 | Inverter | Inverter062_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2427 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC Input 1 | Inverter | Inverter062_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2428 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 2 | Inverter | Inverter062_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2429 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 2 | Inverter | Inverter062_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2430 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 3 | Inverter | Inverter062_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 3 | Inverter | Inverter062_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2432 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 4 | Inverter | Inverter062_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 4 | Inverter | Inverter062_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2434 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 5 | Inverter | Inverter062_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2435 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 5 | Inverter | Inverter062_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2436 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 6 | Inverter | Inverter062_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2437 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 6 | Inverter | Inverter062_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2438 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 7 | Inverter | Inverter062_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2439 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 7 | Inverter | Inverter062_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2440 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 8 | Inverter | Inverter062_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2441 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 8 | Inverter | Inverter062_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2442 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 9 | Inverter | Inverter062_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2443 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 9 | Inverter | Inverter062_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2444 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 10 | Inverter | Inverter062_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2445 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 10 | Inverter | Inverter062_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2446 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 11 | Inverter | Inverter062_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 11 | Inverter | Inverter062_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2448 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 12 | Inverter | Inverter062_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 12 | Inverter | Inverter062_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2450 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 13 | Inverter | Inverter062_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2451 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 13 | Inverter | Inverter062_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2452 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 14 | Inverter | Inverter062_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2453 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 14 | Inverter | Inverter062_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2454 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 15 | Inverter | Inverter062_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2455 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 15 | Inverter | Inverter062_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2456 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 16 | Inverter | Inverter062_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2457 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 16 | Inverter | Inverter062_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2458 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 17 | Inverter | Inverter062_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2459 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 17 | Inverter | Inverter062_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2460 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 18 | Inverter | Inverter062_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2461 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 18 | Inverter | Inverter062_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2462 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 19 | Inverter | Inverter062_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2463 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 19 | Inverter | Inverter062_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2464 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current DC Input 20 | Inverter | Inverter062_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC input 20 | Inverter | Inverter062_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2466 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current-AC | Inverter | Inverter062_MODBUS.HR1007_i3Avg_A | Current-AC | 2467 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Current-DC | Inverter | Inverter062_MODBUS.HR1062_idcInput_A | Current-DC | 2468 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Daily Energy Delivered | Inverter | Inverter062_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2469 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power Set Point | Inverter | Inverter062_MODBUS.HR0553_pRef | Real Power Set Point | 2470 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Reactive Power Set Point | Inverter | Inverter062_MODBUS.HR0558_qRef | Reactive Power Set Point | 2471 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Frequency | Inverter | Inverter062_MODBUS.HR1012_f3_Hz | Frequency | 2472 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV062 | Daggett 3_SUB1_INV062_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Insulation Resistance | Inverter | Inverter062_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2473 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Number of DU Channels | Inverter | Inverter062_MODBUS.HR0653_duChannels | Number of DU Channels | 2474 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Number of Running Modules | Inverter | Inverter062_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2475 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Operating State | Inverter | Inverter062_MODBUS.HR1123_currentStatus | Operating State | 2476 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Power Factor | Inverter | Inverter062_MODBUS.HR1011_pf3 | Power Factor | 2477 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV062 | Daggett 3_SUB1_INV062_Ramp Down | Inverter | Inverter062_MODBUS.HR0286_dropGradient_p | Ramp Down | 2478 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Ramp Up | Inverter | Inverter062_MODBUS.HR0282_riseGradient_p | Ramp Up | 2479 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power Delivered | Inverter | Inverter062_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2480 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Reactive Power Delivered | Inverter | Inverter062_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2481 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power | 2482 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Reactive Power | Inverter | Inverter062_MODBUS.HR1009_q3_kvar | Reactive Power | 2483 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Reactive Power Mode | Inverter | Inverter062_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2484 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Reactive Power Set Point Percent | Inverter | Inverter062_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2485 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power AC Percent | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2486 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power-AC | Inverter | Inverter062_MODBUS.HR1008_p3_kW | Real Power-AC | 2487 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Real Power-DC | Inverter | Inverter062_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2488 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Air Intake | Inverter | Inverter062_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2489 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Cabinet | Inverter | Inverter062_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2490 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-IGBT | Inverter | Inverter062_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2491 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Temperature-Module | Inverter | Inverter062_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2492 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage A-B | Inverter | Inverter062_MODBUS.HR1002_vRS_V | Voltage A-B | 2493 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage B-C | Inverter | Inverter062_MODBUS.HR1002_vST_V | Voltage B-C | 2494 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage C-A | Inverter | Inverter062_MODBUS.HR1003_vTR_V | Voltage C-A | 2495 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV062 | Daggett 3_SUB1_INV062_Voltage DC | Inverter | Inverter062_MODBUS.HR1051_vdcBus_V | Voltage DC | 2496 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV062 | Daggett 3_SUB1_INV062_Fault Code 1 | Inverter | Inverter062_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2497 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Warning | Inverter | Inverter062_MODBUS.HRxxxx_currentWarning | Warning | 2498 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Internal Input Status | Inverter | Inverter062_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2499 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Internal Output Status | Inverter | Inverter062_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2500 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Module Fault Code | Inverter | Inverter062_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2501 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Internal Humidity | Inverter | Inverter062_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2502 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Humidity | Inverter | Inverter062_MODBUS.HRxxxx_humidity | Humidity | 2503 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_Comms Fault Time | Inverter | Inverter062_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2504 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Status | Inverter | Inverter062_MODBUS.HRxxxx_M1_status | Module Status | 2505 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 IR | Inverter | Inverter062_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2506 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 IS | Inverter | Inverter062_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2507 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 IT | Inverter | Inverter062_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2508 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2509 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2510 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2511 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2512 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 P | Inverter | Inverter062_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2513 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Q | Inverter | Inverter062_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2514 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2515 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2516 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2517 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2518 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M1 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2519 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Status | Inverter | Inverter062_MODBUS.HRxxxx_M2_status | Module Status | 2520 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 IR | Inverter | Inverter062_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2521 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 IS | Inverter | Inverter062_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2522 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 IT | Inverter | Inverter062_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2523 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2524 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2525 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2526 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2527 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 P | Inverter | Inverter062_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2528 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Q | Inverter | Inverter062_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2529 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2530 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2531 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2532 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2533 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M2 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2534 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Status | Inverter | Inverter062_MODBUS.HRxxxx_M3_status | Module Status | 2535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 IR | Inverter | Inverter062_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2536 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 IS | Inverter | Inverter062_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2537 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 IT | Inverter | Inverter062_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2538 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2539 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2540 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2541 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2542 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 P | Inverter | Inverter062_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2543 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Q | Inverter | Inverter062_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2544 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2545 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2546 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2547 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2548 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M3 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2549 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Status | Inverter | Inverter062_MODBUS.HRxxxx_M4_status | Module Status | 2550 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 IR | Inverter | Inverter062_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2551 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 IS | Inverter | Inverter062_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2552 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 IT | Inverter | Inverter062_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2553 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2554 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2555 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2556 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2557 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 P | Inverter | Inverter062_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2558 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Q | Inverter | Inverter062_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2559 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2560 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2561 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2562 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2563 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M4 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2564 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Status | Inverter | Inverter062_MODBUS.HRxxxx_M5_status | Module Status | 2565 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 IR | Inverter | Inverter062_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2566 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 IS | Inverter | Inverter062_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2567 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 IT | Inverter | Inverter062_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2568 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2569 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2570 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2571 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2572 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 P | Inverter | Inverter062_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2573 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Q | Inverter | Inverter062_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2574 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2575 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2576 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2577 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2578 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M5 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2579 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Status | Inverter | Inverter062_MODBUS.HRxxxx_M6_status | Module Status | 2580 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 IR | Inverter | Inverter062_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2581 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 IS | Inverter | Inverter062_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2582 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 IT | Inverter | Inverter062_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2583 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 IDC | Inverter | Inverter062_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2584 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 VDCP | Inverter | Inverter062_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2585 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 VDCN | Inverter | Inverter062_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2586 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 VDC | Inverter | Inverter062_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2587 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 P | Inverter | Inverter062_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2588 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Q | Inverter | Inverter062_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2589 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Ambient Temp | Inverter | Inverter062_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2590 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Max IGBT Temp | Inverter | Inverter062_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2591 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 IO Status | Inverter | Inverter062_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2592 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Hardware Version | Inverter | Inverter062_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2593 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV062 | Daggett 3_SUB1_INV062_M6 Software Version | Inverter | Inverter062_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2594 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_A Phase Current | Inverter | Inverter063_MODBUS.HR1004_i1_A | A Phase Current | 2595 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_B Phase Current | Inverter | Inverter063_MODBUS.HR1005_i2_A | B Phase Current | 2596 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_C Phase Current | Inverter | Inverter063_MODBUS.HR1006_i3_A | C Phase Current | 2597 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Bus Voltage | Inverter | Inverter063_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2598 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV063 | Daggett 3_SUB1_INV063_Apparent Power | Inverter | Inverter063_MODBUS.HR1010_s3_VA | Apparent Power | 2599 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 1 | Inverter | Inverter063_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2600 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC Input 1 | Inverter | Inverter063_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2601 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 2 | Inverter | Inverter063_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2602 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 2 | Inverter | Inverter063_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2603 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 3 | Inverter | Inverter063_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 3 | Inverter | Inverter063_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2605 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 4 | Inverter | Inverter063_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 4 | Inverter | Inverter063_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2607 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 5 | Inverter | Inverter063_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2608 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 5 | Inverter | Inverter063_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2609 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 6 | Inverter | Inverter063_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2610 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 6 | Inverter | Inverter063_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2611 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 7 | Inverter | Inverter063_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2612 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 7 | Inverter | Inverter063_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2613 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 8 | Inverter | Inverter063_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2614 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 8 | Inverter | Inverter063_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2615 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 9 | Inverter | Inverter063_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2616 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 9 | Inverter | Inverter063_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2617 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 10 | Inverter | Inverter063_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2618 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 10 | Inverter | Inverter063_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2619 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 11 | Inverter | Inverter063_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 11 | Inverter | Inverter063_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2621 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 12 | Inverter | Inverter063_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 12 | Inverter | Inverter063_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2623 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 13 | Inverter | Inverter063_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2624 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 13 | Inverter | Inverter063_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2625 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 14 | Inverter | Inverter063_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2626 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 14 | Inverter | Inverter063_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2627 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 15 | Inverter | Inverter063_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2628 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 15 | Inverter | Inverter063_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2629 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 16 | Inverter | Inverter063_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2630 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 16 | Inverter | Inverter063_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2631 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 17 | Inverter | Inverter063_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2632 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 17 | Inverter | Inverter063_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2633 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 18 | Inverter | Inverter063_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2634 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 18 | Inverter | Inverter063_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2635 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 19 | Inverter | Inverter063_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2636 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 19 | Inverter | Inverter063_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2637 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current DC Input 20 | Inverter | Inverter063_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC input 20 | Inverter | Inverter063_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2639 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current-AC | Inverter | Inverter063_MODBUS.HR1007_i3Avg_A | Current-AC | 2640 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Current-DC | Inverter | Inverter063_MODBUS.HR1062_idcInput_A | Current-DC | 2641 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Daily Energy Delivered | Inverter | Inverter063_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2642 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power Set Point | Inverter | Inverter063_MODBUS.HR0553_pRef | Real Power Set Point | 2643 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Reactive Power Set Point | Inverter | Inverter063_MODBUS.HR0558_qRef | Reactive Power Set Point | 2644 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Frequency | Inverter | Inverter063_MODBUS.HR1012_f3_Hz | Frequency | 2645 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV063 | Daggett 3_SUB1_INV063_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Insulation Resistance | Inverter | Inverter063_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2646 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Number of DU Channels | Inverter | Inverter063_MODBUS.HR0653_duChannels | Number of DU Channels | 2647 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Number of Running Modules | Inverter | Inverter063_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2648 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Operating State | Inverter | Inverter063_MODBUS.HR1123_currentStatus | Operating State | 2649 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Power Factor | Inverter | Inverter063_MODBUS.HR1011_pf3 | Power Factor | 2650 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV063 | Daggett 3_SUB1_INV063_Ramp Down | Inverter | Inverter063_MODBUS.HR0286_dropGradient_p | Ramp Down | 2651 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Ramp Up | Inverter | Inverter063_MODBUS.HR0282_riseGradient_p | Ramp Up | 2652 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power Delivered | Inverter | Inverter063_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2653 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Reactive Power Delivered | Inverter | Inverter063_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2654 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power | 2655 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Reactive Power | Inverter | Inverter063_MODBUS.HR1009_q3_kvar | Reactive Power | 2656 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Reactive Power Mode | Inverter | Inverter063_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2657 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Reactive Power Set Point Percent | Inverter | Inverter063_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2658 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power AC Percent | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2659 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power-AC | Inverter | Inverter063_MODBUS.HR1008_p3_kW | Real Power-AC | 2660 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Real Power-DC | Inverter | Inverter063_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2661 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Air Intake | Inverter | Inverter063_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2662 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Cabinet | Inverter | Inverter063_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2663 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-IGBT | Inverter | Inverter063_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2664 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Temperature-Module | Inverter | Inverter063_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2665 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage A-B | Inverter | Inverter063_MODBUS.HR1003_vRS_V | Voltage A-B | 2666 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage B-C | Inverter | Inverter063_MODBUS.HR1002_vST_V | Voltage B-C | 2667 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage C-A | Inverter | Inverter063_MODBUS.HR1003_vTR_V | Voltage C-A | 2668 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV063 | Daggett 3_SUB1_INV063_Voltage DC | Inverter | Inverter063_MODBUS.HR1051_vdcBus_V | Voltage DC | 2669 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV063 | Daggett 3_SUB1_INV063_Fault Code 1 | Inverter | Inverter063_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2670 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Warning | Inverter | Inverter063_MODBUS.HRxxxx_currentWarning | Warning | 2671 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Internal Input Status | Inverter | Inverter063_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2672 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Internal Output Status | Inverter | Inverter063_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2673 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Module Fault Code | Inverter | Inverter063_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2674 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Internal Humidity | Inverter | Inverter063_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2675 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Humidity | Inverter | Inverter063_MODBUS.HRxxxx_humidity | Humidity | 2676 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_Comms Fault Time | Inverter | Inverter063_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2677 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Status | Inverter | Inverter063_MODBUS.HRxxxx_M1_status | Module Status | 2678 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 IR | Inverter | Inverter063_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2679 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 IS | Inverter | Inverter063_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2680 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 IT | Inverter | Inverter063_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2681 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2682 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2683 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2684 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2685 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 P | Inverter | Inverter063_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2686 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Q | Inverter | Inverter063_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2687 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2688 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2689 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2690 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2691 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M1 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2692 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Status | Inverter | Inverter063_MODBUS.HRxxxx_M2_status | Module Status | 2693 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 IR | Inverter | Inverter063_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2694 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 IS | Inverter | Inverter063_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2695 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 IT | Inverter | Inverter063_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2696 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2697 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2698 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2699 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2700 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 P | Inverter | Inverter063_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2701 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Q | Inverter | Inverter063_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2702 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2703 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2704 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2705 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2706 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M2 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2707 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Status | Inverter | Inverter063_MODBUS.HRxxxx_M3_status | Module Status | 2708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 IR | Inverter | Inverter063_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2709 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 IS | Inverter | Inverter063_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2710 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 IT | Inverter | Inverter063_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2711 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2712 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2713 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2714 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2715 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 P | Inverter | Inverter063_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2716 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Q | Inverter | Inverter063_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2717 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2718 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2719 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2720 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2721 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M3 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2722 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Status | Inverter | Inverter063_MODBUS.HRxxxx_M4_status | Module Status | 2723 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 IR | Inverter | Inverter063_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2724 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 IS | Inverter | Inverter063_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2725 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 IT | Inverter | Inverter063_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2726 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2727 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2728 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2729 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2730 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 P | Inverter | Inverter063_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2731 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Q | Inverter | Inverter063_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2732 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2733 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2734 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2735 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2736 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M4 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2737 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Status | Inverter | Inverter063_MODBUS.HRxxxx_M5_status | Module Status | 2738 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 IR | Inverter | Inverter063_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2739 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 IS | Inverter | Inverter063_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2740 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 IT | Inverter | Inverter063_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2741 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2742 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2743 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2744 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2745 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 P | Inverter | Inverter063_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2746 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Q | Inverter | Inverter063_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2747 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2748 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2749 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2750 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2751 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M5 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2752 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Status | Inverter | Inverter063_MODBUS.HRxxxx_M6_status | Module Status | 2753 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 IR | Inverter | Inverter063_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2754 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 IS | Inverter | Inverter063_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2755 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 IT | Inverter | Inverter063_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2756 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 IDC | Inverter | Inverter063_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2757 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 VDCP | Inverter | Inverter063_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2758 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 VDCN | Inverter | Inverter063_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2759 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 VDC | Inverter | Inverter063_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2760 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 P | Inverter | Inverter063_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2761 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Q | Inverter | Inverter063_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2762 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Ambient Temp | Inverter | Inverter063_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2763 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Max IGBT Temp | Inverter | Inverter063_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2764 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 IO Status | Inverter | Inverter063_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2765 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Hardware Version | Inverter | Inverter063_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2766 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV063 | Daggett 3_SUB1_INV063_M6 Software Version | Inverter | Inverter063_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2767 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_A Phase Current | Inverter | Inverter064_MODBUS.HR1004_i1_A | A Phase Current | 2768 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_B Phase Current | Inverter | Inverter064_MODBUS.HR1005_i2_A | B Phase Current | 2769 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_C Phase Current | Inverter | Inverter064_MODBUS.HR1006_i3_A | C Phase Current | 2770 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Bus Voltage | Inverter | Inverter064_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2771 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV064 | Daggett 3_SUB1_INV064_Apparent Power | Inverter | Inverter064_MODBUS.HR1010_s3_VA | Apparent Power | 2772 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 1 | Inverter | Inverter064_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2773 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC Input 1 | Inverter | Inverter064_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2774 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 2 | Inverter | Inverter064_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2775 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 2 | Inverter | Inverter064_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2776 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 3 | Inverter | Inverter064_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 3 | Inverter | Inverter064_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2778 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 4 | Inverter | Inverter064_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 4 | Inverter | Inverter064_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2780 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 5 | Inverter | Inverter064_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2781 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 5 | Inverter | Inverter064_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2782 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 6 | Inverter | Inverter064_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2783 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 6 | Inverter | Inverter064_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2784 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 7 | Inverter | Inverter064_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2785 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 7 | Inverter | Inverter064_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2786 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 8 | Inverter | Inverter064_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2787 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 8 | Inverter | Inverter064_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2788 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 9 | Inverter | Inverter064_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2789 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 9 | Inverter | Inverter064_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2790 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 10 | Inverter | Inverter064_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2791 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 10 | Inverter | Inverter064_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2792 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 11 | Inverter | Inverter064_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 11 | Inverter | Inverter064_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2794 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 12 | Inverter | Inverter064_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 12 | Inverter | Inverter064_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2796 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 13 | Inverter | Inverter064_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2797 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 13 | Inverter | Inverter064_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2798 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 14 | Inverter | Inverter064_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2799 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 14 | Inverter | Inverter064_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2800 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 15 | Inverter | Inverter064_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2801 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 15 | Inverter | Inverter064_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2802 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 16 | Inverter | Inverter064_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2803 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 16 | Inverter | Inverter064_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2804 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 17 | Inverter | Inverter064_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2805 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 17 | Inverter | Inverter064_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2806 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 18 | Inverter | Inverter064_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2807 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 18 | Inverter | Inverter064_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2808 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 19 | Inverter | Inverter064_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2809 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 19 | Inverter | Inverter064_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2810 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current DC Input 20 | Inverter | Inverter064_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC input 20 | Inverter | Inverter064_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2812 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current-AC | Inverter | Inverter064_MODBUS.HR1007_i3Avg_A | Current-AC | 2813 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Current-DC | Inverter | Inverter064_MODBUS.HR1062_idcInput_A | Current-DC | 2814 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Daily Energy Delivered | Inverter | Inverter064_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2815 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power Set Point | Inverter | Inverter064_MODBUS.HR0553_pRef | Real Power Set Point | 2816 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Reactive Power Set Point | Inverter | Inverter064_MODBUS.HR0558_qRef | Reactive Power Set Point | 2817 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Frequency | Inverter | Inverter064_MODBUS.HR1012_f3_Hz | Frequency | 2818 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV064 | Daggett 3_SUB1_INV064_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Insulation Resistance | Inverter | Inverter064_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2819 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Number of DU Channels | Inverter | Inverter064_MODBUS.HR0653_duChannels | Number of DU Channels | 2820 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Number of Running Modules | Inverter | Inverter064_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2821 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Operating State | Inverter | Inverter064_MODBUS.HR1123_currentStatus | Operating State | 2822 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Power Factor | Inverter | Inverter064_MODBUS.HR1011_pf3 | Power Factor | 2823 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV064 | Daggett 3_SUB1_INV064_Ramp Down | Inverter | Inverter064_MODBUS.HR0286_dropGradient_p | Ramp Down | 2824 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Ramp Up | Inverter | Inverter064_MODBUS.HR0282_riseGradient_p | Ramp Up | 2825 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power Delivered | Inverter | Inverter064_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2826 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Reactive Power Delivered | Inverter | Inverter064_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 2827 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power | 2828 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Reactive Power | Inverter | Inverter064_MODBUS.HR1009_q3_kvar | Reactive Power | 2829 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Reactive Power Mode | Inverter | Inverter064_MODBUS.HR0552_qControlMode | Reactive Power Mode | 2830 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Reactive Power Set Point Percent | Inverter | Inverter064_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 2831 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power AC Percent | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power AC Percent | 2832 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power-AC | Inverter | Inverter064_MODBUS.HR1008_p3_kW | Real Power-AC | 2833 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Real Power-DC | Inverter | Inverter064_MODBUS.HR1061_pdcInput_W | Real Power-DC | 2834 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Air Intake | Inverter | Inverter064_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 2835 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Cabinet | Inverter | Inverter064_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 2836 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-IGBT | Inverter | Inverter064_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 2837 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Temperature-Module | Inverter | Inverter064_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 2838 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage A-B | Inverter | Inverter064_MODBUS.HR1004_vRS_V | Voltage A-B | 2839 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage B-C | Inverter | Inverter064_MODBUS.HR1002_vST_V | Voltage B-C | 2840 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage C-A | Inverter | Inverter064_MODBUS.HR1003_vTR_V | Voltage C-A | 2841 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV064 | Daggett 3_SUB1_INV064_Voltage DC | Inverter | Inverter064_MODBUS.HR1051_vdcBus_V | Voltage DC | 2842 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV064 | Daggett 3_SUB1_INV064_Fault Code 1 | Inverter | Inverter064_MODBUS.HRxxxx_currentFault | Fault Code 1 | 2843 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Warning | Inverter | Inverter064_MODBUS.HRxxxx_currentWarning | Warning | 2844 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Internal Input Status | Inverter | Inverter064_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 2845 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Internal Output Status | Inverter | Inverter064_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 2846 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Module Fault Code | Inverter | Inverter064_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 2847 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Internal Humidity | Inverter | Inverter064_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 2848 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Humidity | Inverter | Inverter064_MODBUS.HRxxxx_humidity | Humidity | 2849 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_Comms Fault Time | Inverter | Inverter064_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 2850 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Status | Inverter | Inverter064_MODBUS.HRxxxx_M1_status | Module Status | 2851 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 IR | Inverter | Inverter064_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 2852 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 IS | Inverter | Inverter064_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 2853 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 IT | Inverter | Inverter064_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 2854 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 2855 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 2856 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 2857 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 2858 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 P | Inverter | Inverter064_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 2859 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Q | Inverter | Inverter064_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 2860 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 2861 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 2862 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 2863 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 2864 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M1 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 2865 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Status | Inverter | Inverter064_MODBUS.HRxxxx_M2_status | Module Status | 2866 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 IR | Inverter | Inverter064_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 2867 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 IS | Inverter | Inverter064_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 2868 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 IT | Inverter | Inverter064_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 2869 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 2870 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 2871 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 2872 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 2873 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 P | Inverter | Inverter064_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 2874 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Q | Inverter | Inverter064_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 2875 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 2876 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 2877 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 2878 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 2879 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M2 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 2880 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Status | Inverter | Inverter064_MODBUS.HRxxxx_M3_status | Module Status | 2881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 IR | Inverter | Inverter064_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 2882 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 IS | Inverter | Inverter064_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 2883 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 IT | Inverter | Inverter064_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 2884 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 2885 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 2886 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 2887 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 2888 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 P | Inverter | Inverter064_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 2889 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Q | Inverter | Inverter064_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 2890 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 2891 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 2892 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 2893 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 2894 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M3 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 2895 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Status | Inverter | Inverter064_MODBUS.HRxxxx_M4_status | Module Status | 2896 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 IR | Inverter | Inverter064_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 2897 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 IS | Inverter | Inverter064_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 2898 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 IT | Inverter | Inverter064_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 2899 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 2900 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 2901 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 2902 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 2903 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 P | Inverter | Inverter064_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 2904 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Q | Inverter | Inverter064_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 2905 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 2906 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 2907 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 2908 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 2909 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M4 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 2910 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Status | Inverter | Inverter064_MODBUS.HRxxxx_M5_status | Module Status | 2911 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 IR | Inverter | Inverter064_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 2912 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 IS | Inverter | Inverter064_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 2913 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 IT | Inverter | Inverter064_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 2914 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 2915 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 2916 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 2917 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 2918 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 P | Inverter | Inverter064_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 2919 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Q | Inverter | Inverter064_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 2920 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 2921 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 2922 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 2923 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 2924 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M5 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 2925 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Status | Inverter | Inverter064_MODBUS.HRxxxx_M6_status | Module Status | 2926 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 IR | Inverter | Inverter064_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 2927 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 IS | Inverter | Inverter064_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 2928 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 IT | Inverter | Inverter064_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 2929 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 IDC | Inverter | Inverter064_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 2930 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 VDCP | Inverter | Inverter064_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 2931 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 VDCN | Inverter | Inverter064_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 2932 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 VDC | Inverter | Inverter064_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 2933 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 P | Inverter | Inverter064_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 2934 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Q | Inverter | Inverter064_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 2935 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Ambient Temp | Inverter | Inverter064_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 2936 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Max IGBT Temp | Inverter | Inverter064_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 2937 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 IO Status | Inverter | Inverter064_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 2938 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Hardware Version | Inverter | Inverter064_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 2939 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV064 | Daggett 3_SUB1_INV064_M6 Software Version | Inverter | Inverter064_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 2940 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_A Phase Current | Inverter | Inverter065_MODBUS.HR1004_i1_A | A Phase Current | 2941 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_B Phase Current | Inverter | Inverter065_MODBUS.HR1005_i2_A | B Phase Current | 2942 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_C Phase Current | Inverter | Inverter065_MODBUS.HR1006_i3_A | C Phase Current | 2943 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Bus Voltage | Inverter | Inverter065_MODBUS.HR1051_vdcBus_V | Bus Voltage | 2944 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV065 | Daggett 3_SUB1_INV065_Apparent Power | Inverter | Inverter065_MODBUS.HR1010_s3_VA | Apparent Power | 2945 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 1 | Inverter | Inverter065_MODBUS.HR5805_du1_idc_A | Current DC Input# | 2946 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC Input 1 | Inverter | Inverter065_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 2947 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 2 | Inverter | Inverter065_MODBUS.HR5811_du2_idc_A | Current DC Input# | 2948 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 2 | Inverter | Inverter065_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 2949 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 3 | Inverter | Inverter065_MODBUS.HR5817_du3_idc_A | Current DC Input# | 2950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 3 | Inverter | Inverter065_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 2951 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 4 | Inverter | Inverter065_MODBUS.HR5823_du4_idc_A | Current DC Input# | 2952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 4 | Inverter | Inverter065_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 2953 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 5 | Inverter | Inverter065_MODBUS.HR5829_du5_idc_A | Current DC Input# | 2954 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 5 | Inverter | Inverter065_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 2955 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 6 | Inverter | Inverter065_MODBUS.HR5835_du6_idc_A | Current DC Input# | 2956 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 6 | Inverter | Inverter065_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 2957 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 7 | Inverter | Inverter065_MODBUS.HR5841_du7_idc_A | Current DC Input# | 2958 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 7 | Inverter | Inverter065_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 2959 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 8 | Inverter | Inverter065_MODBUS.HR5847_du8_idc_A | Current DC Input# | 2960 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 8 | Inverter | Inverter065_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 2961 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 9 | Inverter | Inverter065_MODBUS.HR5853_du9_idc_A | Current DC Input# | 2962 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 9 | Inverter | Inverter065_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 2963 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 10 | Inverter | Inverter065_MODBUS.HR5859_du10_idc_A | Current DC Input# | 2964 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 10 | Inverter | Inverter065_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 2965 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 11 | Inverter | Inverter065_MODBUS.HR5865_du11_idc_A | Current DC Input# | 2966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 11 | Inverter | Inverter065_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 2967 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 12 | Inverter | Inverter065_MODBUS.HR5871_du12_idc_A | Current DC Input# | 2968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 12 | Inverter | Inverter065_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 2969 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 13 | Inverter | Inverter065_MODBUS.HR5877_du13_idc_A | Current DC Input# | 2970 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 13 | Inverter | Inverter065_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 2971 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 14 | Inverter | Inverter065_MODBUS.HR5883_du14_idc_A | Current DC Input# | 2972 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 14 | Inverter | Inverter065_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 2973 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 15 | Inverter | Inverter065_MODBUS.HR5889_du15_idc_A | Current DC Input# | 2974 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 15 | Inverter | Inverter065_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 2975 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 16 | Inverter | Inverter065_MODBUS.HR5895_du16_idc_A | Current DC Input# | 2976 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 16 | Inverter | Inverter065_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 2977 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 17 | Inverter | Inverter065_MODBUS.HR5901_du17_idc_A | Current DC Input# | 2978 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 17 | Inverter | Inverter065_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 2979 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 18 | Inverter | Inverter065_MODBUS.HR5907_du18_idc_A | Current DC Input# | 2980 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 18 | Inverter | Inverter065_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 2981 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 19 | Inverter | Inverter065_MODBUS.HR5913_du19_idc_A | Current DC Input# | 2982 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 19 | Inverter | Inverter065_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 2983 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current DC Input 20 | Inverter | Inverter065_MODBUS.HR5919_du20_idc_A | Current DC Input# | 2984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC input 20 | Inverter | Inverter065_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 2985 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current-AC | Inverter | Inverter065_MODBUS.HR1007_i3Avg_A | Current-AC | 2986 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Current-DC | Inverter | Inverter065_MODBUS.HR1062_idcInput_A | Current-DC | 2987 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Daily Energy Delivered | Inverter | Inverter065_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 2988 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power Set Point | Inverter | Inverter065_MODBUS.HR0553_pRef | Real Power Set Point | 2989 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Reactive Power Set Point | Inverter | Inverter065_MODBUS.HR0558_qRef | Reactive Power Set Point | 2990 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Frequency | Inverter | Inverter065_MODBUS.HR1012_f3_Hz | Frequency | 2991 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV065 | Daggett 3_SUB1_INV065_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Insulation Resistance | Inverter | Inverter065_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 2992 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Number of DU Channels | Inverter | Inverter065_MODBUS.HR0653_duChannels | Number of DU Channels | 2993 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Number of Running Modules | Inverter | Inverter065_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 2994 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Operating State | Inverter | Inverter065_MODBUS.HR1123_currentStatus | Operating State | 2995 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Power Factor | Inverter | Inverter065_MODBUS.HR1011_pf3 | Power Factor | 2996 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV065 | Daggett 3_SUB1_INV065_Ramp Down | Inverter | Inverter065_MODBUS.HR0286_dropGradient_p | Ramp Down | 2997 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Ramp Up | Inverter | Inverter065_MODBUS.HR0282_riseGradient_p | Ramp Up | 2998 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power Delivered | Inverter | Inverter065_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 2999 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Reactive Power Delivered | Inverter | Inverter065_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3000 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power | 3001 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Reactive Power | Inverter | Inverter065_MODBUS.HR1009_q3_kvar | Reactive Power | 3002 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Reactive Power Mode | Inverter | Inverter065_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3003 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Reactive Power Set Point Percent | Inverter | Inverter065_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3004 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power AC Percent | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3005 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power-AC | Inverter | Inverter065_MODBUS.HR1008_p3_kW | Real Power-AC | 3006 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Real Power-DC | Inverter | Inverter065_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3007 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Air Intake | Inverter | Inverter065_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3008 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Cabinet | Inverter | Inverter065_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3009 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-IGBT | Inverter | Inverter065_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3010 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Temperature-Module | Inverter | Inverter065_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3011 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage A-B | Inverter | Inverter065_MODBUS.HR1005_vRS_V | Voltage A-B | 3012 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage B-C | Inverter | Inverter065_MODBUS.HR1002_vST_V | Voltage B-C | 3013 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage C-A | Inverter | Inverter065_MODBUS.HR1003_vTR_V | Voltage C-A | 3014 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV065 | Daggett 3_SUB1_INV065_Voltage DC | Inverter | Inverter065_MODBUS.HR1051_vdcBus_V | Voltage DC | 3015 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV065 | Daggett 3_SUB1_INV065_Fault Code 1 | Inverter | Inverter065_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3016 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Warning | Inverter | Inverter065_MODBUS.HRxxxx_currentWarning | Warning | 3017 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Internal Input Status | Inverter | Inverter065_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3018 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Internal Output Status | Inverter | Inverter065_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3019 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Module Fault Code | Inverter | Inverter065_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3020 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Internal Humidity | Inverter | Inverter065_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3021 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Humidity | Inverter | Inverter065_MODBUS.HRxxxx_humidity | Humidity | 3022 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_Comms Fault Time | Inverter | Inverter065_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3023 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Status | Inverter | Inverter065_MODBUS.HRxxxx_M1_status | Module Status | 3024 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 IR | Inverter | Inverter065_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3025 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 IS | Inverter | Inverter065_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3026 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 IT | Inverter | Inverter065_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3027 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3028 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3029 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3030 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3031 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 P | Inverter | Inverter065_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3032 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Q | Inverter | Inverter065_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3033 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3034 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3035 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3036 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3037 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M1 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3038 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Status | Inverter | Inverter065_MODBUS.HRxxxx_M2_status | Module Status | 3039 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 IR | Inverter | Inverter065_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3040 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 IS | Inverter | Inverter065_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3041 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 IT | Inverter | Inverter065_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3042 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3043 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3044 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3045 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3046 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 P | Inverter | Inverter065_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3047 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Q | Inverter | Inverter065_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3048 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3049 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3050 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3051 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3052 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M2 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3053 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Status | Inverter | Inverter065_MODBUS.HRxxxx_M3_status | Module Status | 3054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 IR | Inverter | Inverter065_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3055 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 IS | Inverter | Inverter065_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3056 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 IT | Inverter | Inverter065_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3057 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3058 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3059 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3060 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3061 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 P | Inverter | Inverter065_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3062 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Q | Inverter | Inverter065_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3063 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3064 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3065 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3066 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3067 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M3 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3068 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Status | Inverter | Inverter065_MODBUS.HRxxxx_M4_status | Module Status | 3069 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 IR | Inverter | Inverter065_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3070 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 IS | Inverter | Inverter065_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3071 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 IT | Inverter | Inverter065_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3072 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3073 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3074 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3075 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3076 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 P | Inverter | Inverter065_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3077 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Q | Inverter | Inverter065_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3078 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3079 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3080 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3081 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3082 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M4 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3083 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Status | Inverter | Inverter065_MODBUS.HRxxxx_M5_status | Module Status | 3084 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 IR | Inverter | Inverter065_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3085 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 IS | Inverter | Inverter065_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3086 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 IT | Inverter | Inverter065_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3087 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3088 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3089 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3090 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3091 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 P | Inverter | Inverter065_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3092 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Q | Inverter | Inverter065_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3093 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3094 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3095 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3096 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3097 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M5 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3098 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Status | Inverter | Inverter065_MODBUS.HRxxxx_M6_status | Module Status | 3099 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 IR | Inverter | Inverter065_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3100 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 IS | Inverter | Inverter065_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3101 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 IT | Inverter | Inverter065_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3102 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 IDC | Inverter | Inverter065_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3103 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 VDCP | Inverter | Inverter065_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3104 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 VDCN | Inverter | Inverter065_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3105 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 VDC | Inverter | Inverter065_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3106 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 P | Inverter | Inverter065_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3107 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Q | Inverter | Inverter065_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3108 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Ambient Temp | Inverter | Inverter065_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3109 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Max IGBT Temp | Inverter | Inverter065_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3110 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 IO Status | Inverter | Inverter065_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3111 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Hardware Version | Inverter | Inverter065_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3112 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV065 | Daggett 3_SUB1_INV065_M6 Software Version | Inverter | Inverter065_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3113 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_A Phase Current | Inverter | Inverter066_MODBUS.HR1004_i1_A | A Phase Current | 3114 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_B Phase Current | Inverter | Inverter066_MODBUS.HR1005_i2_A | B Phase Current | 3115 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_C Phase Current | Inverter | Inverter066_MODBUS.HR1006_i3_A | C Phase Current | 3116 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Bus Voltage | Inverter | Inverter066_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3117 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV066 | Daggett 3_SUB1_INV066_Apparent Power | Inverter | Inverter066_MODBUS.HR1010_s3_VA | Apparent Power | 3118 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 1 | Inverter | Inverter066_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3119 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC Input 1 | Inverter | Inverter066_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3120 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 2 | Inverter | Inverter066_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3121 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 2 | Inverter | Inverter066_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3122 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 3 | Inverter | Inverter066_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 3 | Inverter | Inverter066_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3124 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 4 | Inverter | Inverter066_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 4 | Inverter | Inverter066_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3126 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 5 | Inverter | Inverter066_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3127 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 5 | Inverter | Inverter066_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3128 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 6 | Inverter | Inverter066_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3129 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 6 | Inverter | Inverter066_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3130 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 7 | Inverter | Inverter066_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3131 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 7 | Inverter | Inverter066_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3132 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 8 | Inverter | Inverter066_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3133 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 8 | Inverter | Inverter066_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3134 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 9 | Inverter | Inverter066_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3135 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 9 | Inverter | Inverter066_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3136 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 10 | Inverter | Inverter066_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3137 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 10 | Inverter | Inverter066_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3138 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 11 | Inverter | Inverter066_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 11 | Inverter | Inverter066_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3140 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 12 | Inverter | Inverter066_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 12 | Inverter | Inverter066_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3142 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 13 | Inverter | Inverter066_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3143 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 13 | Inverter | Inverter066_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3144 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 14 | Inverter | Inverter066_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3145 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 14 | Inverter | Inverter066_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3146 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 15 | Inverter | Inverter066_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3147 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 15 | Inverter | Inverter066_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3148 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 16 | Inverter | Inverter066_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3149 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 16 | Inverter | Inverter066_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3150 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 17 | Inverter | Inverter066_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3151 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 17 | Inverter | Inverter066_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3152 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 18 | Inverter | Inverter066_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3153 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 18 | Inverter | Inverter066_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3154 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 19 | Inverter | Inverter066_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3155 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 19 | Inverter | Inverter066_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3156 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current DC Input 20 | Inverter | Inverter066_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC input 20 | Inverter | Inverter066_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3158 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current-AC | Inverter | Inverter066_MODBUS.HR1007_i3Avg_A | Current-AC | 3159 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Current-DC | Inverter | Inverter066_MODBUS.HR1062_idcInput_A | Current-DC | 3160 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Daily Energy Delivered | Inverter | Inverter066_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3161 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power Set Point | Inverter | Inverter066_MODBUS.HR0553_pRef | Real Power Set Point | 3162 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Reactive Power Set Point | Inverter | Inverter066_MODBUS.HR0558_qRef | Reactive Power Set Point | 3163 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Frequency | Inverter | Inverter066_MODBUS.HR1012_f3_Hz | Frequency | 3164 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV066 | Daggett 3_SUB1_INV066_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Insulation Resistance | Inverter | Inverter066_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3165 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Number of DU Channels | Inverter | Inverter066_MODBUS.HR0653_duChannels | Number of DU Channels | 3166 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Number of Running Modules | Inverter | Inverter066_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3167 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Operating State | Inverter | Inverter066_MODBUS.HR1123_currentStatus | Operating State | 3168 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Power Factor | Inverter | Inverter066_MODBUS.HR1011_pf3 | Power Factor | 3169 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV066 | Daggett 3_SUB1_INV066_Ramp Down | Inverter | Inverter066_MODBUS.HR0286_dropGradient_p | Ramp Down | 3170 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Ramp Up | Inverter | Inverter066_MODBUS.HR0282_riseGradient_p | Ramp Up | 3171 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power Delivered | Inverter | Inverter066_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3172 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Reactive Power Delivered | Inverter | Inverter066_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3173 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power | 3174 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Reactive Power | Inverter | Inverter066_MODBUS.HR1009_q3_kvar | Reactive Power | 3175 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Reactive Power Mode | Inverter | Inverter066_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3176 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Reactive Power Set Point Percent | Inverter | Inverter066_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3177 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power AC Percent | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3178 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power-AC | Inverter | Inverter066_MODBUS.HR1008_p3_kW | Real Power-AC | 3179 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Real Power-DC | Inverter | Inverter066_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3180 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Air Intake | Inverter | Inverter066_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3181 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Cabinet | Inverter | Inverter066_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3182 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-IGBT | Inverter | Inverter066_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3183 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Temperature-Module | Inverter | Inverter066_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3184 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage A-B | Inverter | Inverter066_MODBUS.HR1006_vRS_V | Voltage A-B | 3185 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage B-C | Inverter | Inverter066_MODBUS.HR1002_vST_V | Voltage B-C | 3186 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage C-A | Inverter | Inverter066_MODBUS.HR1003_vTR_V | Voltage C-A | 3187 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV066 | Daggett 3_SUB1_INV066_Voltage DC | Inverter | Inverter066_MODBUS.HR1051_vdcBus_V | Voltage DC | 3188 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV066 | Daggett 3_SUB1_INV066_Fault Code 1 | Inverter | Inverter066_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3189 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Warning | Inverter | Inverter066_MODBUS.HRxxxx_currentWarning | Warning | 3190 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Internal Input Status | Inverter | Inverter066_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3191 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Internal Output Status | Inverter | Inverter066_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3192 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Module Fault Code | Inverter | Inverter066_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3193 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Internal Humidity | Inverter | Inverter066_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3194 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Humidity | Inverter | Inverter066_MODBUS.HRxxxx_humidity | Humidity | 3195 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_Comms Fault Time | Inverter | Inverter066_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3196 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Status | Inverter | Inverter066_MODBUS.HRxxxx_M1_status | Module Status | 3197 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 IR | Inverter | Inverter066_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3198 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 IS | Inverter | Inverter066_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3199 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 IT | Inverter | Inverter066_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3200 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3201 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3202 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3203 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3204 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 P | Inverter | Inverter066_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3205 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Q | Inverter | Inverter066_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3206 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3207 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3208 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3209 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3210 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M1 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3211 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Status | Inverter | Inverter066_MODBUS.HRxxxx_M2_status | Module Status | 3212 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 IR | Inverter | Inverter066_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3213 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 IS | Inverter | Inverter066_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3214 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 IT | Inverter | Inverter066_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3215 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3216 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3217 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3218 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3219 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 P | Inverter | Inverter066_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3220 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Q | Inverter | Inverter066_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3221 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3222 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3223 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3224 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3225 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M2 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3226 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Status | Inverter | Inverter066_MODBUS.HRxxxx_M3_status | Module Status | 3227 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 IR | Inverter | Inverter066_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3228 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 IS | Inverter | Inverter066_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3229 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 IT | Inverter | Inverter066_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3230 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3231 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3232 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3233 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3234 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 P | Inverter | Inverter066_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3235 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Q | Inverter | Inverter066_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3236 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3237 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3238 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3239 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3240 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M3 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3241 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Status | Inverter | Inverter066_MODBUS.HRxxxx_M4_status | Module Status | 3242 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 IR | Inverter | Inverter066_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3243 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 IS | Inverter | Inverter066_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3244 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 IT | Inverter | Inverter066_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3245 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3246 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3247 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3248 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3249 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 P | Inverter | Inverter066_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3250 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Q | Inverter | Inverter066_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3251 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3252 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3253 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3254 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3255 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M4 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3256 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Status | Inverter | Inverter066_MODBUS.HRxxxx_M5_status | Module Status | 3257 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 IR | Inverter | Inverter066_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3258 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 IS | Inverter | Inverter066_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3259 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 IT | Inverter | Inverter066_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3260 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3261 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3262 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3263 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3264 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 P | Inverter | Inverter066_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3265 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Q | Inverter | Inverter066_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3266 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3267 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3268 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3269 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3270 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M5 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3271 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Status | Inverter | Inverter066_MODBUS.HRxxxx_M6_status | Module Status | 3272 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 IR | Inverter | Inverter066_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3273 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 IS | Inverter | Inverter066_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3274 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 IT | Inverter | Inverter066_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3275 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 IDC | Inverter | Inverter066_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3276 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 VDCP | Inverter | Inverter066_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3277 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 VDCN | Inverter | Inverter066_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3278 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 VDC | Inverter | Inverter066_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3279 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 P | Inverter | Inverter066_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3280 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Q | Inverter | Inverter066_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3281 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Ambient Temp | Inverter | Inverter066_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3282 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Max IGBT Temp | Inverter | Inverter066_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3283 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 IO Status | Inverter | Inverter066_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3284 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Hardware Version | Inverter | Inverter066_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3285 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV066 | Daggett 3_SUB1_INV066_M6 Software Version | Inverter | Inverter066_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3286 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_A Phase Current | Inverter | Inverter067_MODBUS.HR1004_i1_A | A Phase Current | 3287 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_B Phase Current | Inverter | Inverter067_MODBUS.HR1005_i2_A | B Phase Current | 3288 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_C Phase Current | Inverter | Inverter067_MODBUS.HR1006_i3_A | C Phase Current | 3289 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Bus Voltage | Inverter | Inverter067_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3290 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV067 | Daggett 3_SUB1_INV067_Apparent Power | Inverter | Inverter067_MODBUS.HR1010_s3_VA | Apparent Power | 3291 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 1 | Inverter | Inverter067_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3292 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC Input 1 | Inverter | Inverter067_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3293 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 2 | Inverter | Inverter067_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3294 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 2 | Inverter | Inverter067_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3295 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 3 | Inverter | Inverter067_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3296 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 3 | Inverter | Inverter067_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3297 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 4 | Inverter | Inverter067_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3298 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 4 | Inverter | Inverter067_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3299 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 5 | Inverter | Inverter067_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3300 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 5 | Inverter | Inverter067_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3301 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 6 | Inverter | Inverter067_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3302 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 6 | Inverter | Inverter067_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3303 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 7 | Inverter | Inverter067_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3304 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 7 | Inverter | Inverter067_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3305 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 8 | Inverter | Inverter067_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3306 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 8 | Inverter | Inverter067_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3307 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 9 | Inverter | Inverter067_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3308 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 9 | Inverter | Inverter067_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3309 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 10 | Inverter | Inverter067_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3310 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 10 | Inverter | Inverter067_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3311 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 11 | Inverter | Inverter067_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3312 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 11 | Inverter | Inverter067_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3313 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 12 | Inverter | Inverter067_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3314 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 12 | Inverter | Inverter067_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3315 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 13 | Inverter | Inverter067_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3316 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 13 | Inverter | Inverter067_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3317 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 14 | Inverter | Inverter067_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3318 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 14 | Inverter | Inverter067_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3319 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 15 | Inverter | Inverter067_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3320 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 15 | Inverter | Inverter067_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3321 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 16 | Inverter | Inverter067_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3322 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 16 | Inverter | Inverter067_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3323 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 17 | Inverter | Inverter067_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3324 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 17 | Inverter | Inverter067_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3325 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 18 | Inverter | Inverter067_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3326 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 18 | Inverter | Inverter067_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3327 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 19 | Inverter | Inverter067_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3328 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 19 | Inverter | Inverter067_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3329 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current DC Input 20 | Inverter | Inverter067_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3330 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC input 20 | Inverter | Inverter067_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3331 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current-AC | Inverter | Inverter067_MODBUS.HR1007_i3Avg_A | Current-AC | 3332 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Current-DC | Inverter | Inverter067_MODBUS.HR1062_idcInput_A | Current-DC | 3333 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Daily Energy Delivered | Inverter | Inverter067_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3334 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power Set Point | Inverter | Inverter067_MODBUS.HR0553_pRef | Real Power Set Point | 3335 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Reactive Power Set Point | Inverter | Inverter067_MODBUS.HR0558_qRef | Reactive Power Set Point | 3336 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Frequency | Inverter | Inverter067_MODBUS.HR1012_f3_Hz | Frequency | 3337 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV067 | Daggett 3_SUB1_INV067_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Insulation Resistance | Inverter | Inverter067_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3338 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Number of DU Channels | Inverter | Inverter067_MODBUS.HR0653_duChannels | Number of DU Channels | 3339 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Number of Running Modules | Inverter | Inverter067_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3340 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Operating State | Inverter | Inverter067_MODBUS.HR1123_currentStatus | Operating State | 3341 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Power Factor | Inverter | Inverter067_MODBUS.HR1011_pf3 | Power Factor | 3342 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV067 | Daggett 3_SUB1_INV067_Ramp Down | Inverter | Inverter067_MODBUS.HR0286_dropGradient_p | Ramp Down | 3343 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Ramp Up | Inverter | Inverter067_MODBUS.HR0282_riseGradient_p | Ramp Up | 3344 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power Delivered | Inverter | Inverter067_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3345 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Reactive Power Delivered | Inverter | Inverter067_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3346 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power | 3347 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Reactive Power | Inverter | Inverter067_MODBUS.HR1009_q3_kvar | Reactive Power | 3348 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Reactive Power Mode | Inverter | Inverter067_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3349 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Reactive Power Set Point Percent | Inverter | Inverter067_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3350 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power AC Percent | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3351 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power-AC | Inverter | Inverter067_MODBUS.HR1008_p3_kW | Real Power-AC | 3352 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Real Power-DC | Inverter | Inverter067_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3353 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Air Intake | Inverter | Inverter067_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3354 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Cabinet | Inverter | Inverter067_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3355 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-IGBT | Inverter | Inverter067_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3356 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Temperature-Module | Inverter | Inverter067_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3357 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage A-B | Inverter | Inverter067_MODBUS.HR1007_vRS_V | Voltage A-B | 3358 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage B-C | Inverter | Inverter067_MODBUS.HR1002_vST_V | Voltage B-C | 3359 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage C-A | Inverter | Inverter067_MODBUS.HR1003_vTR_V | Voltage C-A | 3360 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV067 | Daggett 3_SUB1_INV067_Voltage DC | Inverter | Inverter067_MODBUS.HR1051_vdcBus_V | Voltage DC | 3361 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV067 | Daggett 3_SUB1_INV067_Fault Code 1 | Inverter | Inverter067_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3362 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Warning | Inverter | Inverter067_MODBUS.HRxxxx_currentWarning | Warning | 3363 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Internal Input Status | Inverter | Inverter067_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3364 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Internal Output Status | Inverter | Inverter067_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3365 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Module Fault Code | Inverter | Inverter067_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3366 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Internal Humidity | Inverter | Inverter067_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3367 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Humidity | Inverter | Inverter067_MODBUS.HRxxxx_humidity | Humidity | 3368 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_Comms Fault Time | Inverter | Inverter067_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3369 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Status | Inverter | Inverter067_MODBUS.HRxxxx_M1_status | Module Status | 3370 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 IR | Inverter | Inverter067_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3371 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 IS | Inverter | Inverter067_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3372 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 IT | Inverter | Inverter067_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3373 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3374 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3375 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3376 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3377 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 P | Inverter | Inverter067_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3378 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Q | Inverter | Inverter067_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3379 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3380 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3381 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3382 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3383 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M1 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3384 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Status | Inverter | Inverter067_MODBUS.HRxxxx_M2_status | Module Status | 3385 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 IR | Inverter | Inverter067_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3386 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 IS | Inverter | Inverter067_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3387 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 IT | Inverter | Inverter067_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3388 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3389 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3390 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3391 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3392 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 P | Inverter | Inverter067_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3393 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Q | Inverter | Inverter067_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3394 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3395 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3396 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3397 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3398 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M2 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3399 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Status | Inverter | Inverter067_MODBUS.HRxxxx_M3_status | Module Status | 3400 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 IR | Inverter | Inverter067_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3401 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 IS | Inverter | Inverter067_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3402 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 IT | Inverter | Inverter067_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3403 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3404 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3405 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3406 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3407 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 P | Inverter | Inverter067_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3408 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Q | Inverter | Inverter067_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3409 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3410 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3411 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3412 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3413 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M3 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3414 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Status | Inverter | Inverter067_MODBUS.HRxxxx_M4_status | Module Status | 3415 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 IR | Inverter | Inverter067_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3416 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 IS | Inverter | Inverter067_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3417 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 IT | Inverter | Inverter067_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3418 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3419 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3420 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3421 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3422 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 P | Inverter | Inverter067_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3423 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Q | Inverter | Inverter067_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3424 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3425 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3426 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3427 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3428 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M4 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3429 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Status | Inverter | Inverter067_MODBUS.HRxxxx_M5_status | Module Status | 3430 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 IR | Inverter | Inverter067_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3431 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 IS | Inverter | Inverter067_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3432 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 IT | Inverter | Inverter067_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3433 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3434 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3435 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3436 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3437 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 P | Inverter | Inverter067_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3438 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Q | Inverter | Inverter067_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3439 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3440 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3441 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3442 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3443 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M5 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3444 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Status | Inverter | Inverter067_MODBUS.HRxxxx_M6_status | Module Status | 3445 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 IR | Inverter | Inverter067_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3446 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 IS | Inverter | Inverter067_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3447 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 IT | Inverter | Inverter067_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3448 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 IDC | Inverter | Inverter067_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3449 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 VDCP | Inverter | Inverter067_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3450 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 VDCN | Inverter | Inverter067_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3451 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 VDC | Inverter | Inverter067_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3452 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 P | Inverter | Inverter067_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3453 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Q | Inverter | Inverter067_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3454 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Ambient Temp | Inverter | Inverter067_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3455 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Max IGBT Temp | Inverter | Inverter067_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3456 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 IO Status | Inverter | Inverter067_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3457 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Hardware Version | Inverter | Inverter067_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3458 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV067 | Daggett 3_SUB1_INV067_M6 Software Version | Inverter | Inverter067_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3459 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_A Phase Current | Inverter | Inverter068_MODBUS.HR1004_i1_A | A Phase Current | 3460 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_B Phase Current | Inverter | Inverter068_MODBUS.HR1005_i2_A | B Phase Current | 3461 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_C Phase Current | Inverter | Inverter068_MODBUS.HR1006_i3_A | C Phase Current | 3462 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Bus Voltage | Inverter | Inverter068_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3463 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV068 | Daggett 3_SUB1_INV068_Apparent Power | Inverter | Inverter068_MODBUS.HR1010_s3_VA | Apparent Power | 3464 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 1 | Inverter | Inverter068_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3465 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC Input 1 | Inverter | Inverter068_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3466 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 2 | Inverter | Inverter068_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3467 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 2 | Inverter | Inverter068_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3468 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 3 | Inverter | Inverter068_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3469 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 3 | Inverter | Inverter068_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3470 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 4 | Inverter | Inverter068_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3471 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 4 | Inverter | Inverter068_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3472 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 5 | Inverter | Inverter068_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3473 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 5 | Inverter | Inverter068_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3474 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 6 | Inverter | Inverter068_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3475 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 6 | Inverter | Inverter068_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3476 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 7 | Inverter | Inverter068_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3477 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 7 | Inverter | Inverter068_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3478 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 8 | Inverter | Inverter068_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3479 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 8 | Inverter | Inverter068_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3480 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 9 | Inverter | Inverter068_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3481 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 9 | Inverter | Inverter068_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3482 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 10 | Inverter | Inverter068_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3483 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 10 | Inverter | Inverter068_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3484 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 11 | Inverter | Inverter068_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3485 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 11 | Inverter | Inverter068_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3486 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 12 | Inverter | Inverter068_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3487 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 12 | Inverter | Inverter068_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3488 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 13 | Inverter | Inverter068_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3489 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 13 | Inverter | Inverter068_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3490 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 14 | Inverter | Inverter068_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3491 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 14 | Inverter | Inverter068_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3492 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 15 | Inverter | Inverter068_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3493 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 15 | Inverter | Inverter068_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3494 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 16 | Inverter | Inverter068_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3495 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 16 | Inverter | Inverter068_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3496 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 17 | Inverter | Inverter068_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3497 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 17 | Inverter | Inverter068_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3498 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 18 | Inverter | Inverter068_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3499 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 18 | Inverter | Inverter068_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3500 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 19 | Inverter | Inverter068_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3501 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 19 | Inverter | Inverter068_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3502 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current DC Input 20 | Inverter | Inverter068_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3503 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC input 20 | Inverter | Inverter068_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3504 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current-AC | Inverter | Inverter068_MODBUS.HR1007_i3Avg_A | Current-AC | 3505 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Current-DC | Inverter | Inverter068_MODBUS.HR1062_idcInput_A | Current-DC | 3506 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Daily Energy Delivered | Inverter | Inverter068_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3507 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power Set Point | Inverter | Inverter068_MODBUS.HR0553_pRef | Real Power Set Point | 3508 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Reactive Power Set Point | Inverter | Inverter068_MODBUS.HR0558_qRef | Reactive Power Set Point | 3509 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Frequency | Inverter | Inverter068_MODBUS.HR1012_f3_Hz | Frequency | 3510 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV068 | Daggett 3_SUB1_INV068_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Insulation Resistance | Inverter | Inverter068_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3511 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Number of DU Channels | Inverter | Inverter068_MODBUS.HR0653_duChannels | Number of DU Channels | 3512 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Number of Running Modules | Inverter | Inverter068_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3513 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Operating State | Inverter | Inverter068_MODBUS.HR1123_currentStatus | Operating State | 3514 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Power Factor | Inverter | Inverter068_MODBUS.HR1011_pf3 | Power Factor | 3515 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV068 | Daggett 3_SUB1_INV068_Ramp Down | Inverter | Inverter068_MODBUS.HR0286_dropGradient_p | Ramp Down | 3516 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Ramp Up | Inverter | Inverter068_MODBUS.HR0282_riseGradient_p | Ramp Up | 3517 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power Delivered | Inverter | Inverter068_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3518 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Reactive Power Delivered | Inverter | Inverter068_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3519 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power | 3520 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Reactive Power | Inverter | Inverter068_MODBUS.HR1009_q3_kvar | Reactive Power | 3521 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Reactive Power Mode | Inverter | Inverter068_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3522 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Reactive Power Set Point Percent | Inverter | Inverter068_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3523 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power AC Percent | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3524 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power-AC | Inverter | Inverter068_MODBUS.HR1008_p3_kW | Real Power-AC | 3525 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Real Power-DC | Inverter | Inverter068_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3526 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Air Intake | Inverter | Inverter068_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3527 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Cabinet | Inverter | Inverter068_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3528 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-IGBT | Inverter | Inverter068_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3529 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Temperature-Module | Inverter | Inverter068_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3530 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage A-B | Inverter | Inverter068_MODBUS.HR1008_vRS_V | Voltage A-B | 3531 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage B-C | Inverter | Inverter068_MODBUS.HR1002_vST_V | Voltage B-C | 3532 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage C-A | Inverter | Inverter068_MODBUS.HR1003_vTR_V | Voltage C-A | 3533 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV068 | Daggett 3_SUB1_INV068_Voltage DC | Inverter | Inverter068_MODBUS.HR1051_vdcBus_V | Voltage DC | 3534 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV068 | Daggett 3_SUB1_INV068_Fault Code 1 | Inverter | Inverter068_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3535 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Warning | Inverter | Inverter068_MODBUS.HRxxxx_currentWarning | Warning | 3536 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Internal Input Status | Inverter | Inverter068_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3537 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Internal Output Status | Inverter | Inverter068_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3538 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Module Fault Code | Inverter | Inverter068_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3539 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Internal Humidity | Inverter | Inverter068_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3540 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Humidity | Inverter | Inverter068_MODBUS.HRxxxx_humidity | Humidity | 3541 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_Comms Fault Time | Inverter | Inverter068_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3542 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Status | Inverter | Inverter068_MODBUS.HRxxxx_M1_status | Module Status | 3543 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 IR | Inverter | Inverter068_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3544 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 IS | Inverter | Inverter068_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3545 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 IT | Inverter | Inverter068_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3546 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3547 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3548 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3549 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3550 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 P | Inverter | Inverter068_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3551 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Q | Inverter | Inverter068_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3552 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3553 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3554 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3555 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3556 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M1 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3557 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Status | Inverter | Inverter068_MODBUS.HRxxxx_M2_status | Module Status | 3558 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 IR | Inverter | Inverter068_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3559 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 IS | Inverter | Inverter068_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3560 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 IT | Inverter | Inverter068_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3561 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3562 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3563 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3564 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3565 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 P | Inverter | Inverter068_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3566 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Q | Inverter | Inverter068_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3567 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3568 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3569 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3570 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3571 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M2 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3572 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Status | Inverter | Inverter068_MODBUS.HRxxxx_M3_status | Module Status | 3573 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 IR | Inverter | Inverter068_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3574 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 IS | Inverter | Inverter068_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3575 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 IT | Inverter | Inverter068_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3576 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3577 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3578 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3579 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3580 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 P | Inverter | Inverter068_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3581 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Q | Inverter | Inverter068_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3582 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3583 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3584 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3585 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3586 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M3 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3587 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Status | Inverter | Inverter068_MODBUS.HRxxxx_M4_status | Module Status | 3588 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 IR | Inverter | Inverter068_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3589 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 IS | Inverter | Inverter068_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3590 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 IT | Inverter | Inverter068_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3591 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3592 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3593 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3594 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3595 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 P | Inverter | Inverter068_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3596 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Q | Inverter | Inverter068_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3597 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3598 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3599 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3600 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3601 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M4 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3602 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Status | Inverter | Inverter068_MODBUS.HRxxxx_M5_status | Module Status | 3603 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 IR | Inverter | Inverter068_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3604 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 IS | Inverter | Inverter068_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3605 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 IT | Inverter | Inverter068_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3606 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3607 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3608 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3609 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3610 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 P | Inverter | Inverter068_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3611 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Q | Inverter | Inverter068_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3612 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3613 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3614 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3615 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3616 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M5 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3617 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Status | Inverter | Inverter068_MODBUS.HRxxxx_M6_status | Module Status | 3618 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 IR | Inverter | Inverter068_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3619 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 IS | Inverter | Inverter068_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3620 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 IT | Inverter | Inverter068_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3621 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 IDC | Inverter | Inverter068_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3622 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 VDCP | Inverter | Inverter068_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3623 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 VDCN | Inverter | Inverter068_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3624 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 VDC | Inverter | Inverter068_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3625 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 P | Inverter | Inverter068_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3626 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Q | Inverter | Inverter068_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3627 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Ambient Temp | Inverter | Inverter068_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3628 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Max IGBT Temp | Inverter | Inverter068_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3629 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 IO Status | Inverter | Inverter068_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3630 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Hardware Version | Inverter | Inverter068_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3631 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV068 | Daggett 3_SUB1_INV068_M6 Software Version | Inverter | Inverter068_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3632 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_A Phase Current | Inverter | Inverter069_MODBUS.HR1004_i1_A | A Phase Current | 3633 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_B Phase Current | Inverter | Inverter069_MODBUS.HR1005_i2_A | B Phase Current | 3634 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_C Phase Current | Inverter | Inverter069_MODBUS.HR1006_i3_A | C Phase Current | 3635 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Bus Voltage | Inverter | Inverter069_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3636 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV069 | Daggett 3_SUB1_INV069_Apparent Power | Inverter | Inverter069_MODBUS.HR1010_s3_VA | Apparent Power | 3637 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 1 | Inverter | Inverter069_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3638 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC Input 1 | Inverter | Inverter069_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3639 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 2 | Inverter | Inverter069_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3640 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 2 | Inverter | Inverter069_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3641 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 3 | Inverter | Inverter069_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3642 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 3 | Inverter | Inverter069_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3643 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 4 | Inverter | Inverter069_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3644 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 4 | Inverter | Inverter069_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3645 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 5 | Inverter | Inverter069_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3646 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 5 | Inverter | Inverter069_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3647 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 6 | Inverter | Inverter069_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3648 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 6 | Inverter | Inverter069_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3649 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 7 | Inverter | Inverter069_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3650 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 7 | Inverter | Inverter069_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3651 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 8 | Inverter | Inverter069_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3652 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 8 | Inverter | Inverter069_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3653 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 9 | Inverter | Inverter069_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3654 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 9 | Inverter | Inverter069_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3655 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 10 | Inverter | Inverter069_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3656 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 10 | Inverter | Inverter069_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3657 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 11 | Inverter | Inverter069_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3658 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 11 | Inverter | Inverter069_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3659 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 12 | Inverter | Inverter069_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3660 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 12 | Inverter | Inverter069_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3661 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 13 | Inverter | Inverter069_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3662 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 13 | Inverter | Inverter069_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3663 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 14 | Inverter | Inverter069_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3664 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 14 | Inverter | Inverter069_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3665 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 15 | Inverter | Inverter069_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3666 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 15 | Inverter | Inverter069_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3667 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 16 | Inverter | Inverter069_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3668 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 16 | Inverter | Inverter069_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3669 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 17 | Inverter | Inverter069_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3670 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 17 | Inverter | Inverter069_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3671 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 18 | Inverter | Inverter069_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3672 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 18 | Inverter | Inverter069_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3673 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 19 | Inverter | Inverter069_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3674 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 19 | Inverter | Inverter069_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3675 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current DC Input 20 | Inverter | Inverter069_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3676 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC input 20 | Inverter | Inverter069_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3677 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current-AC | Inverter | Inverter069_MODBUS.HR1007_i3Avg_A | Current-AC | 3678 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Current-DC | Inverter | Inverter069_MODBUS.HR1062_idcInput_A | Current-DC | 3679 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Daily Energy Delivered | Inverter | Inverter069_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3680 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power Set Point | Inverter | Inverter069_MODBUS.HR0553_pRef | Real Power Set Point | 3681 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Reactive Power Set Point | Inverter | Inverter069_MODBUS.HR0558_qRef | Reactive Power Set Point | 3682 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Frequency | Inverter | Inverter069_MODBUS.HR1012_f3_Hz | Frequency | 3683 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV069 | Daggett 3_SUB1_INV069_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Insulation Resistance | Inverter | Inverter069_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3684 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Number of DU Channels | Inverter | Inverter069_MODBUS.HR0653_duChannels | Number of DU Channels | 3685 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Number of Running Modules | Inverter | Inverter069_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3686 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Operating State | Inverter | Inverter069_MODBUS.HR1123_currentStatus | Operating State | 3687 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Power Factor | Inverter | Inverter069_MODBUS.HR1011_pf3 | Power Factor | 3688 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV069 | Daggett 3_SUB1_INV069_Ramp Down | Inverter | Inverter069_MODBUS.HR0286_dropGradient_p | Ramp Down | 3689 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Ramp Up | Inverter | Inverter069_MODBUS.HR0282_riseGradient_p | Ramp Up | 3690 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power Delivered | Inverter | Inverter069_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3691 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Reactive Power Delivered | Inverter | Inverter069_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3692 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power | 3693 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Reactive Power | Inverter | Inverter069_MODBUS.HR1009_q3_kvar | Reactive Power | 3694 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Reactive Power Mode | Inverter | Inverter069_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3695 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Reactive Power Set Point Percent | Inverter | Inverter069_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3696 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power AC Percent | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3697 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power-AC | Inverter | Inverter069_MODBUS.HR1008_p3_kW | Real Power-AC | 3698 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Real Power-DC | Inverter | Inverter069_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3699 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Air Intake | Inverter | Inverter069_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3700 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Cabinet | Inverter | Inverter069_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3701 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-IGBT | Inverter | Inverter069_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3702 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Temperature-Module | Inverter | Inverter069_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3703 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage A-B | Inverter | Inverter069_MODBUS.HR1009_vRS_V | Voltage A-B | 3704 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage B-C | Inverter | Inverter069_MODBUS.HR1002_vST_V | Voltage B-C | 3705 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage C-A | Inverter | Inverter069_MODBUS.HR1003_vTR_V | Voltage C-A | 3706 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV069 | Daggett 3_SUB1_INV069_Voltage DC | Inverter | Inverter069_MODBUS.HR1051_vdcBus_V | Voltage DC | 3707 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV069 | Daggett 3_SUB1_INV069_Fault Code 1 | Inverter | Inverter069_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3708 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Warning | Inverter | Inverter069_MODBUS.HRxxxx_currentWarning | Warning | 3709 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Internal Input Status | Inverter | Inverter069_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3710 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Internal Output Status | Inverter | Inverter069_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3711 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Module Fault Code | Inverter | Inverter069_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3712 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Internal Humidity | Inverter | Inverter069_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3713 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Humidity | Inverter | Inverter069_MODBUS.HRxxxx_humidity | Humidity | 3714 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_Comms Fault Time | Inverter | Inverter069_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3715 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Status | Inverter | Inverter069_MODBUS.HRxxxx_M1_status | Module Status | 3716 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 IR | Inverter | Inverter069_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3717 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 IS | Inverter | Inverter069_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3718 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 IT | Inverter | Inverter069_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3719 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3720 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3721 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3722 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3723 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 P | Inverter | Inverter069_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3724 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Q | Inverter | Inverter069_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3725 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3726 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3727 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3728 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3729 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M1 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3730 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Status | Inverter | Inverter069_MODBUS.HRxxxx_M2_status | Module Status | 3731 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 IR | Inverter | Inverter069_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3732 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 IS | Inverter | Inverter069_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3733 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 IT | Inverter | Inverter069_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3734 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3735 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3736 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3737 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3738 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 P | Inverter | Inverter069_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3739 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Q | Inverter | Inverter069_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3740 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3741 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3742 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3743 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3744 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M2 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3745 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Status | Inverter | Inverter069_MODBUS.HRxxxx_M3_status | Module Status | 3746 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 IR | Inverter | Inverter069_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3747 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 IS | Inverter | Inverter069_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3748 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 IT | Inverter | Inverter069_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3749 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3750 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3751 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3752 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3753 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 P | Inverter | Inverter069_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3754 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Q | Inverter | Inverter069_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3755 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3756 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3757 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3758 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3759 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M3 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3760 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Status | Inverter | Inverter069_MODBUS.HRxxxx_M4_status | Module Status | 3761 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 IR | Inverter | Inverter069_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3762 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 IS | Inverter | Inverter069_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3763 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 IT | Inverter | Inverter069_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3764 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3765 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3766 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3767 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3768 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 P | Inverter | Inverter069_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3769 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Q | Inverter | Inverter069_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3770 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3771 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3772 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3773 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3774 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M4 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3775 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Status | Inverter | Inverter069_MODBUS.HRxxxx_M5_status | Module Status | 3776 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 IR | Inverter | Inverter069_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3777 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 IS | Inverter | Inverter069_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3778 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 IT | Inverter | Inverter069_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3779 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3780 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3781 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3782 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3783 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 P | Inverter | Inverter069_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3784 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Q | Inverter | Inverter069_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3785 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3786 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3787 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3788 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3789 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M5 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3790 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Status | Inverter | Inverter069_MODBUS.HRxxxx_M6_status | Module Status | 3791 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 IR | Inverter | Inverter069_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3792 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 IS | Inverter | Inverter069_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3793 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 IT | Inverter | Inverter069_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3794 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 IDC | Inverter | Inverter069_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3795 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 VDCP | Inverter | Inverter069_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3796 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 VDCN | Inverter | Inverter069_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3797 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 VDC | Inverter | Inverter069_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3798 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 P | Inverter | Inverter069_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3799 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Q | Inverter | Inverter069_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3800 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Ambient Temp | Inverter | Inverter069_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3801 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Max IGBT Temp | Inverter | Inverter069_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3802 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 IO Status | Inverter | Inverter069_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3803 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Hardware Version | Inverter | Inverter069_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3804 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV069 | Daggett 3_SUB1_INV069_M6 Software Version | Inverter | Inverter069_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3805 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_A Phase Current | Inverter | inverter070_MODBUS.HR1004_i1_A | A Phase Current | 3806 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_B Phase Current | Inverter | inverter070_MODBUS.HR1005_i2_A | B Phase Current | 3807 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_C Phase Current | Inverter | inverter070_MODBUS.HR1006_i3_A | C Phase Current | 3808 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Bus Voltage | Inverter | inverter070_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3809 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV070 | Daggett 3_SUB1_INV070_Apparent Power | Inverter | inverter070_MODBUS.HR1010_s3_VA | Apparent Power | 3810 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 1 | Inverter | Inverter070_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3811 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC Input 1 | Inverter | Inverter070_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3812 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 2 | Inverter | Inverter070_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3813 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 2 | Inverter | Inverter070_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3814 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 3 | Inverter | Inverter070_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3815 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 3 | Inverter | Inverter070_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3816 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 4 | Inverter | Inverter070_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3817 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 4 | Inverter | Inverter070_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3818 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 5 | Inverter | Inverter070_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3819 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 5 | Inverter | Inverter070_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3820 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 6 | Inverter | Inverter070_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3821 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 6 | Inverter | Inverter070_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3822 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 7 | Inverter | Inverter070_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3823 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 7 | Inverter | Inverter070_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3824 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 8 | Inverter | Inverter070_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3825 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 8 | Inverter | Inverter070_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3826 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 9 | Inverter | Inverter070_MODBUS.HR5853_du9_idc_A | Current DC Input# | 3827 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 9 | Inverter | Inverter070_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 3828 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 10 | Inverter | Inverter070_MODBUS.HR5859_du10_idc_A | Current DC Input# | 3829 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 10 | Inverter | Inverter070_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 3830 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 11 | Inverter | Inverter070_MODBUS.HR5865_du11_idc_A | Current DC Input# | 3831 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 11 | Inverter | Inverter070_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 3832 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 12 | Inverter | Inverter070_MODBUS.HR5871_du12_idc_A | Current DC Input# | 3833 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 12 | Inverter | Inverter070_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 3834 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 13 | Inverter | Inverter070_MODBUS.HR5877_du13_idc_A | Current DC Input# | 3835 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 13 | Inverter | Inverter070_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 3836 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 14 | Inverter | Inverter070_MODBUS.HR5883_du14_idc_A | Current DC Input# | 3837 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 14 | Inverter | Inverter070_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 3838 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 15 | Inverter | Inverter070_MODBUS.HR5889_du15_idc_A | Current DC Input# | 3839 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 15 | Inverter | Inverter070_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 3840 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 16 | Inverter | Inverter070_MODBUS.HR5895_du16_idc_A | Current DC Input# | 3841 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 16 | Inverter | Inverter070_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 3842 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 17 | Inverter | Inverter070_MODBUS.HR5901_du17_idc_A | Current DC Input# | 3843 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 17 | Inverter | Inverter070_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 3844 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 18 | Inverter | Inverter070_MODBUS.HR5907_du18_idc_A | Current DC Input# | 3845 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 18 | Inverter | Inverter070_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 3846 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 19 | Inverter | Inverter070_MODBUS.HR5913_du19_idc_A | Current DC Input# | 3847 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 19 | Inverter | Inverter070_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 3848 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current DC Input 20 | Inverter | Inverter070_MODBUS.HR5919_du20_idc_A | Current DC Input# | 3849 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC input 20 | Inverter | Inverter070_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 3850 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current-AC | Inverter | inverter070_MODBUS.HR1007_i3Avg_A | Current-AC | 3851 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Current-DC | Inverter | inverter070_MODBUS.HR1062_idcInput_A | Current-DC | 3852 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Daily Energy Delivered | Inverter | inverter070_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 3853 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power Set Point | Inverter | inverter070_MODBUS.HR0553_pRef | Real Power Set Point | 3854 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Reactive Power Set Point | Inverter | inverter070_MODBUS.HR0558_qRef | Reactive Power Set Point | 3855 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Frequency | Inverter | inverter070_MODBUS.HR1012_f3_Hz | Frequency | 3856 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV070 | Daggett 3_SUB1_INV070_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Insulation Resistance | Inverter | inverter070_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 3857 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Number of DU Channels | Inverter | inverter070_MODBUS.HR0653_duChannels | Number of DU Channels | 3858 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Number of Running Modules | Inverter | inverter070_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 3859 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Operating State | Inverter | inverter070_MODBUS.HR1123_currentStatus | Operating State | 3860 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Power Factor | Inverter | inverter070_MODBUS.HR1011_pf3 | Power Factor | 3861 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV070 | Daggett 3_SUB1_INV070_Ramp Down | Inverter | inverter070_MODBUS.HR0286_dropGradient_p | Ramp Down | 3862 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Ramp Up | Inverter | inverter070_MODBUS.HR0282_riseGradient_p | Ramp Up | 3863 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power Delivered | Inverter | inverter070_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 3864 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Reactive Power Delivered | Inverter | inverter070_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 3865 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power | 3866 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Reactive Power | Inverter | inverter070_MODBUS.HR1009_q3_kvar | Reactive Power | 3867 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Reactive Power Mode | Inverter | inverter070_MODBUS.HR0552_qControlMode | Reactive Power Mode | 3868 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Reactive Power Set Point Percent | Inverter | inverter070_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 3869 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power AC Percent | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power AC Percent | 3870 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power-AC | Inverter | inverter070_MODBUS.HR1008_p3_kW | Real Power-AC | 3871 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Real Power-DC | Inverter | inverter070_MODBUS.HR1061_pdcInput_W | Real Power-DC | 3872 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Air Intake | Inverter | inverter070_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 3873 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Cabinet | Inverter | inverter070_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 3874 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-IGBT | Inverter | inverter070_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 3875 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Temperature-Module | Inverter | inverter070_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 3876 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage A-B | Inverter | inverter070_MODBUS.HR1010_vRS_V | Voltage A-B | 3877 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage B-C | Inverter | inverter070_MODBUS.HR1002_vST_V | Voltage B-C | 3878 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage C-A | Inverter | inverter070_MODBUS.HR1003_vTR_V | Voltage C-A | 3879 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV070 | Daggett 3_SUB1_INV070_Voltage DC | Inverter | inverter070_MODBUS.HR1051_vdcBus_V | Voltage DC | 3880 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV070 | Daggett 3_SUB1_INV070_Fault Code 1 | Inverter | Inverter070_MODBUS.HRxxxx_currentFault | Fault Code 1 | 3881 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Warning | Inverter | Inverter070_MODBUS.HRxxxx_currentWarning | Warning | 3882 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Internal Input Status | Inverter | Inverter070_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 3883 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Internal Output Status | Inverter | Inverter070_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 3884 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Module Fault Code | Inverter | Inverter070_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 3885 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Internal Humidity | Inverter | Inverter070_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 3886 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Humidity | Inverter | Inverter070_MODBUS.HRxxxx_humidity | Humidity | 3887 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_Comms Fault Time | Inverter | Inverter070_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 3888 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Status | Inverter | Inverter070_MODBUS.HRxxxx_M1_status | Module Status | 3889 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 IR | Inverter | Inverter070_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 3890 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 IS | Inverter | Inverter070_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 3891 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 IT | Inverter | Inverter070_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 3892 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 3893 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 3894 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 3895 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 3896 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 P | Inverter | Inverter070_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 3897 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Q | Inverter | Inverter070_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 3898 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 3899 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 3900 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 3901 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 3902 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M1 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 3903 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Status | Inverter | Inverter070_MODBUS.HRxxxx_M2_status | Module Status | 3904 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 IR | Inverter | Inverter070_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 3905 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 IS | Inverter | Inverter070_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 3906 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 IT | Inverter | Inverter070_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 3907 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 3908 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 3909 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 3910 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 3911 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 P | Inverter | Inverter070_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 3912 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Q | Inverter | Inverter070_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 3913 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 3914 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 3915 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 3916 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 3917 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M2 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 3918 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Status | Inverter | Inverter070_MODBUS.HRxxxx_M3_status | Module Status | 3919 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 IR | Inverter | Inverter070_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 3920 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 IS | Inverter | Inverter070_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 3921 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 IT | Inverter | Inverter070_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 3922 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 3923 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 3924 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 3925 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 3926 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 P | Inverter | Inverter070_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 3927 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Q | Inverter | Inverter070_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 3928 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 3929 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 3930 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 3931 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 3932 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M3 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 3933 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Status | Inverter | Inverter070_MODBUS.HRxxxx_M4_status | Module Status | 3934 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 IR | Inverter | Inverter070_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 3935 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 IS | Inverter | Inverter070_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 3936 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 IT | Inverter | Inverter070_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 3937 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 3938 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 3939 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 3940 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 3941 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 P | Inverter | Inverter070_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 3942 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Q | Inverter | Inverter070_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 3943 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 3944 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 3945 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 3946 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 3947 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M4 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 3948 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Status | Inverter | Inverter070_MODBUS.HRxxxx_M5_status | Module Status | 3949 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 IR | Inverter | Inverter070_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 3950 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 IS | Inverter | Inverter070_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 3951 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 IT | Inverter | Inverter070_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 3952 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 3953 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 3954 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 3955 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 3956 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 P | Inverter | Inverter070_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 3957 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Q | Inverter | Inverter070_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 3958 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 3959 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 3960 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 3961 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 3962 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M5 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 3963 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Status | Inverter | Inverter070_MODBUS.HRxxxx_M6_status | Module Status | 3964 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 IR | Inverter | Inverter070_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 3965 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 IS | Inverter | Inverter070_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 3966 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 IT | Inverter | Inverter070_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 3967 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 IDC | Inverter | Inverter070_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 3968 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 VDCP | Inverter | Inverter070_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 3969 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 VDCN | Inverter | Inverter070_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 3970 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 VDC | Inverter | Inverter070_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 3971 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 P | Inverter | Inverter070_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 3972 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Q | Inverter | Inverter070_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 3973 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Ambient Temp | Inverter | Inverter070_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 3974 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Max IGBT Temp | Inverter | Inverter070_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 3975 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 IO Status | Inverter | Inverter070_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 3976 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Hardware Version | Inverter | Inverter070_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 3977 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV070 | Daggett 3_SUB1_INV070_M6 Software Version | Inverter | Inverter070_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 3978 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_A Phase Current | Inverter | inverter071_MODBUS.HR1004_i1_A | A Phase Current | 3979 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_B Phase Current | Inverter | inverter071_MODBUS.HR1005_i2_A | B Phase Current | 3980 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_C Phase Current | Inverter | inverter071_MODBUS.HR1006_i3_A | C Phase Current | 3981 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Bus Voltage | Inverter | inverter071_MODBUS.HR1051_vdcBus_V | Bus Voltage | 3982 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV071 | Daggett 3_SUB1_INV071_Apparent Power | Inverter | inverter071_MODBUS.HR1010_s3_VA | Apparent Power | 3983 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 1 | Inverter | Inverter071_MODBUS.HR5805_du1_idc_A | Current DC Input# | 3984 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC Input 1 | Inverter | Inverter071_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 3985 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 2 | Inverter | Inverter071_MODBUS.HR5811_du2_idc_A | Current DC Input# | 3986 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 2 | Inverter | Inverter071_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 3987 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 3 | Inverter | Inverter071_MODBUS.HR5817_du3_idc_A | Current DC Input# | 3988 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 3 | Inverter | Inverter071_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 3989 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 4 | Inverter | Inverter071_MODBUS.HR5823_du4_idc_A | Current DC Input# | 3990 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 4 | Inverter | Inverter071_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 3991 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 5 | Inverter | Inverter071_MODBUS.HR5829_du5_idc_A | Current DC Input# | 3992 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 5 | Inverter | Inverter071_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 3993 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 6 | Inverter | Inverter071_MODBUS.HR5835_du6_idc_A | Current DC Input# | 3994 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 6 | Inverter | Inverter071_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 3995 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 7 | Inverter | Inverter071_MODBUS.HR5841_du7_idc_A | Current DC Input# | 3996 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 7 | Inverter | Inverter071_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 3997 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 8 | Inverter | Inverter071_MODBUS.HR5847_du8_idc_A | Current DC Input# | 3998 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 8 | Inverter | Inverter071_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 3999 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 9 | Inverter | Inverter071_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4000 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 9 | Inverter | Inverter071_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4001 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 10 | Inverter | Inverter071_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4002 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 10 | Inverter | Inverter071_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4003 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 11 | Inverter | Inverter071_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4004 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 11 | Inverter | Inverter071_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4005 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 12 | Inverter | Inverter071_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4006 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 12 | Inverter | Inverter071_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4007 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 13 | Inverter | Inverter071_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4008 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 13 | Inverter | Inverter071_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4009 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 14 | Inverter | Inverter071_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4010 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 14 | Inverter | Inverter071_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4011 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 15 | Inverter | Inverter071_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4012 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 15 | Inverter | Inverter071_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4013 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 16 | Inverter | Inverter071_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4014 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 16 | Inverter | Inverter071_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4015 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 17 | Inverter | Inverter071_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4016 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 17 | Inverter | Inverter071_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4017 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 18 | Inverter | Inverter071_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4018 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 18 | Inverter | Inverter071_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4019 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 19 | Inverter | Inverter071_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4020 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 19 | Inverter | Inverter071_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4021 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current DC Input 20 | Inverter | Inverter071_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4022 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC input 20 | Inverter | Inverter071_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4023 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current-AC | Inverter | inverter071_MODBUS.HR1007_i3Avg_A | Current-AC | 4024 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Current-DC | Inverter | inverter071_MODBUS.HR1062_idcInput_A | Current-DC | 4025 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Daily Energy Delivered | Inverter | inverter071_MODBUS.HR1202_p3DeliveredDaily_kWh | Daily Energy Delivered | 4026 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power Set Point | Inverter | inverter071_MODBUS.HR0553_pRef | Real Power Set Point | 4027 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Reactive Power Set Point | Inverter | inverter071_MODBUS.HR0558_qRef | Reactive Power Set Point | 4028 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Frequency | Inverter | inverter071_MODBUS.HR1012_f3_Hz | Frequency | 4029 | Hz | Requested-Available | 56 | 64 | 0.01
SUB1 | INV071 | Daggett 3_SUB1_INV071_IGBT Current | Inverter |  | IGBT Current |  | A | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Insulation Resistance | Inverter | inverter071_MODBUS.HR1104_dcInsulation_resistance_Ohm | Insulation Resistance | 4030 | Ω | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Isolation Measure Timeout | Inverter |  | Isolation Measure Timeout |  | V | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Maximum DC Voltage | Inverter |  | Maximum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Minimum DC Voltage | Inverter |  | Minimum DC Voltage |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Number of DU Channels | Inverter | inverter071_MODBUS.HR0653_duChannels | Number of DU Channels | 4031 | # | Requested-Available | 0 | 40 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Number of Running Modules | Inverter | inverter071_MODBUS.HR1392_runningModulesCount | Number of Running Modules | 4032 | # | Requested-Available | 0 | 7 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Operating State | Inverter | inverter071_MODBUS.HR1123_currentStatus | Operating State | 4033 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Power Factor | Inverter | inverter071_MODBUS.HR1011_pf3 | Power Factor | 4034 | Unitless | Requested-Available | -1 | 1 | 0.001
SUB1 | INV071 | Daggett 3_SUB1_INV071_Ramp Down | Inverter | inverter071_MODBUS.HR0286_dropGradient_p | Ramp Down | 4035 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Ramp Rate | Inverter |  | Ramp Rate |  | MW/sec | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Ramp Up | Inverter | inverter071_MODBUS.HR0282_riseGradient_p | Ramp Up | 4036 | MW/sec | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power Delivered | Inverter | inverter071_MODBUS.HR1210_e3Total_kWh | Real Power Delivered | 4037 | kWh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Reactive Power Delivered | Inverter | inverter071_MODBUS.HR1221_er3Total_kvarh | Reactive Power Delivered | 4038 | kVARh | Requested-Available | 0 | 2147483647 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power | 4039 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Reactive Power | Inverter | inverter071_MODBUS.HR1009_q3_kvar | Reactive Power | 4040 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Reactive Power Mode | Inverter | inverter071_MODBUS.HR0552_qControlMode | Reactive Power Mode | 4041 | # | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Reactive Power Set Point Percent | Inverter | inverter071_MODBUS.HR0558_qRef | Reactive Power Set Point Percent | 4042 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power AC Percent | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power AC Percent | 4043 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power-AC | Inverter | inverter071_MODBUS.HR1008_p3_kW | Real Power-AC | 4044 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Real Power-DC | Inverter | inverter071_MODBUS.HR1061_pdcInput_W | Real Power-DC | 4045 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Air Intake | Inverter | inverter071_MODBUS.HR1129_acModuleAdmissionTemp | Temperature-Air Intake | 4046 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Ambient | Inverter |  | Temperature-Ambient |  | °C | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Cabinet | Inverter | inverter071_MODBUS.HR1124_internalTemp | Temperature-Cabinet | 4047 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Combiner Box | Inverter |  | Temperature-Combiner Box |  | °C | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Coolant | Inverter |  | Temperature-Coolant |  | °C | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Filter Choke | Inverter |  | Temperature-Filter Choke |  | °C | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-IGBT | Inverter | inverter071_MODBUS.HR1125_maxIgbtTemp | Temperature-IGBT | 4048 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-IGBT Heat Sink | Inverter |  | Temperature-IGBT Heat Sink |  | °C | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Temperature-Module | Inverter | inverter071_MODBUS.HR1126_maxModuleTemp | Temperature-Module | 4049 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Uptime | Inverter |  | Uptime |  | seconds | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage A-B | Inverter | inverter071_MODBUS.HR1001_vRS_V | Voltage A-B | 4050 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage A-N | Inverter |  | Voltage A-N |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage B-C | Inverter | inverter071_MODBUS.HR1002_vST_V | Voltage B-C | 4051 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage B-N | Inverter |  | Voltage B-N |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage C-A | Inverter | inverter071_MODBUS.HR1003_vTR_V | Voltage C-A | 4052 | kV | Requested-Available | 0 | 35 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage C-N | Inverter |  | Voltage C-N |  | kV | Requested-Not Available
SUB1 | INV071 | Daggett 3_SUB1_INV071_Voltage DC | Inverter | inverter071_MODBUS.HR1051_vdcBus_V | Voltage DC | 4053 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV071 | Daggett 3_SUB1_INV071_Fault Code 1 | Inverter | Inverter071_MODBUS.HRxxxx_currentFault | Fault Code 1 | 4054 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Warning | Inverter | Inverter071_MODBUS.HRxxxx_currentWarning | Warning | 4055 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Internal Input Status | Inverter | Inverter071_MODBUS.HRxxxx_internalInputStatus | Internal Input Status | 4056 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Internal Output Status | Inverter | Inverter071_MODBUS.HRxxxx_internalOutputStatus | Internal Output Status | 4057 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Module Fault Code | Inverter | Inverter071_MODBUS.HRxxxx_currentFaultModule | Module Fault Code | 4058 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Internal Humidity | Inverter | Inverter071_MODBUS.HRxxxx_internalHumidity | Internal Humidity | 4059 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Humidity | Inverter | Inverter071_MODBUS.HRxxxx_humidity | Humidity | 4060 | % | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_Comms Fault Time | Inverter | Inverter071_MODBUS.HRxxxx_commsFaultTime | Comms Fault Time | 4061 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Status | Inverter | Inverter071_MODBUS.HRxxxx_M1_status | Module Status | 4062 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 IR | Inverter | Inverter071_MODBUS.HRxxxx_M1_iR_A | Module Current IR | 4063 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 IS | Inverter | Inverter071_MODBUS.HRxxxx_M1_iS_A | Module Current IS | 4064 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 IT | Inverter | Inverter071_MODBUS.HRxxxx_M1_iT_A | Module Current IT | 4065 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M1_iDC_A | Module Current IDC | 4066 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M1_vDCP_V | Module Vdc P | 4067 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M1_vDCN_V | Module Vdc N | 4068 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M1_vDC_V | Module Vdc | 4069 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 P | Inverter | Inverter071_MODBUS.HRxxxx_M1_p_kW | Module Real Power | 4070 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Q | Inverter | Inverter071_MODBUS.HRxxxx_M1_q_kVar | Module Reactive Power | 4071 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M1_ambientTemp_c | Module Ambient Temperature | 4072 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M1_maxIGBTTemp_c | Module Max IGBT Temperature | 4073 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M1_ioStatus | Module IO Status | 4074 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M1_hwVersion | Module Hardware Version | 4075 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M1 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M1_swVersion | Module Software Version | 4076 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Status | Inverter | Inverter071_MODBUS.HRxxxx_M2_status | Module Status | 4077 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 IR | Inverter | Inverter071_MODBUS.HRxxxx_M2_iR_A | Module Current IR | 4078 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 IS | Inverter | Inverter071_MODBUS.HRxxxx_M2_iS_A | Module Current IS | 4079 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 IT | Inverter | Inverter071_MODBUS.HRxxxx_M2_iT_A | Module Current IT | 4080 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M2_iDC_A | Module Current IDC | 4081 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M2_vDCP_V | Module Vdc P | 4082 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M2_vDCN_V | Module Vdc N | 4083 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M2_vDC_V | Module Vdc | 4084 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 P | Inverter | Inverter071_MODBUS.HRxxxx_M2_p_kW | Module Real Power | 4085 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Q | Inverter | Inverter071_MODBUS.HRxxxx_M2_q_kVar | Module Reactive Power | 4086 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M2_ambientTemp_c | Module Ambient Temperature | 4087 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M2_maxIGBTTemp_c | Module Max IGBT Temperature | 4088 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M2_ioStatus | Module IO Status | 4089 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M2_hwVersion | Module Hardware Version | 4090 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M2 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M2_swVersion | Module Software Version | 4091 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Status | Inverter | Inverter071_MODBUS.HRxxxx_M3_status | Module Status | 4092 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 IR | Inverter | Inverter071_MODBUS.HRxxxx_M3_iR_A | Module Current IR | 4093 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 IS | Inverter | Inverter071_MODBUS.HRxxxx_M3_iS_A | Module Current IS | 4094 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 IT | Inverter | Inverter071_MODBUS.HRxxxx_M3_iT_A | Module Current IT | 4095 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M3_iDC_A | Module Current IDC | 4096 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M3_vDCP_V | Module Vdc P | 4097 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M3_vDCN_V | Module Vdc N | 4098 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M3_vDC_V | Module Vdc | 4099 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 P | Inverter | Inverter071_MODBUS.HRxxxx_M3_p_kW | Module Real Power | 4100 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Q | Inverter | Inverter071_MODBUS.HRxxxx_M3_q_kVar | Module Reactive Power | 4101 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M3_ambientTemp_c | Module Ambient Temperature | 4102 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M3_maxIGBTTemp_c | Module Max IGBT Temperature | 4103 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M3_ioStatus | Module IO Status | 4104 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M3_hwVersion | Module Hardware Version | 4105 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M3 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M3_swVersion | Module Software Version | 4106 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Status | Inverter | Inverter071_MODBUS.HRxxxx_M4_status | Module Status | 4107 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 IR | Inverter | Inverter071_MODBUS.HRxxxx_M4_iR_A | Module Current IR | 4108 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 IS | Inverter | Inverter071_MODBUS.HRxxxx_M4_iS_A | Module Current IS | 4109 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 IT | Inverter | Inverter071_MODBUS.HRxxxx_M4_iT_A | Module Current IT | 4110 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M4_iDC_A | Module Current IDC | 4111 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M4_vDCP_V | Module Vdc P | 4112 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M4_vDCN_V | Module Vdc N | 4113 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M4_vDC_V | Module Vdc | 4114 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 P | Inverter | Inverter071_MODBUS.HRxxxx_M4_p_kW | Module Real Power | 4115 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Q | Inverter | Inverter071_MODBUS.HRxxxx_M4_q_kVar | Module Reactive Power | 4116 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M4_ambientTemp_c | Module Ambient Temperature | 4117 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M4_maxIGBTTemp_c | Module Max IGBT Temperature | 4118 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M4_ioStatus | Module IO Status | 4119 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M4_hwVersion | Module Hardware Version | 4120 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M4 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M4_swVersion | Module Software Version | 4121 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Status | Inverter | Inverter071_MODBUS.HRxxxx_M5_status | Module Status | 4122 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 IR | Inverter | Inverter071_MODBUS.HRxxxx_M5_iR_A | Module Current IR | 4123 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 IS | Inverter | Inverter071_MODBUS.HRxxxx_M5_iS_A | Module Current IS | 4124 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 IT | Inverter | Inverter071_MODBUS.HRxxxx_M5_iT_A | Module Current IT | 4125 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M5_iDC_A | Module Current IDC | 4126 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M5_vDCP_V | Module Vdc P | 4127 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M5_vDCN_V | Module Vdc N | 4128 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M5_vDC_V | Module Vdc | 4129 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 P | Inverter | Inverter071_MODBUS.HRxxxx_M5_p_kW | Module Real Power | 4130 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Q | Inverter | Inverter071_MODBUS.HRxxxx_M5_q_kVar | Module Reactive Power | 4131 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M5_ambientTemp_c | Module Ambient Temperature | 4132 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M5_maxIGBTTemp_c | Module Max IGBT Temperature | 4133 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M5_ioStatus | Module IO Status | 4134 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M5_hwVersion | Module Hardware Version | 4135 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M5 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M5_swVersion | Module Software Version | 4136 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Status | Inverter | Inverter071_MODBUS.HRxxxx_M6_status | Module Status | 4137 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 IR | Inverter | Inverter071_MODBUS.HRxxxx_M6_iR_A | Module Current IR | 4138 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 IS | Inverter | Inverter071_MODBUS.HRxxxx_M6_iS_A | Module Current IS | 4139 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 IT | Inverter | Inverter071_MODBUS.HRxxxx_M6_iT_A | Module Current IT | 4140 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 IDC | Inverter | Inverter071_MODBUS.HRxxxx_M6_iDC_A | Module Current IDC | 4141 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 VDCP | Inverter | Inverter071_MODBUS.HRxxxx_M6_vDCP_V | Module Vdc P | 4142 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 VDCN | Inverter | Inverter071_MODBUS.HRxxxx_M6_vDCN_V | Module Vdc N | 4143 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 VDC | Inverter | Inverter071_MODBUS.HRxxxx_M6_vDC_V | Module Vdc | 4144 | V | Requested-Available | 0 | 1500 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 P | Inverter | Inverter071_MODBUS.HRxxxx_M6_p_kW | Module Real Power | 4145 | kW | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Q | Inverter | Inverter071_MODBUS.HRxxxx_M6_q_kVar | Module Reactive Power | 4146 | kVAR | Requested-Available | 0 | 5000 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Ambient Temp | Inverter | Inverter071_MODBUS.HRxxxx_M6_ambientTemp_c | Module Ambient Temperature | 4147 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Max IGBT Temp | Inverter | Inverter071_MODBUS.HRxxxx_M6_maxIGBTTemp_c | Module Max IGBT Temperature | 4148 | °C | Requested-Available | 0 | 100 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 IO Status | Inverter | Inverter071_MODBUS.HRxxxx_M6_ioStatus | Module IO Status | 4149 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Hardware Version | Inverter | Inverter071_MODBUS.HRxxxx_M6_hwVersion | Module Hardware Version | 4150 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV071 | Daggett 3_SUB1_INV071_M6 Software Version | Inverter | Inverter071_MODBUS.HRxxxx_M6_swVersion | Module Software Version | 4151 |  | Requested-Available | 0 | 65535 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_A Phase Current | Inverter | inverter072_MODBUS.HR1004_i1_A | A Phase Current | 4152 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_B Phase Current | Inverter | inverter072_MODBUS.HR1005_i2_A | B Phase Current | 4153 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_C Phase Current | Inverter | inverter072_MODBUS.HR1006_i3_A | C Phase Current | 4154 | A | Requested-Available | 0 | 600 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Bus Voltage | Inverter | inverter072_MODBUS.HR1051_vdcBus_V | Bus Voltage | 4155 | kV | Requested-Available | 0 | 35 | 0.001
SUB1 | INV072 | Daggett 3_SUB1_INV072_Apparent Power | Inverter | inverter072_MODBUS.HR1010_s3_VA | Apparent Power | 4156 | kVA | Requested-Available | 0 | 5000 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Common Mode Voltage | Inverter |  | Common Mode Voltage |  | kV | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 1 | Inverter | Inverter072_MODBUS.HR5805_du1_idc_A | Current DC Input# | 4157 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC Input 1 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC Input 1 | Inverter | Inverter072_MODBUS.HR5806_du1_vdc_V | Voltage DC Input # | 4158 | V | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 2 | Inverter | Inverter072_MODBUS.HR5811_du2_idc_A | Current DC Input# | 4159 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 2 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 2 | Inverter | Inverter072_MODBUS.HR5812_du2_vdc_V | Voltage DC Input # | 4160 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 3 | Inverter | Inverter072_MODBUS.HR5817_du3_idc_A | Current DC Input# | 4161 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 3 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 3 | Inverter | Inverter072_MODBUS.HR5818_du3_vdc_V | Voltage DC Input # | 4162 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 4 | Inverter | Inverter072_MODBUS.HR5823_du4_idc_A | Current DC Input# | 4163 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 4 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 4 | Inverter | Inverter072_MODBUS.HR5824_du4_vdc_V | Voltage DC Input # | 4164 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 5 | Inverter | Inverter072_MODBUS.HR5829_du5_idc_A | Current DC Input# | 4165 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 5 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 5 | Inverter | Inverter072_MODBUS.HR5830_du5_vdc_V | Voltage DC Input # | 4166 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 6 | Inverter | Inverter072_MODBUS.HR5835_du6_idc_A | Current DC Input# | 4167 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 6 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 6 | Inverter | Inverter072_MODBUS.HR5836_du6_vdc_V | Voltage DC Input # | 4168 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 7 | Inverter | Inverter072_MODBUS.HR5841_du7_idc_A | Current DC Input# | 4169 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 7 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 7 | Inverter | Inverter072_MODBUS.HR5842_du7_vdc_V | Voltage DC Input # | 4170 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 8 | Inverter | Inverter072_MODBUS.HR5847_du8_idc_A | Current DC Input# | 4171 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 8 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 8 | Inverter | Inverter072_MODBUS.HR5848_du8_vdc_V | Voltage DC Input # | 4172 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 9 | Inverter | Inverter072_MODBUS.HR5853_du9_idc_A | Current DC Input# | 4173 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 9 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 9 | Inverter | Inverter072_MODBUS.HR5854_du9_vdc_V | Voltage DC Input # | 4174 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 10 | Inverter | Inverter072_MODBUS.HR5859_du10_idc_A | Current DC Input# | 4175 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 10 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 10 | Inverter | Inverter072_MODBUS.HR5860_du10_vdc_V | Voltage DC Input # | 4176 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 11 | Inverter | Inverter072_MODBUS.HR5865_du11_idc_A | Current DC Input# | 4177 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 11 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 11 | Inverter | Inverter072_MODBUS.HR5866_du11_vdc_V | Voltage DC Input # | 4178 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 12 | Inverter | Inverter072_MODBUS.HR5871_du12_idc_A | Current DC Input# | 4179 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 12 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 12 | Inverter | Inverter072_MODBUS.HR5872_du12_vdc_V | Voltage DC Input # | 4180 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 13 | Inverter | Inverter072_MODBUS.HR5877_du13_idc_A | Current DC Input# | 4181 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 13 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 13 | Inverter | Inverter072_MODBUS.HR5878_du13_vdc_V | Voltage DC Input # | 4182 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 14 | Inverter | Inverter072_MODBUS.HR5883_du14_idc_A | Current DC Input# | 4183 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 14 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 14 | Inverter | Inverter072_MODBUS.HR5884_du14_vdc_V | Voltage DC Input # | 4184 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 15 | Inverter | Inverter072_MODBUS.HR5889_du15_idc_A | Current DC Input# | 4185 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 15 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 15 | Inverter | Inverter072_MODBUS.HR5890_du15_vdc_V | Voltage DC Input # | 4186 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 16 | Inverter | Inverter072_MODBUS.HR5895_du16_idc_A | Current DC Input# | 4187 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 16 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 16 | Inverter | Inverter072_MODBUS.HR5896_du16_vdc_V | Voltage DC Input # | 4188 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 17 | Inverter | Inverter072_MODBUS.HR5901_du17_idc_A | Current DC Input# | 4189 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 17 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 17 | Inverter | Inverter072_MODBUS.HR5902_du17_vdc_V | Voltage DC Input # | 4190 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 18 | Inverter | Inverter072_MODBUS.HR5907_du18_idc_A | Current DC Input# | 4191 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 18 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 18 | Inverter | Inverter072_MODBUS.HR5908_du18_vdc_V | Voltage DC Input # | 4192 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 19 | Inverter | Inverter072_MODBUS.HR5913_du19_idc_A | Current DC Input# | 4193 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 19 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 19 | Inverter | Inverter072_MODBUS.HR5914_du19_vdc_V | Voltage DC Input # | 4194 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current DC Input 20 | Inverter | Inverter072_MODBUS.HR5919_du20_idc_A | Current DC Input# | 4195 | A | Requested-Available | 0 | 300 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Real Power DC input 20 | Inverter |  | Real Power DC Input # |  | KW | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Voltage DC input 20 | Inverter | Inverter072_MODBUS.HR5920_du20_vdc_V | Voltage DC Input # | 4196 | kV | Requested-Available | 0 | 1500 | 0.1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current Ground | Inverter |  | Current Ground |  | A | Requested-Not Available
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current-AC | Inverter | inverter072_MODBUS.HR1007_i3Avg_A | Current-AC | 4197 | A | Requested-Available | 0 | 600 | 1
SUB1 | INV072 | Daggett 3_SUB1_INV072_Current-DC | Inverter | inverter072_MODBUS.HR1062_idcInput_A | Current-DC | 4198 | A | Requested-Available | 0 | 600 | 1