## TagNaming Criteria and Examples
Point Names follow the naming convention: | Site_Substation_DeviceID_AttributeName
Total Length of tag name <=60 | Example: Rock Creek_SUB1_MET1_Battery Voltage
Individual DeviceIDs <= 20 characters
Do not use underscores in any Attributes as they are reserved to delineate the hierarchy
Site
Use Name of Site from Electrical Drawings
Example: Rock Creek
Substation
Use SUB1 unless explicitly told otherwise
Example: SUB1
Device Type | DeviceID (< 20 chars) | Example1 | Example2 | Notes
Turbine | WTG### | WTG002 | WTG013D
Inverter | INV### | INV003 | INV001A
Inverter Module | INV###<X> | INV002A | INV002-01 | Modules are the only exception to the 4-level device hiearchy, and their attributes exist at a 5th level
MET Station | MET# | MET1 | MET2
Meter | use model #-Name on one-line and HS or LS for High/Low Side | SEL-735-M1 HS | SEL-735-M2 LS
Breaker Relay | use model #-Name on one-line | SEL-351S-11F1
Bus Relay | use model #-Name on one-line | SEL-587Z-87B1
Transformer Relay | use model #-Name on one-line | SEL-487E-87T1P
Line Relay | use model #-Name on one-line | SEL-411L-87L1S
Reactive Power Relay | use model #-Name on one-line | SEL-487V-87VC1P
Annunciator | use model #-Name on one-line | SEL-2523-ANN
Medium-High Voltage Transformer | XFMR###-Device Model | XFMR001-Qualitrol ITM | XFMR002-Hydran
Tracker Controller | TC(INV###)-## | TC001-01 | TC002A-02 | The first three number characters in the tracker name represent the respective inverter that the tracker is a child of.
Tracker Motor | TC(INV###)-##_M### | TC001-01_M001 | TC002A-02_M001 | The first three number characters in the tracker name represent the respective inverter that the tracker is a child of.
Soiling Station | SOIL### | SOIL001 | SOIL002
Power Plant Controller | PPC | PPC
Discrete IO (DPAC) | use model #-Name on one-line | SEL-2440-1
Analog IO (Axion) | use model #-Name on one-line | SEL-2240-1
Transmission Operator | TOP | TOP
AttributeName
Provide full list of attibutes from the Device Type
Device Type attributes are listed in the other tabs of this spreadsheet
Notes:
1. Do not skip any of the attributes
2. Spell all of the attributes exactly as shown in the template including spacing, underscores, upper and lower casing
3. Fill out the Availabilty column as detailed in Attachment 2
4. Make sure to use the Description from the templates for the Description in the points list, do not invent your own unless the point is not in the template

## Breaker Relay
Attribute Name | Units | Point Type | Description | Notes
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contact om the relay's INXXX contacts not explicitly called out above, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay
# Breaker Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | Invert any breakers where 0=Closed, typical of B contacts. If it is a 3 pole breaker logical OR them for a single status. Replace # with breaker name from one line (i.e. 52T1)
# Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | Replace # with breaker name from one line (i.e. 52T1)
# Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | Replace # with breaker name from one line (i.e. 52T1)
# Loss of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | Replace # with breaker name from one line (i.e. 52T1)
# Loss of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | Replace # with breaker name from one line (i.e. 52T1)
# Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | Replace # with breaker name from one line (i.e. 52T1)
# Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | Replace # with breaker name from one line (i.e. 52T1)
Real Power-AC | MW | Analog Input | AC Real Power | Should be positive when exporting to the grid
Reactive Power | MVAR | Analog Input | AC Reactive Power | Should be positive when exporting to the grid
Power Factor | Unitless | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
Voltage A-N | kV | Analog Input | L-N Phase Voltages
Voltage B-N | kV | Analog Input | L-N Phase Voltages
Voltage C-N | kV | Analog Input | L-N Phase Voltages
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | Unitless | Analog Input | Phase Power Factor
B Phase Power Factor | Unitless | Analog Input | Phase Power Factor
C Phase Power Factor | Unitless | Analog Input | Phase Power Factor
Energy Received | MWh | Accumulator | Energy Received
Energy Delivered | MWh | Accumulator | Energy Delivered
Reactive Energy Received | MVARh | Accumulator | Reactive Energy Received
Reactive Energy Delivered | MVARh | Accumulator | Reactive Energy Delivered
A Phase Energy Received | MWh | Accumulator | Phase Energy Received
B Phase Energy Received | MWh | Accumulator | Phase Energy Received
C Phase Energy Received | MWh | Accumulator | Phase Energy Received
A Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
B Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
C Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
A Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
B Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
C Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
A Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
B Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
C Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered

## MET Station
Attribute Name | Units | Point Type | Description | Notes
Battery Voltage | V | Analog Input | Battery Voltage
Humidity | % | Analog Input | Humidity
Pressure | hPa | Analog Input | Pressure
Temperature | °C | Analog Input | Temperature
Wind Direction | ° | Analog Input | Wind Direction
Wind Speed | m/s | Analog Input | Wind Speed
Wind Speed-10 minute average | m/s | Analog Input | Wind Speed-10 minute average
Wind Direction Average | m/s | Analog Input | Wind Direction Average
Humidity Average | % | Analog Input | Humidity Average
Pressure Average | hPa | Analog Input | Pressure Average
Temperature Average | °C | Analog Input | Temperature Average
Rain-10 Minute | in | Analog Input | Rain-10 Minute
Panel Temperature | °C | Analog Input | Panel Temperature
Heartbeat | Counts | Analog Input | Heartbeat

## Inverter
Attribute Name | Units | Point Type | Description | Notes
AutoStart On | 0=False, 1=TRUE | Binary Input | AutoStart On
Comm Fail | 0=False, 1=TRUE | Binary Input | Comm Fail
DC Monitor Offline | 0=False, 1=TRUE | Binary Input | DC Monitor Offline
Faulted | 0=False, 1=TRUE | Binary Input | Faulted
Locked Out | 0=False, 1=TRUE | Binary Input | Locked Out
Master Control Enabled | 0=False, 1=TRUE | Binary Input | Master Control Enabled
Offline | 0=False, 1=TRUE | Binary Input | Offline
Ramp Up Enabled | 0=False, 1=TRUE | Binary Input | Ramp Up Enabled
Ramp Down Enabled | 0=False, 1=TRUE | Binary Input | Ramp Down Enabled
Real Power Curtailment Flag | 0=False, 1=TRUE | Binary Input | Real Power Curtailment Flag | Flag indicating that inverter real power is being curtailed
Surge MOV Failed | 0=False, 1=TRUE | Binary Input | Surge MOV Failed
Following Setpoint | 0=False, 1=TRUE | Binary Input | Following Setpoint | Flag indicating that inverter is tracking the setpoint issud by the PPC
A Phase Current | A | Analog Input | A Phase Current
B Phase Current | A | Analog Input | B Phase Current
C Phase Current | A | Analog Input | C Phase Current
Bus Voltage | kV | Analog Input | Bus Voltage
Apparent Power | kVA | Analog Input | Apparent Power
Common Mode Voltage | kV | Analog Input | Common Mode Voltage
Current DC Input# | A | Analog Input | Current DC Input# | Replace # with Input Number and create additional points for all additional Inputs
Real Power DC Input # | KW | Analog Input | Real Power DC Input # | Replace # with Input Number and create additional points for all additional Inputs
Voltage DC Input # | kV | Analog Input | Voltage DC Input # | Replace # with Input Number and create additional points for all additional Inputs
Current Ground | A | Analog Input | Current Ground
Current-AC | A | Analog Input | Current-AC
Current-DC | A | Analog Input | Current-DC
Daily Energy Delivered | kWh | Analog Input | Daily Energy Delivered
Real Power Set Point | kW | Analog Input | Real Power Set Point
Reactive Power Set Point | kVAR | Analog Input | Reactive Power Set Point
Frequency | Hz | Analog Input | Frequency
IGBT Current | A | Analog Input | IGBT Current
Insulation Resistance | Ω | Analog Input | Insulation Resistance
Isolation Measure Timeout | V | Analog Input | Isolation Measure Timeout
Maximum DC Voltage | kV | Analog Input | Maximum DC Voltage
Minimum DC Voltage | kV | Analog Input | Minimum DC Voltage
Number of DU Channels | # | Analog Input | Number of DU Channels
Number of Running Modules | # | Analog Input | Number of Running Modules
Operating State | # | Analog Input | Operating State
Power Factor | Unitless | Analog Input | Power Factor
Ramp Down | MW/sec | Analog Input | Ramp Down
Ramp Rate | MW/sec | Analog Input | Ramp Rate
Ramp Up | MW/sec | Analog Input | Ramp Up
Real Power Delivered | kWh | Analog Input | Real Power Delivered
Reactive Power Delivered | kVARh | Analog Input | Reactive Power Delivered
Real Power | kW | Analog Input | Real Power
Reactive Power | kVAR | Analog Input | Reactive Power
Reactive Power Mode | # | Analog Input | Reactive Power Mode
Reactive Power Set Point Percent | % | Analog Input | Reactive Power Set Point Percent
Real Power AC Percent | % | Analog Input | Real Power AC Percent
Real Power-AC | kW | Analog Input | Real Power-AC
Real Power-DC | kW | Analog Input | Real Power-DC
Temperature-Air Intake | °C | Analog Input | Temperature-Air Intake
Temperature-Ambient | °C | Analog Input | Temperature-Ambient
Temperature-Cabinet | °C | Analog Input | Temperature-Cabinet
Temperature-Combiner Box | °C | Analog Input | Temperature-Combiner Box
Temperature-Coolant | °C | Analog Input | Temperature-Coolant
Temperature-Filter Choke | °C | Analog Input | Temperature-Filter Choke
Temperature-IGBT | °C | Analog Input | Temperature-IGBT
Temperature-IGBT Heat Sink | °C | Analog Input | Temperature-IGBT Heat Sink
Temperature-Module | °C | Analog Input | Temperature-Module
Uptime | seconds | Analog Input | Uptime
Voltage A-B | kV | Analog Input | Voltage A-B
Voltage A-N | kV | Analog Input | Voltage A-N
Voltage B-C | kV | Analog Input | Voltage B-C
Voltage B-N | kV | Analog Input | Voltage B-N
Voltage C-A | kV | Analog Input | Voltage C-A
Voltage C-N | kV | Analog Input | Voltage C-N
Voltage DC | kV | Analog Input | Voltage DC
Start | Latch On | Binary Output | Start
Stop | Latch On | Binary Output | Stop

## Inverter Module
Attribute Name | Units | Point Type | Description | Notes
A Phase Current | A | Analog Input
B Phase Current | A | Analog Input
C Phase Current | A | Analog Input
Current-DC | A | Analog Input
Energy Delivered | kWh | Analog Input
Firmware version |  | Analog Input
Hardware version |  | Analog Input
Inverter Name |  | Analog Input
IO Status |  | Analog Input
Module Status |  | Analog Input
Operating State |  | Analog Input
Reactive Energy | kVARh | Analog Input
Reactive Power | kVAR | Analog Input
Real Power-AC | kW | Analog Input
Temperature-Cabinet | °C | Analog Input
Temperature-IGBT-R1 | °C | Analog Input
Temperature-IGBT-R2 | °C | Analog Input
Temperature-IGBT-R3 | °C | Analog Input
Temperature-IGBT-S1 | °C | Analog Input
Temperature-IGBT-S2 | °C | Analog Input
Temperature-IGBT-S3 | °C | Analog Input
Temperature-IGBT-T1 | °C | Analog Input
Temperature-IGBT-T2 | °C | Analog Input
Temperature-IGBT-T3 | °C | Analog Input
Temperature-Max | °C | Analog Input
Tracker_Commanded Tilt AngleA | ° | Analog Input
Tracker_Commanded Tilt AngleB | ° | Analog Input
Tracker_Commanded Tilt AngleC | ° | Analog Input
Tracker_Commanded Tilt AngleD | ° | Analog Input
Tracker_Commanded Tilt AngleE | ° | Analog Input
Tracker_Commanded Tilt AngleF | ° | Analog Input
Tracker_Commanded Tilt AngleG | ° | Analog Input
Tracker_Commanded Tilt AngleH | ° | Analog Input
Voltage DC | kV | Analog Input
Voltage DC N | kV | Analog Input
Voltage DC P | kV | Analog Input
Current DC Input1 | A | Analog Input
Current DC Input2 | A | Analog Input
Current DC Input3 | A | Analog Input
Current DC Input4 | A | Analog Input
Current DC Input5 | A | Analog Input
Current DC Input6 | A | Analog Input
Current DC Input7 | A | Analog Input
Current DC Input8 | A | Analog Input
Power Command FB |  | Analog Input
Power Setpoint FB | kW | Analog Input
React Command FB |  | Analog Input
Reactive Setpoint FB | kVAR | Analog Input
Real Power-DC | kW | Analog Input
Temperature-Ambient | °C | Analog Input
Voltage DC Bus | kV | Analog Input

## Meter
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Normal, 1 = Alarm | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay
Real Power-AC | MW | Analog Input | AC Real Power
Reactive Power | MVAR | Analog Input | AC Reactive Power
Power Factor | N/A | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
Voltage THD | % | Analog Input | Phase Total Harmonic Voltage Distortion
Current THD | % | Analog Input | Phase Total Harmonic Current Distortion
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
Voltage A-N | kV | Analog Input | L-N Phase Voltages
Voltage B-N | kV | Analog Input | L-N Phase Voltages
Voltage C-N | kV | Analog Input | L-N Phase Voltages
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | N/A | Analog Input | Phase Power Factor
B Phase Power Factor | N/A | Analog Input | Phase Power Factor
C Phase Power Factor | N/A | Analog Input | Phase Power Factor
A Phase Energy Received | MWh | Accumulator | Phase Energy Received
B Phase Energy Received | MWh | Accumulator | Phase Energy Received
C Phase Energy Received | MWh | Accumulator | Phase Energy Received
A Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
B Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
C Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
A Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
B Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
C Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
A Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
B Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
C Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
Energy Received | MWh | Accumulator | Energy Received
Energy Delivered | MWh | Accumulator | Energy Delivered
Reactive Energy Received | MVARh | Accumulator | Reactive Energy Received
Reactive Energy Delivered | MVARh | Accumulator | Reactive Energy Delivered

## Bus Relay
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out above, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents

## Transformer Relay
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay
Breaker Fail Initiate | 0 = Normal, 1 = BFI | Binary Input | Breaker Fail Initiate
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out above, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
Real Power-AC | MW | Analog Input | AC Real Power | Should be positive when exporting to the grid
Reactive Power | MVAR | Analog Input | AC Reactive Power | Should be positive when exporting to the grid
Power Factor | Unitless | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
Voltage A-N | kV | Analog Input | L-N Phase Voltages
Voltage B-N | kV | Analog Input | L-N Phase Voltages
Voltage C-N | kV | Analog Input | L-N Phase Voltages
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | Unitless | Analog Input | Phase Power Factor
B Phase Power Factor | Unitless | Analog Input | Phase Power Factor
C Phase Power Factor | Unitless | Analog Input | Phase Power Factor
Energy Received | MWh | Accumulator | Energy Received
Energy Delivered | MWh | Accumulator | Energy Delivered
Reactive Energy Received | MVARh | Accumulator | Reactive Energy Received
Reactive Energy Delivered | MVARh | Accumulator | Reactive Energy Delivered
A Phase Energy Received | MWh | Accumulator | Phase Energy Received
B Phase Energy Received | MWh | Accumulator | Phase Energy Received
C Phase Energy Received | MWh | Accumulator | Phase Energy Received
A Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
B Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
C Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
A Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
B Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
C Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
A Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
B Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
C Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered

## Line Relay
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay
Breaker Fail Initiate | 0 = Normal, 1 = BFI | Binary Input | Breaker Fail Initiate
Line Comm Cutout | 0 = Normal, 1 = Cutout | Binary Input | Line Relaying Comm Cutout
Line Comm Failure | 0 = Normal, 1 = Alarm | Binary Input | Line Relaying Comm Failure
Direct Transfer Trip | 0 = Normal, 1 = Trip | Binary Input | Direct Transfer Trip
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out above, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2. Include the numeric INXXX in the Native RTAC Point Name
Real Power-AC | MW | Analog Input | AC Real Power | Should be positive when exporting to the grid
Reactive Power | MVAR | Analog Input | AC Reactive Power | Should be positive when exporting to the grid
Power Factor | Unitless | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
Voltage A-N | kV | Analog Input | L-N Phase Voltages
Voltage B-N | kV | Analog Input | L-N Phase Voltages
Voltage C-N | kV | Analog Input | L-N Phase Voltages
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | Unitless | Analog Input | Phase Power Factor
B Phase Power Factor | Unitless | Analog Input | Phase Power Factor
C Phase Power Factor | Unitless | Analog Input | Phase Power Factor

## Reactive Power Relay
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status | This should be the SEL_POU.Offline point in the relay inverted
Relay Enabled | 0 = Disabled, 1 = Enabled | Binary Input | Relay Online | This should be the SEL.FM_INST_EN point in the relay
Software Alarm | 0 = Normal, 1 = Alarm | Binary Input | Software Alarm | This should be the SEL.FM_INST_SALARM in the relay
Hardware Alarm | 0 = Normal, 1 = Alarm | Binary Input | Hardware Alarm | This should be the SEL.FM_INST_HALARM in the relay | Use this template for the relay that controls the capcitors and reactor banks
# Breaker Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | Invert any breakers where 0=Closed, typical of B contacts. If it is a 3 pole breaker logical OR them for a single status. Replace # with breaker name from one line (i.e. 52T1)
# Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | Replace # with breaker name from one line (i.e. 52V1)
# Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | Replace # with breaker name from one line (i.e. 52V1)
# Loss of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | Replace # with breaker name from one line (i.e. 52V1)
# Loss of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | Replace # with breaker name from one line (i.e. 52V1)
# Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | Replace # with breaker name from one line (i.e. 52V1)
# Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | Replace # with breaker name from one line (i.e. 52V1)
# Switch Status | 0 = Open, 1 = Closed | Binary Input | Switch Status | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Remote/Local At Breaker | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (At Breaker) | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Remote/Local Ctl House | 0 = Remote, 1 = Local | Binary Input | Remote Local Status (In Control House) | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Loss of AC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of AC Alarm | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Loss of DC Alarm | 0 = Normal, 1 = Alarm | Binary Input | Loss of DC Alarm | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Spring Charge Alarm | 0 = Normal, 1 = Alarm | Binary Input | Spring Charge Alarm | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
# Low SF6 Alarm | 0 = Normal, 1 = Alarm | Binary Input | Low SF6 Alarm | Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts not explicitly called out above, use the ansi relay and the relay name from the one line for the name (i.e. 86T1P) Mark these hardwired points as Not Requested-Available on Attachment 2
# MVAR Contribution | MVAR | Analog Input | MVAR Contribution | Should be positive for caps negative for reactors. VAR = VAR Nameplate(Voltage/Nameplate Voltage)^2 Replace # with the cap/reactor switcher name on the one-line (i.e 89C1, 89R1, 52CS1, 52RS1, etc). Include the proper amount of capacitors/reactors from the one lines.
Real Power-AC | MW | Analog Input | AC Real Power | Should be positive when exporting to the grid
Reactive Power | MVAR | Analog Input | AC Reactive Power | Should be positive when exporting to the grid
Power Factor | Unitless | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
Voltage A-N | kV | Analog Input | L-N Phase Voltages
Voltage B-N | kV | Analog Input | L-N Phase Voltages
Voltage C-N | kV | Analog Input | L-N Phase Voltages
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | Unitless | Analog Input | Phase Power Factor
B Phase Power Factor | Unitless | Analog Input | Phase Power Factor
C Phase Power Factor | Unitless | Analog Input | Phase Power Factor

## Medium-High Voltage Transformer
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status
Oil Temperature High Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Winding Temperature High Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
High Pressure Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Low Pressure Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Low Vacuum Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Oil Level Low Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Sudden Pressure Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Loss Of Cooling Alarm | 0 = Normal, 1 = Alarm | Binary Input | Transformer Alarms
Fan Stage | 0,1,2 | Analog Input | Stage fan status
Temperature Oil | °C | Analog Input | Oil Temperature
Temperature Winding | °C | Analog Input | Winding Temperature
Pressure | hPa | Analog Input | Pressure
Oil Level | % | Analog Input | Oil Level
Tap Position | Tap Number | Analog Input | Transformer Tap Position

## Tracker Controller
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status
Auto Track | 0 = False, 1 = True | Binary Input | autotrack
Global Clean | 0 = False, 1 = True | Binary Input | clean
Fault | 0 = False, 1 = True | Binary Input | fault
Stow | 0 = False, 1 = True | Binary Input | stow
Alarm | 0 = Normal, 1 = Alarm | Binary Input | alarm
Status | 0 = Normal, 1 = Alarm | Binary Input | status
Status2 | 0 = Normal, 1 = Alarm | Binary Input | status2
SPC Count | # | Analog Input | SPC Count
Setpoint | ° | Analog Input | Set Point
Position | ° | Analog Input | Position
Wind speed | m/s | Analog Input | Current wind speed
Snow |  | Analog Input | Current snow depth
LAT |  | Analog Input | Latitude of tracker controller
LONG |  | Analog Input | Longitude of tracker controller
H2O |  | Analog Input
MotorXXX-Tracking-Angle | ° | Analog Input | Current tracking angle of motor # XXX | Repeat these two lines for each motor connected to this controller
MotorXXX-Tracking-Setpoint | ° | Analog Input | Current tracking setpoint of motor # XXX

## PPC
Attribute Name | Units | Point Type | Description | Notes
GMS Unit # MW Setpoint Feedback | MW | Analog Input | GMS MW Setpoint Feedback | Replace # with the unit number. Start at 1. If the site is controlled as more than one unit duplicate this point for Unit 2, 3, n
GMS POI VAR Setpoint Feedback | MVAR | Analog Input | GMS POI VAR Setpoint Feedback
GMS POI PF Setpoint Feedback | positive is lagging, negative is leading | Analog Input | GMS POI PF Setpoint Feedback
GMS POI Voltage Setpoint Feedback | KV | Analog Input | GMS POI Voltage Setpoint Feedback
GMS Ramp Up Rate Setpoint Feedback | MW/Min | Analog Input | GMS Ramp Up Rate Setpoint Feedback
GMS Ramp Down Rate Setpoint Feedback | MW/Min | Analog Input | GMS Ramp Down Rate Setpoint Feedback
Effective Real Power Setpoint | MW | Analog Input | PPC Real Power Setpoint | This is the real power setpoint active in the PPC
Effective Reactive Power Setpoint | MVAR | Analog Input | PPC Reactive Power Setpoint | This is the reactive power setpoint active in the PPC
Effective Power Factor Setpoint | positive is lagging, negative is leading | Analog Input | PPC Power Factor Setpoint | This is the power factor setpoint active in the PPC
Effective Voltage Setpoint | KV | Analog Input | PPC Voltage Setpoint | This is the real power setpoint active in the PPC
Effective Ramp Rate Up Setpoint | MW/Min | Analog Input | PPC Ramp Rate Up Setpoint
Effective Ramp Rate Down Setpoint | MW/Min | Analog Input | PPC Ramp Rate Down Setpoint
Effective Reactive Power Control Mode | 0=error/off, 1=Voltage, 2=VAR, 3=PF | Analog Input | PPC Control Status | The mode the PPC is currently operating in
Real Time Power Potential | MW | Analog Input | PPC Real Time Power Potential | The amount of MW the available turbines can produce based on current conditions
GMS Unit # Curtailment Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Curtailment Disabled/Enabled | Replace # with the unit number. Start at 1. If the site is controlled as more than one unit duplicate this point for Unit 2, 3, n
GMS Reactive Power Control Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Reactive Power Control Disabled/Enabled
GMS Power Factor Control Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Power Factor Control Disabled/Enabled
GMS Voltage Control Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Voltage Control Disabled/Enabled
GMS Ramp Up Rate Control Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Ramp Up Rate Control Disabled/Enabled
GMS Ramp Down Rate Control Disabled/Enabled | 0=Disabled, 1=Enabled | Binary Input | GMS Ramp Down Rate Control Disabled/Enabled
AVR Active | 0=FALSE, 1=TRUE | Binary Input | AVR Active | Should be True if the PPC is running and reactive power is being controlled at the plant via some means. Should be FALSE if there is a failure in the PPC that causes reactive power control to fail for any reason
Unit # Active Curtailment | 0=FALSE, 1=TRUE | Binary Input | Active Curtailment | Should be True if any entity (including frequency events) is actively curtailing the unit, else False If the site is controlled as more than one unit duplicate this point for Unit 2
Invalid GMS Unit # Curtailment Setpoint Alarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Curtailment Setpoint Alarm | Discuss with Clearway what deadbands should be for rejecting setpoints and triggering this alarm If the site is controlled as more than one unit duplicate this point for Unit 2
Invalid GMS Voltage Setpoint Alarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Voltage Setpoint Alarm | Discuss with Clearway what deadbands should be for rejecting setpoints and triggering this alarm
Invalid GMS VAR Setpoint Alarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS VAR Setpoint Alarm | Discuss with Clearway what deadbands should be for rejecting setpoints and triggering this alarm
Invalid GMS PF Setpoint Alarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS PF Setpoint Alarm | Discuss with Clearway what deadbands should be for rejecting setpoints and triggering this alarm
Invalid GMS Ramp Rate Setpoint Alarm | 0=Normal, 1=Alarm | Binary Input | Invalid GMS Ramp Rate Setpoint Alarm | Discuss with Clearway what deadbands should be for rejecting setpoints and triggering this alarm
INV# Control Status | 0=Disabled, 1=Enabled | Binary Input | Inverter Control Status
High Frequency Event Flag | 0=Off, 1=On | Binary Input | High Frequency Event Flag | TRUE when the site is being curtailed due to a high frequency excursion
Low Frequency Event Flag | 0=Off, 1=On | Binary Input | Low Frequency Event Flag | TRUE when site setpoint is increasing due to a low frequency excursion
GMS Unit # MW Setpoint | MW*100 | Analog Output | MW Setpoint | Replace # with the unit number. Start at 1. If the site is controlled as more than one unit duplicate this point for Unit 2, 3, n
GMS POI PF Setpoint | MVAR*100 | Analog Output | GMS POI PF Setpoint
GMS POI Voltage Setpoint | PF*100 | Analog Output | GMS POI Voltage Setpoint
GMS POI VAR Setpoint | KV*100 | Analog Output | GMS POI VAR Setpoint
GMS Ramp Up Rate Setpoint | (MW/min)*100 | Analog Output | GMS Ramp Up Rate Setpoint
GMS Ramp Down Rate Setpoint | (MW/min)*100 | Analog Output | GMS Ramp Down Rate Setpoint
GMS Unit # Curtailment Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | Curtailment Disable/Enable | Replace # with the unit number. Start at 1. If the site is controlled as more than one unit duplicate this point for Unit 2, 3, n
GMS Voltage Mode Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Voltage Mode Disable/Enable
GMS PF Mode Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS PF Mode Disable/Enable
GMS MVAR Mode Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS MVAR Mode Disable/Enable
GMS Ramp Up Rate Setpoint Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Ramp Up Rate Setpoint Disable/Enable
GMS Ramp Down Rate Setpoint Disable/Enable | Latch Off = Disable, Latch On = Enable | Binary Output | GMS Ramp Down Rate Setpoint Disable/Enable
GMS # Breaker Control | Latch Off = Trip, Latch On = Close | Binary Output | Breaker Controls | Include all controls for all breakers shown on the one lines (i.e. GMS 52T1 Breaker Control)
GMS # MOD Control | Latch Off = Open, Latch On = Close | Binary Output | Breaker Controls | Include all controls for all MOD switches shown on the one lines (i.e. GMS 89L1 MOD Control)
GMS Inverter # Control | Latch On = Reset | Binary Output | Inverter Controls | Replace # with the inverter number and duplicate for all inverters
GMS Turbine # Control | Latch On = Reset | Binary Output | Turbine Controls | Replace # with the turbine number and duplicate for all turbines

## TOP
Attribute Name | Units | Point Type | Description | Notes
POI Breaker 52# Status | 0 = Open, 1 = Closed | Binary Input | Breaker Status | Get the status of all breakers that we are connected to at the POI. If this is a ring bus there may be more than one Replace # with the actual breaker notation on the one line
Real Power-AC | MW | Analog Input | AC Real Power
Reactive Power | MVAR | Analog Input | AC Reactive Power
Power Factor | N/A | Analog Input | Power Factor
Voltage A-B | kV | Analog Input | Phase-Phase Voltages
Voltage B-C | kV | Analog Input | Phase-Phase Voltages
Voltage C-A | kV | Analog Input | Phase-Phase Voltages
A Phase Current | A | Analog Input | Phase Currents
B Phase Current | A | Analog Input | Phase Currents
C Phase Current | A | Analog Input | Phase Currents
Frequency | Hz | Analog Input | Frequency
A Phase Power | MW | Analog Input | Phase Power
B Phase Power | MW | Analog Input | Phase Power
C Phase Power | MW | Analog Input | Phase Power
A Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
B Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
C Phase Apparent Power | MVA | Analog Input | Phase Apparent Power
A Phase Power Factor | N/A | Analog Input | Phase Power Factor
B Phase Power Factor | N/A | Analog Input | Phase Power Factor
C Phase Power Factor | N/A | Analog Input | Phase Power Factor
A Phase Energy Received | MWh | Accumulator | Phase Energy Received
B Phase Energy Received | MWh | Accumulator | Phase Energy Received
C Phase Energy Received | MWh | Accumulator | Phase Energy Received
A Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
B Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
C Phase Energy Delivered | MWh | Accumulator | Phase Energy Delivered
A Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
B Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
C Phase Reactive Energy Received | MVARh | Accumulator | Phase Reactive Energy Received
A Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
B Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
C Phase Reactive Energy Delivered | MVARh | Accumulator | Phase Reactive Energy Delivered
Energy Received | MWh | Accumulator | Energy Received
Energy Delivered | MWh | Accumulator | Energy Delivered
Reactive Energy Received | MVARh | Accumulator | Reactive Energy Received
Reactive Energy Delivered | MVARh | Accumulator | Reactive Energy Delivered

## Analog IO (Axion)
Attribute Name | Units | Point Type | Description | Notes
|  | Analog Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2

## Discrete IO (DPAC)
Attribute Name | Units | Point Type | Description | Notes
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the relay's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2
Use this template for any SEL DPACs

## Annunciator
Attribute Name | Units | Point Type | Description | Notes
|  | Binary Input | Hard Wired Contacts | Provide all hard wired contacts from the Annunciator's INXXX contacts Mark these hardwired points as Not Requested-Available on Attachment 2
Use this template for any SEL DPACs

## Soiling Station
Attribute Name | Units | Point Type | Description | Notes
Communication Status | 0 = Offline, 1 = Online | Binary Input | Communication Status
Soiling Ratio | % | Analog Input | Soiling Ratio | Fraction loss of transmission due to soiling particles
Transmission Loss | % | Analog Input | Transmission Loss